## Executive Summary
Executive Summary: DISIS-2020-001-1 Restudy of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on April 30, 2020. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 4.2 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2020-001-1 Restudy includes study requests in the following cluster groups: ( 01 NORTH, 02 NEBRASKA, 03 CENTRAL, 04 SOUTHEAST, 05 SOUTHWEST)
DISIS Manual Version 4.2
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20250225.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
8,872.86 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade: $690,779,010.00 Steady State Network Upgrade: $113,878,336.00 Stability Network Upgrade: $0.00 Steady State/Stability Network Upgrade: $73,524,573.00 Interconnection Costs: $503,376,101.00
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: 7/6/2026
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the DISIS Manual Section 4.2.2.2.
Proxy or Potential P4 contingencies were tested for steady state analysis, and verified with the TOs for validity if the contingencies report the most limiting constraint.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
4572200% | SPP | Initial Draft
4573000% | SPP | Final
4577900% | SPP | Final Revision #2
4584100% | SPP | Final Revision #3
4595200% | SPP | Final Revision #4
4596100% | SPP | Final Revision #5
4618800% | SPP | Final Revision #6
4620900% | SPP | Final Revision #7

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4573000% | Upgrade Name/Details | 6,7,8,10 | Constraints Summary, Assigned Upgrade Costs, Upgrade Summary, All Thermal | Remove 'Build New S1362 to S1363 161 kV Second Circuit' Network Upgrade due to feedback received that the circuit is currently in-service.
4573000% | Upgrade Name/Details | 6,7,8,10 | Constraints Summary, Assigned Upgrade Costs, Upgrade Summary, All Thermal | Remove 'S1209 - S1231 Ckt 2 161 kV Reconductor' Network Upgrade due to feedback received that the project is complete.
4573000% | Upgrade Name/Details | 7,8 | Assigned Upgrade Costs, Upgrade Summary | Updated Upgrade Details for the Catoosa Terminal Upgrade to reflect correct minimum rating of 218 MVA
4573000% | LOIS Amount | 4 | Requests | Updated LOIS values for GEN-2020-025, GEN-2020-028, GEN-2020-031, GEN-2020-043, GEN-2020-044, and GEN-2020-045 due to removed Network Upgrades
4573000% | LOIS Amount | 5 | Seasonal LOIS | Updated LOIS values for GEN-2020-025, GEN-2020-028, GEN-2020-031, GEN-2020-043, GEN-2020-044, and GEN-2020-045 due to removed Network Upgrades
4573000% | Fuel Type | 4 | Requests | Updated 'Fuel Type' in Requests tab for hybrid study requests
4577900% | Total Costs | 1 | Executive Summary | Updated total MW interconnecting in DISIS-2020-001 and updated total interconnection and network upgrade costs based on sensitivity analysis
4577900% | Requests | 4 | Requests | Removed one (1) withdrawn request in Group 04 (GEN-2020-075) and four (4) withdrawn requests in Group 05 (GEN-2020-009, GEN-2020-017, GEN-2020-059, and GEN-2020-062)
4577900% | LOIS Amount | 5 | Seasonal LOIS | Updated Seasonal LOIS values based on withdrawn requests in Group 04 and new assigned Network Upgrades and sensitivity analysis performed
4577900% | Upgrade Name/Details | 6 | Constraints Summary | Updated Network Upgrades due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4577900% | Upgrade Name/Details | 7 | Assigned Upgrade Costs | Updated Network Upgrades and assigned allocated costs due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4577900% | Upgrade Name/Details | 8 | Upgrade Summary | Updated Network Upgrades due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4577900% | Upgrade Name/Details | 9 | Contingent Upgrades - Screening | Removed results related to withdrawn requests in Group 04 and Group 05
4577900% | Upgrade Name/Details | 10 | All Thermal | Updated Group 04 and Group 05 thermal constraints due to withdrawn requests and sensitivity analysis performed
4577900% | Upgrade Name/Details | 12 | Stability Analysis Results | Updated Group 05 stability results based on Group 05 withdrawn requests and sensitivity analysis performed
4577900% | Results | 13 | Short Circuit Analysis | Removed results related to withdrawn requests in Group 04 and Group 05
4584100% | Contingent Facility | 6 | Constraints Summary | Remove withdrawn NTC 200419 (revised NTC 220861).
4584100% | Contingent Facility | 7 | Assigned Upgrade Costs | Remove withdrawn NTC 200419 (revised NTC 220861).
4584100% | Contingent Facility | 8 | Upgrade Summary | Remove withdrawn NTC 200419 (revised NTC 220861).
4584100% | Contingent Facility | 9 | Contingent Upgrades - Screening | Remove withdrawn NTC 200419 (revised NTC 220861).
4584100% | Results | 10 | All Thermal | Remove withdrawn NTC 200419 (revised NTC 220861) and updated results impacting contingent facility analysis.
4584100% | Group 05 Network Upgrade |  | Constraints Summary / Assigned Upgrade Costs / Upgrade Summary / Stability Analysis Results | Based on TO feedback, replaced the G17-151 Tap to Border 345 kV Network Upgrade with the 350 MVAR STATCOM at Border 345 kV due to more cost effective solution following Facility Study and TO acceptance.
4584100% | Upgrade Cost Estimates |  | Executive Summary / Assigned Upgrade Costs / Upgrade Summary | Updated cost estimate for Build New Tolk to Potter County 345 kV Line based on TO feedback. Updated several Network Upgrades for AEP based on facility study costs.
4584100% | Interconnection Costs |  | Assigned Upgrade Costs / Upgrade Summary | Updated interconnection costs for AEP based on facility studies.
4595200% | Total Costs | 1 | Executive Summary | Updated total MW interconnecting in DISIS-2020-001 and updated total interconnection and network upgrade costs based on sensitivity analysis
4595200% | Requests | 4 | Requests | Removed two (2) withdrawn requests in Group 04 (GEN-2020-074 and GEN-2020-085) and one (1) withdrawn requests in Group 05 (GEN-2020-068)
4595200% | LOIS Amount | 5 | Seasonal LOIS | Updated Seasonal LOIS values based on withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4595200% | Upgrade Name/Details | 6 | Constraints Summary | Updated Network Upgrades due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4595200% | Upgrade Name/Details | 7 | Assigned Upgrade Costs | Updated Network Upgrades and assigned allocated costs due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4595200% | Upgrade Name/Details | 8 | Upgrade Summary | Updated Network Upgrades due to withdrawn requests in Group 04 and Group 05 and sensitivity analysis performed
4595200% | Upgrade Name/Details | 9 | Contingent Upgrades - Screening | Removed results related to withdrawn requests in Group 04 and Group 05
4595200% | Upgrade Name/Details | 10 | All Thermal | Updated Group 04 and Group 05 thermal constraints due to withdrawn requests and sensitivity analysis performed
4595200% | Upgrade Name/Details | 12 | Stability Analysis Results | Updated Group 05 stability results based on Group 05 withdrawn requests and sensitivity analysis performed
4596100% | Total Costs | 1 | Executive Summary | Corrected total interconnection and network upgrade costs based on updated facility studies
4596100% | LOIS Amount | 4 | Requests | Updated LOIS values for GEN-2020-003, GEN-2020-007, GEN-2020-008, GEN-2020-057, GEN-2020-058, GEN-2020-072, GEN-2020-073, GEN-2020-025 and GEN-2020-028
4596100% | Cost allocation | 7 | Assigned Upgrade Costs | Corrected interconnection costs based on updated facility studies
4596100% | Cost allocation | 8 | Upgrade Summary | Corrected interconnection costs based on updated facility studies
4596100% | LOIS Amount | 5 | Seasonal LOIS | Removed Wolf Creek to Blackberry 345 kV as contingent upgrade after being placed in-service and update LOIS values
4596100% | Upgrade Name/Details | 9 | Contingent Upgrades - Screening | Removed Wolf Creek to Blackberry 345 kV as contingent upgrade after being placed in-service
4618800% | Total MW | 1 | Executive Summary | Updated cluster total size to account for the withdrawal of GEN-2020-069
4618800% | Requests | 4 | Requests | Removed one (1) withdrawn request in Group 02 (GEN-2020-069)
4618800% | Results | 7, 9 | Assigned Upgrade Costs / All Thermal | Results updated based on the withdrawal of GEN-2020-069.
4618800% | Results | 10, 13, 14 | Contingent Upgrades Summary - Screening / Short Circuit Analysis / SCRCCT | GEN-2020-069 results removed.
4620900% | Total MW | 1 | Executive Summary | Updated cluster total size to account for the withdrawal of GEN-2020-073
4620900% | Requests | 4 | Requests | Removed one (1) withdrawn request in Group 03 (GEN-2020-073)
4620900% | Results | 7, 8, 9 | Upgrade Summary/Assigned Upgrade Costs / All Thermal | Updated Network Upgrades due to withdrawn request in Group 03 (GEN-2020-073) and sensitivity analysis performed
4620900% | Results | 10, 13, 14 | Contingent Upgrades Summary - Screening /All Thermal/ Short Circuit Analysis / SCRCCT | GEN-2020-073 results removed and updated results for thermal analysis.

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 0 | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | -41.1024 | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | 74.5 | -1.9199 | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -1.6437 | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | 258 | 258 | 258 | 258 | 258 | 258 | 272.7 | 272.7 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | 258 | 258 | 258 | 258 | 258 | 258 | 272.7 | 272.7 | 0 | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | -1.7567 | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | -3 | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 215 | 124.196 | 124.196 | 124.232 | 124.22 | 124.196 | 124.196 | 124.196 | 124.196 | -1.8 | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 0 | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | 56.52 | -0.58 | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -2.5718 | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | -3 | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -7.1298 | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Storage | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | -4.0632 | ER/NR | WERE | Wolf Creek- Blackberry 345 kV Substation | DISIS STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | -0.27726 | ER | KCPL | South Waverly 69 kV Substation | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | -0.27693 | ER | KCPL | Caroltown 161 kV Substation | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0 | ER/NR | KPP | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | 650 | -11.2113 | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -4.8203 | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | -1.0072 | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | -0.70622 | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | 424.5 | -14.9422 | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | ER/NR | GMO | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 0 | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -3.5856 | ER/NR | GMO | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 3.7309 | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -3.0834 | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | -1.55 | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | -1.4 | ER/NR | AEPW | Snyder-Altus Jct. 138kV | DISIS STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | -3.1 | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | -4.8 | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -6 | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | -0.3 | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | -1.8 | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4 | ER | SPS | Hobbs-Andrews 230 kV Line | DISIS STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -116.7 | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | [9 empty] | ER/NR | NIPCO | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Wind | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | ITCGP | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 80 | [9 empty] | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-051 | 03 CENTRAL | 21 | DIS-19-1 | Storage | 40 | [9 empty] | ER/NR | SUNC | Frey St 115kV bus | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | ITCGP | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Storage | 50 | [9 empty] | ER/NR | ITCGP | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | MWEC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 19.8 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 302.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV Substation | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-063 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 57 | [9 empty] | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Storage | 95 | [9 empty] | ER | ITCGP | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 CENTRAL | 21 | DIS-18-2 | Solar | 150 | [9 empty] | ER/NR | SUNC | Frey Street 115kV bus | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GIA-106 | 03 CENTRAL | 20.5 | DIS-19-1 PQ | Solar | 350.08 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 20.5 | DIS-19-1 PQ | Solar | 250 | [9 empty] | ER/NR | AECI
MPC4300 | 01 NORTH | 20.5 | DIS-18-2-PQ | WIND | 400 | [9 empty] | ER/NR | OTP
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | GAS | 75 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | GAS | 460 | [9 empty] | ER/NR | AECI
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | FACILITY STUDY STAGE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | FACILITY STUDY STAGE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | FACILITY STUDY STAGE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | FACILITY STUDY STAGE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | FACILITY STUDY STAGE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | FACILITY STUDY STAGE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | FACILITY STUDY STAGE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | FACILITY STUDY STAGE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | FACILITY STUDY STAGE
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Storage | 74.1 | [9 empty] | ER/NR | BEPC | Neset 230kV Substation | FACILITY STUDY STAGE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | FACILITY STUDY STAGE
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | FACILITY STUDY STAGE
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | FACILITY STUDY STAGE
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | FACILITY STUDY STAGE
GEN-2018-060 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | FACILITY STUDY STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | FACILITY STUDY STAGE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | FACILITY STUDY STAGE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Storage | 50 | [9 empty] | ER | INDN | Blue Valley 161kV Substation | FACILITY STUDY STAGE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | FACILITY STUDY STAGE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | ITCGP | Thistle 345kV Substation | FACILITY STUDY STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | FACILITY STUDY STAGE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | FACILITY STUDY STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | FACILITY STUDY STAGE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | FACILITY STUDY STAGE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | FACILITY STUDY STAGE
MPC3600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 170 | [9 empty] | ER | OTP | Frontier-Wahpeton 230 kV Line
MPC3700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 130 | [9 empty] | ER | OTP | Frontier-Wahpeton 230 kV Line
MPC3800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | OTP | Center-Prairie 345 kV Line
MPC3900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | [9 empty] | ER/NR | OTP | Center-Prairie 345 kV Line
MPC4000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER/NR | OTP | Square Butte 230 kV Substation
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 400 | [9 empty] | ER/NR | AMMO | Spencer Creek 345 kV Substation | IA PENDING
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138 kV line | IA PENDING
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Storage | 20 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL | Byron 345kV | NOT STARTED
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW | Rutland Substation 161kV | NOT STARTED
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Huntley to Blue Earth 161kV | NOT STARTED
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | NOT STARTED
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Nobles County 345 kV Substation | NOT STARTED
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Bison 345kV | NOT STARTED
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL | Sherburne 345kV | NOT STARTED
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 174 | [9 empty] | ER/NR | XEL | Langola 115kV Tap | NOT STARTED
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | XEL | Pipestone to Split Rock 115kV | NOT STARTED
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | XEL | Pine Lake to Apple River 161 kV | NOT STARTED
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL | Eau Claire to AS King 345 kV | NOT STARTED
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 120 | [9 empty] | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | NOT STARTED
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | DPC | Barron 161 kV | NOT STARTED
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER | XEL | Cannon Falls Transmission 69 kV | NOT STARTED
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER | XEL | Adams 345kV Substation | IA PENDING
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW | Ledyard - Colby 345 kV | NOT STARTED
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | NOT STARTED
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | NOT STARTED
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC | Clarinda-Coburg 69 kV | NOT STARTED
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | O'Brien - Raun 345 kV | NOT STARTED
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 | [9 empty] | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 68.4 | [9 empty] | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 | [9 empty] | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 97.5 | [9 empty] | ER | AECI | Stroud 138kV
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Marion - Marked Tree 161kV Line Tap | IA PENDING
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Poco - Menard 138kV Line Tao | IA PENDING
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI | West Memphis - Keo 500 kV Line Tap | IA PENDING
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV Line Tap | IA PENDING
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230 kV Substation | IA PENDING
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC | Centennial - West Bay 138kV Line | IA PENDING
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES | Rilla 115 kV Substation | IA PENDING
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Storage | 50 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI | Crossett - Monticello East 115kV Line | IA PENDING
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Storage | 0 | [9 empty] | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC | Cooper - Penton Road 230kV Line | IA PENDING
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES | Oak Ridge 115 kV Substation | IA PENDING
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI | AECC Dry Creek 161kV Switchyard Station | IA PENDING
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | Rich (SHECO) - Livingston 138 kV Line Tap | IA PENDING
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI | Driver 230kV | NOT STARTED
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | NOT STARTED
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | NOT STARTED
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | NOT STARTED
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Hardin West SS (Endpoint A) to Sheridan (Endpoint B) 115 kV | NOT STARTED
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER | EES | Goos Ferry | NOT STARTED
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Storage | 25 | [9 empty] | ER/NR | EES | Rilla 115kV substation (Same as J1239) | NOT STARTED
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | NOT STARTED
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | NOT STARTED
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | NOT STARTED
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES | Rocky Creek to Lewis Creek 230kV | NOT STARTED
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI | Tinnin Road 230kV | NOT STARTED
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | NOT STARTED
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | NOT STARTED
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI | J830 POI | NOT STARTED
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI | Twinkletown 230 kV | NOT STARTED
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES | Timberland 230kV | NOT STARTED
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | NOT STARTED
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | NOT STARTED
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES | Bastrop tap point | NOT STARTED
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES | Sabine 138/230 kV Substation | NOT STARTED
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI | Forrest City to Wynne S 161 KV | NOT STARTED
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA PENDING
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA PENDING
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA PENDING
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA PENDING
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA PENDING
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA PENDING
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA PENDING
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA PENDING
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 210 | [9 empty] | ER | OKGE | Renfrow 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA PENDING
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA PENDING
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA PENDING
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA PENDING
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC | Logan 230kV Substation | IA PENDING
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC | Logan 230kV Substation | IA PENDING
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA PENDING
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA PENDING
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA PENDING
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA PENDING
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 29.6 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA PENDING
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA PENDING
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA PENDING
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA PENDING
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA PENDING
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA PENDING
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL | Buffalo 115kV Substation
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP | Big Stone South 230kV Substation
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC | Crystal Cave-Rock Elm 161kV line tap
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL | Fenton - Chanarambie 115kV Line
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 101.28 | [9 empty] | ER | XEL | Pine Lake - Apple River 161 kV Line
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW | Ledyard 345kV Substation
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation)
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | ITCGP | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | ITCGP | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA PENDING
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | BEPC | NELSON 7
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC | Cherry Grove 69kV Substation
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC | Highland - Raun 345kV Line Tap
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | Tri-State | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | [9 empty] | ER/NR | XEL | NSP Rock County Substation
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | [9 empty] | ER/NR | AMMO | Atchison County to Booneville 345 kV Line Tap
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS | Palo Duro 115kV
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | CT | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Storage | 20 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | [9 empty] | ER/NR | BEPC | Nelson 115kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | [9 empty] | ER/NR | BEPC | Wessington Springs 230kV
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | BEPC | Hilken 230kV [Ecklund 230kV]
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | BEPC | Hilken 230kV [Ecklund 230kV]
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | BEPC | Groton 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | BEPC | Dickenson-Heskett 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 11.72 | [9 empty] | ER/NR | BEPC | Williston 115kV
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS | FE-Clovis Interchange 115kV
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 SOUTHWEST | 8 | PQ | Gas | 604 | [9 empty] | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBUFFALOCOUNTYSOLAR | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD | Tekamah & Oakland 115kV
GEN-2001-030 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | CT | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | [9 empty] | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | CT | 72 | [9 empty] | ER | KCPL/MIPU | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability 25SP | Stability 25WP
ASGI-2020-001 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-001 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-001 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 35 | 35 | None | None | N/A | N/A | N/A | 35 | N/A | N/A | N/A | N/A | N/A | 35
ASGI-2020-001 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 35 | 35 | None | None | N/A | N/A | N/A | 35 | N/A | N/A | N/A | N/A | N/A | 35
ASGI-2020-001 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | N/A | N/A | N/A | N/A | N/A | 35 | N/A
ASGI-2020-001 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 35 | N/A
ASGI-2020-001 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-001 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-003 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-003 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-003 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 35 | 35 | None | None | N/A | N/A | N/A | 35 | N/A | N/A | N/A | N/A | N/A | 35
ASGI-2020-003 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 35 | 35 | None | None | N/A | N/A | N/A | 35 | N/A | N/A | N/A | N/A | N/A | 35
ASGI-2020-003 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | N/A | N/A | N/A | N/A | N/A | 35 | N/A
ASGI-2020-003 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 35 | N/A
ASGI-2020-003 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 35 | 35 | None | None | N/A | 35 | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
ASGI-2020-003 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 35 | 35 | None | None | 35 | N/A | N/A | 35 | N/A | N/A | N/A | N/A | 35 | 35
GEN-2020-002 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 81 | 81 | None | None | N/A | 81 | N/A | 81 | N/A | N/A | N/A | N/A | 81 | 81
GEN-2020-002 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 81 | 81 | None | None | 81 | N/A | N/A | 81 | N/A | N/A | N/A | N/A | 81 | 81
GEN-2020-002 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 81 | 81 | None | None | N/A | N/A | N/A | 81 | N/A | N/A | N/A | N/A | N/A | 81
GEN-2020-002 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 81 | 81 | None | None | N/A | N/A | N/A | 81 | N/A | N/A | N/A | N/A | N/A | 81
GEN-2020-002 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 81 | 81 | None | None | N/A | 81 | N/A | N/A | N/A | N/A | N/A | N/A | 81 | N/A
GEN-2020-002 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 81 | 81 | None | None | 81 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 81 | N/A
GEN-2020-002 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 81 | 81 | None | None | N/A | 81 | N/A | 81 | N/A | N/A | N/A | N/A | 81 | 81
GEN-2020-002 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 81 | 81 | None | None | 81 | N/A | N/A | 81 | N/A | N/A | N/A | N/A | 81 | 81
GEN-2020-003 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 58 | 58 | None | None | N/A | 58 | N/A | 58 | N/A | 58 | N/A | 58 | 58 | 58
GEN-2020-003 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 58 | 58 | None | None | 58 | N/A | N/A | 58 | 58 | N/A | N/A | 58 | 58 | 58
GEN-2020-003 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 58 | 58 | None | None | N/A | N/A | N/A | 58 | N/A | N/A | N/A | 58 | N/A | 58
GEN-2020-003 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 58 | 58 | None | None | N/A | N/A | N/A | 58 | N/A | N/A | N/A | 58 | N/A | 58
GEN-2020-003 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 58 | 58 | None | None | N/A | 58 | N/A | N/A | N/A | 58 | N/A | N/A | 58 | N/A
GEN-2020-003 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 58 | 58 | None | None | 58 | N/A | N/A | N/A | 58 | N/A | N/A | N/A | 58 | N/A
GEN-2020-003 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 58 | 58 | None | None | N/A | 58 | N/A | 58 | N/A | 58 | N/A | 58 | 58 | 58
GEN-2020-003 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 58 | 58 | None | None | 58 | N/A | N/A | 58 | 58 | N/A | N/A | 58 | 58 | 58
GEN-2020-007 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 650 | 650 | None | None | N/A | 650 | N/A | 650 | N/A | 372.8564 | N/A | 415.448 | 650 | 650
GEN-2020-007 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 650 | 650 | None | None | 650 | N/A | N/A | 650 | 380.549 | N/A | N/A | 415.448 | 650 | 650
GEN-2020-007 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 650 | 650 | None | None | N/A | N/A | N/A | 650 | N/A | N/A | N/A | 415.448 | N/A | 650
GEN-2020-007 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 650 | 650 | None | None | N/A | N/A | N/A | 650 | N/A | N/A | N/A | 415.448 | N/A | 650
GEN-2020-007 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 650 | 650 | None | None | N/A | 650 | N/A | N/A | N/A | 372.8564 | N/A | N/A | 650 | N/A
GEN-2020-007 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 650 | 650 | None | None | 650 | N/A | N/A | N/A | 380.549 | N/A | N/A | N/A | 650 | N/A
GEN-2020-007 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 650 | 650 | None | None | N/A | 650 | N/A | 650 | N/A | 372.8564 | N/A | 415.448 | 650 | 650
GEN-2020-007 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 650 | 650 | None | None | 650 | N/A | N/A | 650 | 380.549 | N/A | N/A | 415.448 | 650 | 650
GEN-2020-008 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2020-008 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2020-008 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2020-008 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | N/A | N/A | 250
GEN-2020-008 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2020-008 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 250 | N/A
GEN-2020-008 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2020-008 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | N/A | N/A | N/A | N/A | 250 | 250
GEN-2020-010 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Long Term) | 140 | 140 | None | None | N/A | 140 | N/A | 140 | N/A | 140 | N/A | 140 | 140 | 140
GEN-2020-010 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Near Term) | 140 | 140 | None | None | 140 | N/A | N/A | 140 | 140 | N/A | N/A | 140 | 140 | 140
GEN-2020-010 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Long Term) | 140 | 140 | None | None | N/A | N/A | N/A | 140 | N/A | N/A | N/A | 140 | N/A | 140
GEN-2020-010 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Near Term) | 140 | 140 | None | None | N/A | N/A | N/A | 140 | N/A | N/A | N/A | 140 | N/A | 140
GEN-2020-010 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Long Term) | 140 | 140 | None | None | N/A | 140 | N/A | N/A | N/A | 140 | N/A | N/A | 140 | N/A
GEN-2020-010 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Near Term) | 140 | 140 | None | None | 140 | N/A | N/A | N/A | 140 | N/A | N/A | N/A | 140 | N/A
GEN-2020-010 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Long Term) | 140 | 140 | None | None | N/A | 140 | N/A | 140 | N/A | 140 | N/A | 140 | 140 | 140
GEN-2020-010 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Near Term) | 140 | 140 | None | None | 140 | N/A | N/A | 140 | 140 | N/A | N/A | 140 | 140 | 140
GEN-2020-011 | 02 NEBRASKA | Hybrid | April 1 - May 31 (Long Term) | 320 | 320 | None | None | N/A | 320 | N/A | 320 | N/A | 320 | N/A | 320 | 320 | 320
GEN-2020-011 | 02 NEBRASKA | Hybrid | April 1 - May 31 (Near Term) | 320 | 320 | None | None | 320 | N/A | N/A | 320 | 320 | N/A | N/A | 320 | 320 | 320
GEN-2020-011 | 02 NEBRASKA | Hybrid | Dec 1 - March 31 (Long Term) | 320 | 320 | None | None | N/A | N/A | N/A | 320 | N/A | N/A | N/A | 320 | N/A | 320
GEN-2020-011 | 02 NEBRASKA | Hybrid | Dec 1 - March 31 (Near Term) | 320 | 320 | None | None | N/A | N/A | N/A | 320 | N/A | N/A | N/A | 320 | N/A | 320
GEN-2020-011 | 02 NEBRASKA | Hybrid | June 1 - Sept 30 (Long Term) | 320 | 320 | None | None | N/A | 320 | N/A | N/A | N/A | 320 | N/A | N/A | 320 | N/A
GEN-2020-011 | 02 NEBRASKA | Hybrid | June 1 - Sept 30 (Near Term) | 320 | 320 | None | None | 320 | N/A | N/A | N/A | 320 | N/A | N/A | N/A | 320 | N/A
GEN-2020-011 | 02 NEBRASKA | Hybrid | Oct 1 - Nov 30 (Long Term) | 320 | 320 | None | None | N/A | 320 | N/A | 320 | N/A | 320 | N/A | 320 | 320 | 320
GEN-2020-011 | 02 NEBRASKA | Hybrid | Oct 1 - Nov 30 (Near Term) | 320 | 320 | None | None | 320 | N/A | N/A | 320 | 320 | N/A | N/A | 320 | 320 | 320
GEN-2020-012 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Long Term) | 113 | 113 | None | None | N/A | 113 | N/A | 113 | N/A | 113 | N/A | 113 | 113 | 113
GEN-2020-012 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Near Term) | 113 | 113 | None | None | 113 | N/A | N/A | 113 | 113 | N/A | N/A | 113 | 113 | 113
GEN-2020-012 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Long Term) | 113 | 113 | None | None | N/A | N/A | N/A | 113 | N/A | N/A | N/A | 113 | N/A | 113
GEN-2020-012 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Near Term) | 113 | 113 | None | None | N/A | N/A | N/A | 113 | N/A | N/A | N/A | 113 | N/A | 113
GEN-2020-012 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Long Term) | 113 | 113 | None | None | N/A | 113 | N/A | N/A | N/A | 113 | N/A | N/A | 113 | N/A
GEN-2020-012 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Near Term) | 113 | 113 | None | None | 113 | N/A | N/A | N/A | 113 | N/A | N/A | N/A | 113 | N/A
GEN-2020-012 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Long Term) | 113 | 113 | None | None | N/A | 113 | N/A | 113 | N/A | 113 | N/A | 113 | 113 | 113
GEN-2020-012 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Near Term) | 113 | 113 | None | None | 113 | N/A | N/A | 113 | 113 | N/A | N/A | 113 | 113 | 113
GEN-2020-013 | 02 NEBRASKA | Hybrid | April 1 - May 31 (Long Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | N/A | 124.22 | N/A | 124.196 | N/A | 124.22 | N/A | 124.184 | 215 | 215
GEN-2020-013 | 02 NEBRASKA | Hybrid | April 1 - May 31 (Near Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | 124.208 | N/A | N/A | 124.196 | 124.232 | N/A | N/A | 124.184 | 215 | 215
GEN-2020-013 | 02 NEBRASKA | Hybrid | Dec 1 - March 31 (Long Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | N/A | N/A | N/A | 124.196 | N/A | N/A | N/A | 124.184 | N/A | 215
GEN-2020-013 | 02 NEBRASKA | Hybrid | Dec 1 - March 31 (Near Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | N/A | N/A | N/A | 124.196 | N/A | N/A | N/A | 124.184 | N/A | 215
GEN-2020-013 | 02 NEBRASKA | Hybrid | June 1 - Sept 30 (Long Term) | 215 | 124.22 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | N/A | 124.22 | N/A | N/A | N/A | 124.22 | N/A | N/A | 215 | N/A
GEN-2020-013 | 02 NEBRASKA | Hybrid | June 1 - Sept 30 (Near Term) | 215 | 124.232 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | 124.208 | N/A | N/A | N/A | 124.232 | N/A | N/A | N/A | 215 | N/A
GEN-2020-013 | 02 NEBRASKA | Hybrid | Oct 1 - Nov 30 (Long Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | N/A | 124.22 | N/A | 124.196 | N/A | 124.22 | N/A | 124.184 | 215 | 215
GEN-2020-013 | 02 NEBRASKA | Hybrid | Oct 1 - Nov 30 (Near Term) | 215 | 124.196 | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 ftlo 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | 124.208 | N/A | N/A | 124.196 | 124.232 | N/A | N/A | 124.184 | 215 | 215
GEN-2020-014 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 45 | 45 | None | None | N/A | 45 | N/A | 45 | N/A | 45 | N/A | 45 | 45 | 45
GEN-2020-014 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 45 | 45 | None | None | N/A | N/A | N/A | 45 | N/A | N/A | N/A | 45 | 45 | 45
GEN-2020-014 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 45 | 45 | None | None | N/A | N/A | N/A | 45 | N/A | N/A | N/A | 45 | N/A | 45
GEN-2020-014 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 45 | 45 | None | None | N/A | N/A | N/A | 45 | N/A | N/A | N/A | 45 | N/A | 45
GEN-2020-014 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 45 | 45 | None | None | N/A | 45 | N/A | N/A | N/A | 45 | N/A | N/A | 45 | N/A
GEN-2020-014 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 45 | 45 | None | None | 45 | N/A | N/A | N/A | 45 | N/A | N/A | N/A | 45 | N/A
GEN-2020-014 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 45 | 45 | None | None | N/A | 45 | N/A | 45 | N/A | 45 | N/A | 45 | 45 | 45
GEN-2020-014 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 45 | 45 | None | None | 45 | N/A | N/A | 45 | 45 | N/A | N/A | 45 | 45 | 45
GEN-2020-020 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 201.6
GEN-2020-020 | 04 SOUTHEAST | Hybrid | April 1 - May 31 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 201.6
GEN-2020-020 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Long Term) | 201.6 | 201.6 | None | None | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 201.6
GEN-2020-020 | 04 SOUTHEAST | Hybrid | Dec 1 - March 31 (Near Term) | 201.6 | 201.6 | None | None | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | 201.6
GEN-2020-020 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | 201.6 | N/A
GEN-2020-020 | 04 SOUTHEAST | Hybrid | June 1 - Sept 30 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | N/A | 201.6 | N/A | N/A | N/A | 201.6 | N/A
GEN-2020-020 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Long Term) | 201.6 | 201.6 | None | None | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | N/A | 201.6 | 201.6 | 201.6
GEN-2020-020 | 04 SOUTHEAST | Hybrid | Oct 1 - Nov 30 (Near Term) | 201.6 | 201.6 | None | None | 201.6 | N/A | N/A | 201.6 | 201.6 | N/A | N/A | 201.6 | 201.6 | 201.6
GEN-2020-021 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 235 | 235 | None | None | N/A | N/A | 149.4414 | N/A | N/A | N/A | 235 | N/A | 235 | 235
GEN-2020-021 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 235 | 235 | None | None | N/A | N/A | 149.4414 | N/A | N/A | N/A | 235 | N/A | 235 | 235
GEN-2020-021 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 235 | 235 | None | None | N/A | N/A | N/A | 235 | N/A | N/A | N/A | 235 | N/A | 235
GEN-2020-021 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 235 | 235 | None | None | N/A | N/A | N/A | 235 | N/A | N/A | N/A | 235 | N/A | 235
GEN-2020-021 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 235 | 235 | None | None | N/A | 235 | N/A | N/A | N/A | 235 | N/A | N/A | 235 | N/A
GEN-2020-021 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 235 | 235 | None | None | 235 | N/A | N/A | N/A | 235 | N/A | N/A | N/A | 235 | N/A
GEN-2020-021 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 235 | 235 | None | None | N/A | N/A | 149.4414 | N/A | N/A | N/A | 235 | N/A | 235 | 235
GEN-2020-021 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 235 | 235 | None | None | N/A | N/A | 149.4414 | N/A | N/A | N/A | 235 | N/A | 235 | 235
GEN-2020-025 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-025 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-025 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 255
GEN-2020-025 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 255
GEN-2020-025 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | N/A | N/A | N/A | N/A | N/A | 255 | N/A
GEN-2020-025 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 255 | N/A
GEN-2020-025 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-025 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 255 | 255 | None | None | N/A | N/A | N/A | 255 | N/A | N/A | N/A | N/A | N/A | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | N/A | N/A | N/A | N/A | N/A | 255 | N/A
GEN-2020-028 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 255 | N/A
GEN-2020-028 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 255 | 255 | None | None | N/A | 255 | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-028 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 255 | 255 | None | None | 255 | N/A | N/A | 255 | N/A | N/A | N/A | N/A | 255 | 255
GEN-2020-031 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-031 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-031 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 272.7 | 272.7 | None | None | N/A | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | N/A | 272.7
GEN-2020-031 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 272.7 | 272.7 | None | None | N/A | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | N/A | 272.7
GEN-2020-031 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | N/A | N/A | N/A | N/A | N/A | 272.7 | N/A
GEN-2020-031 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 272.7 | N/A
GEN-2020-031 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-031 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 272.7 | 272.7 | None | None | N/A | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | N/A | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 272.7 | 272.7 | None | None | N/A | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | N/A | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | N/A | N/A | N/A | N/A | N/A | 272.7 | N/A
GEN-2020-038 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 272.7 | N/A
GEN-2020-038 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 272.7 | 258 | None | None | N/A | 258 | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-038 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 272.7 | 258 | None | None | 258 | N/A | N/A | 272.7 | N/A | N/A | N/A | N/A | 272.7 | 272.7
GEN-2020-043 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-043 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-043 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-043 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-043 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-043 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-043 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-043 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-044 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-044 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-044 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 56.52 | 56.52 | None | None | N/A | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-045 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 56.52 | N/A
GEN-2020-045 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 56.52 | 56.52 | None | None | N/A | 56.52 | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-045 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 56.52 | 56.52 | None | None | 56.52 | N/A | N/A | 56.52 | N/A | N/A | N/A | N/A | 56.52 | 56.52
GEN-2020-054 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 298 | 298 | None | None | N/A | 298 | N/A | 298 | N/A | 298 | N/A | 298 | 298 | 298
GEN-2020-054 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 298 | 298 | None | None | 298 | N/A | N/A | 298 | 298 | N/A | N/A | 298 | 298 | 298
GEN-2020-054 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 298 | 298 | None | None | N/A | N/A | N/A | 298 | N/A | N/A | N/A | 298 | N/A | 298
GEN-2020-054 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 298 | 298 | None | None | N/A | N/A | N/A | 298 | N/A | N/A | N/A | 298 | N/A | 298
GEN-2020-054 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 298 | 298 | None | None | N/A | 298 | N/A | N/A | N/A | 298 | N/A | N/A | 298 | N/A
GEN-2020-054 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 298 | 298 | None | None | 298 | N/A | N/A | N/A | 298 | N/A | N/A | N/A | 298 | N/A
GEN-2020-054 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 298 | 298 | None | None | N/A | 298 | N/A | 298 | N/A | 298 | N/A | 298 | 298 | 298
GEN-2020-054 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 298 | 298 | None | None | 298 | N/A | N/A | 298 | 298 | N/A | N/A | 298 | 298 | 298
GEN-2020-056 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 20 | 20 | None | None | N/A | 20 | N/A | 20 | N/A | 20 | N/A | 20 | 20 | 20
GEN-2020-056 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 20 | 20 | None | None | 20 | N/A | N/A | 20 | 20 | N/A | N/A | 20 | 20 | 20
GEN-2020-056 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 20 | 20 | None | None | N/A | N/A | N/A | 20 | N/A | N/A | N/A | 20 | N/A | 20
GEN-2020-056 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 20 | 20 | None | None | N/A | N/A | N/A | 20 | N/A | N/A | N/A | 20 | N/A | 20
GEN-2020-056 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 20 | 20 | None | None | N/A | 20 | N/A | N/A | N/A | 20 | N/A | N/A | 20 | N/A
GEN-2020-056 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 20 | 20 | None | None | 20 | N/A | N/A | N/A | 20 | N/A | N/A | N/A | 20 | N/A
GEN-2020-056 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 20 | 20 | None | None | N/A | 20 | N/A | 20 | N/A | 20 | N/A | 20 | 20 | 20
GEN-2020-056 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 20 | 20 | None | None | 20 | N/A | N/A | 20 | 20 | N/A | N/A | 20 | 20 | 20
GEN-2020-057 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | 424.5 | N/A | 323.9409 | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-057 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | 424.5 | 156.6198 | N/A | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-057 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 424.5 | 424.5 | None | None | N/A | N/A | N/A | 424.5 | N/A | N/A | N/A | 341.6283 | N/A | 424.5
GEN-2020-057 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 424.5 | 424.5 | None | None | N/A | N/A | N/A | 424.5 | N/A | N/A | N/A | 341.6283 | N/A | 424.5
GEN-2020-057 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | N/A | N/A | 323.9409 | N/A | N/A | 424.5 | N/A
GEN-2020-057 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | N/A | 156.6198 | N/A | N/A | N/A | 424.5 | N/A
GEN-2020-057 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | 424.5 | N/A | 323.9409 | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-057 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | 424.5 | 156.6198 | N/A | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | 424.5 | N/A | 323.9409 | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | 424.5 | 156.6198 | N/A | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 424.5 | 424.5 | None | None | N/A | N/A | N/A | 424.5 | N/A | N/A | N/A | 341.6283 | N/A | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 424.5 | 424.5 | None | None | N/A | N/A | N/A | 424.5 | N/A | N/A | N/A | 341.6283 | N/A | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | N/A | N/A | 323.9409 | N/A | N/A | 424.5 | N/A
GEN-2020-058 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | N/A | 156.6198 | N/A | N/A | N/A | 424.5 | N/A
GEN-2020-058 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 424.5 | 424.5 | None | None | N/A | 424.5 | N/A | 424.5 | N/A | 323.9409 | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-058 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 424.5 | 424.5 | None | None | 424.5 | N/A | N/A | 424.5 | 156.6198 | N/A | N/A | 341.6283 | 424.5 | 424.5
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | 200 | N/A | 98.6948 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | 185.4485 | N/A | N/A | 98.6948 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | N/A | 98.6948 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | N/A | 98.6948 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | 200 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | 185.4485 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | 200 | N/A | 98.6948 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-060 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | 185.4485 | N/A | N/A | 98.6948 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-061 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 29 | 29 | None | None | N/A | 29 | N/A | 29 | N/A | 29 | N/A | 29 | 29 | 29
GEN-2020-061 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 29 | 29 | None | None | 29 | N/A | N/A | 29 | 29 | N/A | N/A | 29 | 29 | 29
GEN-2020-061 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 29 | 29 | None | None | N/A | N/A | N/A | 29 | N/A | N/A | N/A | 29 | N/A | 29
GEN-2020-061 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 29 | 29 | None | None | N/A | N/A | N/A | 29 | N/A | N/A | N/A | 29 | N/A | 29
GEN-2020-061 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 29 | 29 | None | None | N/A | 29 | N/A | N/A | N/A | 29 | N/A | N/A | 29 | N/A
GEN-2020-061 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 29 | 29 | None | None | 29 | N/A | N/A | N/A | 29 | N/A | N/A | N/A | 29 | N/A
GEN-2020-061 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 29 | 29 | None | None | N/A | 29 | N/A | 29 | N/A | 29 | N/A | 29 | 29 | 29
GEN-2020-061 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 29 | 29 | None | None | 29 | N/A | N/A | 29 | 29 | N/A | N/A | 29 | 29 | 29
GEN-2020-064 | 03 CENTRAL | Thermal | April 1 - May 31 (Long Term) | 64 | 64 | None | None | N/A | 64 | N/A | 64 | N/A | 64 | N/A | 64 | 64 | 64
GEN-2020-064 | 03 CENTRAL | Thermal | April 1 - May 31 (Near Term) | 64 | 64 | None | None | 64 | N/A | N/A | 64 | 64 | N/A | N/A | 64 | 64 | 64
GEN-2020-064 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Long Term) | 64 | 64 | None | None | N/A | N/A | N/A | 64 | N/A | N/A | N/A | 64 | N/A | 64
GEN-2020-064 | 03 CENTRAL | Thermal | Dec 1 - March 31 (Near Term) | 64 | 64 | None | None | N/A | N/A | N/A | 64 | N/A | N/A | N/A | 64 | N/A | 64
GEN-2020-064 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Long Term) | 64 | 64 | None | None | N/A | 64 | N/A | N/A | N/A | 64 | N/A | N/A | 64 | N/A
GEN-2020-064 | 03 CENTRAL | Thermal | June 1 - Sept 30 (Near Term) | 64 | 64 | None | None | 64 | N/A | N/A | N/A | 64 | N/A | N/A | N/A | 64 | N/A
GEN-2020-064 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Long Term) | 64 | 64 | None | None | N/A | 64 | N/A | 64 | N/A | 64 | N/A | 64 | 64 | 64
GEN-2020-064 | 03 CENTRAL | Thermal | Oct 1 - Nov 30 (Near Term) | 64 | 64 | None | None | 64 | N/A | N/A | 64 | 64 | N/A | N/A | 64 | 64 | 64
GEN-2020-065 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | N/A | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-065 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | 0 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-065 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-065 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-065 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-065 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-065 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | N/A | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-065 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 1003 | 0 | Non-Convergence/Stability | Build New Andrews to Road Runner 345 kV Line | 0 | N/A | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | 352.5 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | 352.5 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | N/A | 173.9495 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | N/A | 173.9495 | N/A | N/A | N/A | N/A | N/A | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | 352.5 | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-067 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | 326.853 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0 | N/A
GEN-2020-067 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | 352.5 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-067 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 352.5 | 0 | Stability | Build New Phantom to Crossroads to Potter 765 kV Line Build New Beckham to Potter 345 kV Line | N/A | N/A | 352.5 | N/A | N/A | N/A | N/A | N/A | 0 | 0
GEN-2020-072 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-072 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-072 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-072 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-072 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2020-072 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2020-072 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-072 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-078 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2020-078 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2020-078 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2020-078 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2020-078 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | 100 | N/A
GEN-2020-078 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A
GEN-2020-078 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2020-078 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2020-079 | 03 CENTRAL | Hybrid | April 1 - May 31 (Long Term) | 225 | 225 | None | None | N/A | 225 | N/A | 225 | N/A | 225 | N/A | 225 | 225 | 225
GEN-2020-079 | 03 CENTRAL | Hybrid | April 1 - May 31 (Near Term) | 225 | 225 | None | None | 225 | N/A | N/A | 225 | 225 | N/A | N/A | 225 | 225 | 225
GEN-2020-079 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Long Term) | 225 | 225 | None | None | N/A | N/A | N/A | 225 | N/A | N/A | N/A | 225 | N/A | 225
GEN-2020-079 | 03 CENTRAL | Hybrid | Dec 1 - March 31 (Near Term) | 225 | 225 | None | None | N/A | N/A | N/A | 225 | N/A | N/A | N/A | 225 | N/A | 225
GEN-2020-079 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Long Term) | 225 | 225 | None | None | N/A | 225 | N/A | N/A | N/A | 225 | N/A | N/A | 225 | N/A
GEN-2020-079 | 03 CENTRAL | Hybrid | June 1 - Sept 30 (Near Term) | 225 | 225 | None | None | 225 | N/A | N/A | N/A | 225 | N/A | N/A | N/A | 225 | N/A
GEN-2020-079 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Long Term) | 225 | 225 | None | None | N/A | 225 | N/A | 225 | N/A | 225 | N/A | 225 | 225 | 225
GEN-2020-079 | 03 CENTRAL | Hybrid | Oct 1 - Nov 30 (Near Term) | 225 | 225 | None | None | 225 | N/A | N/A | 225 | 225 | N/A | N/A | 225 | 225 | 225
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | None | None | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A | 200
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | N/A | N/A | 200 | N/A | N/A | 200 | N/A
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | N/A | 200 | N/A | N/A | N/A | 200 | N/A
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | None | None | N/A | 200 | N/A | 200 | N/A | 200 | N/A | 200 | 200 | 200
GEN-2020-081 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | None | None | 200 | N/A | N/A | 200 | 200 | N/A | N/A | 200 | 200 | 200
GEN-2020-083 | 01 NORTH | Hybrid | April 1 - May 31 (Long Term) | 74.5 | 74.5 | None | None | N/A | 74.5 | N/A | 74.5 | N/A | 74.5 | N/A | 0 | 74.5 | 74.5
GEN-2020-083 | 01 NORTH | Hybrid | April 1 - May 31 (Near Term) | 74.5 | 74.5 | None | None | 74.5 | N/A | N/A | 74.5 | 74.5 | N/A | N/A | 0 | 74.5 | 74.5
GEN-2020-083 | 01 NORTH | Hybrid | Dec 1 - March 31 (Long Term) | 74.5 | 74.5 | None | None | N/A | N/A | N/A | 74.5 | N/A | N/A | N/A | 0 | N/A | 74.5
GEN-2020-083 | 01 NORTH | Hybrid | Dec 1 - March 31 (Near Term) | 74.5 | 74.5 | None | None | N/A | N/A | N/A | 74.5 | N/A | N/A | N/A | 0 | N/A | 74.5
GEN-2020-083 | 01 NORTH | Hybrid | June 1 - Sept 30 (Long Term) | 74.5 | 74.5 | None | None | N/A | 74.5 | N/A | N/A | N/A | 74.5 | N/A | N/A | 74.5 | N/A
GEN-2020-083 | 01 NORTH | Hybrid | June 1 - Sept 30 (Near Term) | 74.5 | 74.5 | None | None | 74.5 | N/A | N/A | N/A | 74.5 | N/A | N/A | N/A | 74.5 | N/A
GEN-2020-083 | 01 NORTH | Hybrid | Oct 1 - Nov 30 (Long Term) | 74.5 | 74.5 | None | None | N/A | 74.5 | N/A | 74.5 | N/A | 74.5 | N/A | 0 | 74.5 | 74.5
GEN-2020-083 | 01 NORTH | Hybrid | Oct 1 - Nov 30 (Near Term) | 74.5 | 74.5 | None | None | 74.5 | N/A | N/A | 74.5 | 74.5 | N/A | N/A | 0 | 74.5 | 74.5
GEN-2020-084 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 350 | 350 | None | None | N/A | 328.5257 | N/A | 307.1236 | N/A | 350 | N/A | 350 | 350 | 350
GEN-2020-084 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 350 | 350 | None | None | 348.5035 | N/A | N/A | 307.1236 | 350 | N/A | N/A | 350 | 350 | 350
GEN-2020-084 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 350 | 350 | None | None | N/A | N/A | N/A | 307.1236 | N/A | N/A | N/A | 350 | N/A | 350
GEN-2020-084 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 350 | 350 | None | None | N/A | N/A | N/A | 307.1236 | N/A | N/A | N/A | 350 | N/A | 350
GEN-2020-084 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 350 | 350 | None | None | N/A | 328.5257 | N/A | N/A | N/A | 350 | N/A | N/A | 350 | N/A
GEN-2020-084 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 350 | 350 | None | None | 348.5035 | N/A | N/A | N/A | 350 | N/A | N/A | N/A | 350 | N/A
GEN-2020-084 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 350 | 350 | None | None | N/A | 328.5257 | N/A | 307.1236 | N/A |  | N/A | 350 | 350 | 350
GEN-2020-084 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 350 | 350 | None | None | 348.5035 | N/A | N/A | 307.1236 | 350 | N/A | N/A | 350 | 350 | 350
GEN-2020-087 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 500 | 500 | None | None | N/A | 500 | N/A | 500 | N/A | 500 | N/A | 500 | 500 | 500
GEN-2020-087 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 500 | 500 | None | None | 500 | N/A | N/A | 500 | 500 | N/A | N/A | 500 | 500 | 500
GEN-2020-087 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 500 | 500 | None | None | N/A | N/A | N/A | 500 | N/A | N/A | N/A | 500 | N/A | 500
GEN-2020-087 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 500 | 500 | None | None | N/A | N/A | N/A | 500 | N/A | N/A | N/A | 500 | N/A | 500
GEN-2020-087 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 500 | 500 | None | None | N/A | 500 | N/A | N/A | N/A | 500 | N/A | N/A | 500 | N/A
GEN-2020-087 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 500 | 500 | None | None | 500 | N/A | N/A | N/A | 500 | N/A | N/A | N/A | 500 | N/A
GEN-2020-087 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 500 | 500 | None | None | N/A | 500 | N/A | 500 | N/A | 500 | N/A | 500 | 500 | 500
GEN-2020-087 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 500 | 500 | None | None | 500 | N/A | N/A | 500 | 500 | N/A | N/A | 500 | 500 | 500
GEN-2020-088 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-088 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-088 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-088 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-088 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2020-088 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2020-088 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-088 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-090 | 03 CENTRAL | Storage | April 1 - May 31 (Long Term) | 204.3 | 204.3 | None | None | N/A | 204.3 | N/A | 204.3 | N/A | 204.3 | N/A | 204.3 | 204.3 | 204.3
GEN-2020-090 | 03 CENTRAL | Storage | April 1 - May 31 (Near Term) | 204.3 | 204.3 | None | None | 204.3 | N/A | N/A | 204.3 | 204.3 | N/A | N/A | 204.3 | 204.3 | 204.3
GEN-2020-090 | 03 CENTRAL | Storage | Dec 1 - March 31 (Long Term) | 204.3 | 204.3 | None | None | N/A | N/A | N/A | 204.3 | N/A | N/A | N/A | 204.3 | N/A | 204.3
GEN-2020-090 | 03 CENTRAL | Storage | Dec 1 - March 31 (Near Term) | 204.3 | 204.3 | None | None | N/A | N/A | N/A | 204.3 | N/A | N/A | N/A | 204.3 | N/A | 204.3
GEN-2020-090 | 03 CENTRAL | Storage | June 1 - Sept 30 (Long Term) | 204.3 | 204.3 | None | None | N/A | 204.3 | N/A | N/A | N/A | 204.3 | N/A | N/A | 204.3 | N/A
GEN-2020-090 | 03 CENTRAL | Storage | June 1 - Sept 30 (Near Term) | 204.3 | 204.3 | None | None | 204.3 | N/A | N/A | N/A | 204.3 | N/A | N/A | N/A | 204.3 | N/A
GEN-2020-090 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Long Term) | 204.3 | 204.3 | None | None | N/A | 204.3 | N/A | 204.3 | N/A | 204.3 | N/A | 204.3 | 204.3 | 204.3
GEN-2020-090 | 03 CENTRAL | Storage | Oct 1 - Nov 30 (Near Term) | 204.3 | 204.3 | None | None | 204.3 | N/A | N/A | 204.3 | 204.3 | N/A | N/A | 204.3 | 204.3 | 204.3
GEN-2020-091 | 01 NORTH | Solar | April 1 - May 31 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-091 | 01 NORTH | Solar | April 1 - May 31 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-091 | 01 NORTH | Solar | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-091 | 01 NORTH | Solar | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A | 150
GEN-2020-091 | 01 NORTH | Solar | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | N/A | N/A | 150 | N/A | N/A | 150 | N/A
GEN-2020-091 | 01 NORTH | Solar | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | N/A | 150 | N/A | N/A | N/A | 150 | N/A
GEN-2020-091 | 01 NORTH | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | N/A | 150 | N/A | 150 | N/A | 150 | N/A | 150 | 150 | 150
GEN-2020-091 | 01 NORTH | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 150 | None | None | 150 | N/A | N/A | 150 | 150 | N/A | N/A | 150 | 150 | 150
GEN-2020-092 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2020-092 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2020-092 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100
GEN-2020-092 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 100 | 100 | None | None | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A | 100
GEN-2020-092 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | N/A | N/A | 100 | N/A | N/A | 100 | N/A
GEN-2020-092 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | N/A | 100 | N/A | N/A | N/A | 100 | N/A
GEN-2020-092 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 100 | 100 | None | None | N/A | 100 | N/A | 100 | N/A | 100 | N/A | 100 | 100 | 100
GEN-2020-092 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 100 | 100 | None | None | 100 | N/A | N/A | 100 | 100 | N/A | N/A | 100 | 100 | 100
GEN-2020-094 | 02 NEBRASKA | Solar | April 1 - May 31 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 0 | 250 | 250
GEN-2020-094 | 02 NEBRASKA | Solar | April 1 - May 31 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 250 | N/A | N/A | 0 | 250 | 250
GEN-2020-094 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Long Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 0 | N/A | 250
GEN-2020-094 | 02 NEBRASKA | Solar | Dec 1 - March 31 (Near Term) | 250 | 250 | None | None | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 0 | N/A | 250
GEN-2020-094 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | N/A | N/A | 250 | N/A | N/A | 250 | N/A
GEN-2020-094 | 02 NEBRASKA | Solar | June 1 - Sept 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | N/A | 250 | N/A | N/A | N/A | 250 | N/A
GEN-2020-094 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 250 | None | None | N/A | 250 | N/A | 250 | N/A | 250 | N/A | 0 | 250 | 250
GEN-2020-094 | 02 NEBRASKA | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 250 | None | None | 250 | N/A | N/A | 250 | 250 | N/A | N/A | 0 | 250 | 250

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | DISIS-2020-001 | ERIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | [7 empty] | Build New Andrews to Road Runner 345 kV Line
00ALL | DISIS-2020-001 | ERIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | [7 empty] | Hobbs to Andrews Voltage Conversion
00NR | DISIS-2020-001 | NRIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2020-001 | ERIS | Non-Converged | None | 24SP, 27SP, 27WP, 27L | None | [7 empty] | None
01ALL | DISIS-2020-001 CF | ERIS | Non-Converged | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
01NR | DISIS-2020-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
01NR | DISIS-2020-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
02ALL | DISIS-2020-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02ALL | DISIS-2020-001 CF | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02NR | DISIS-2020-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
02NR | DISIS-2020-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
03ALL | DISIS-2020-001 | ERIS | Non-Converged | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
03ALL | DISIS-2020-001 CF | ERIS | Non-Converged | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
03NR | DISIS-2020-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
03NR | DISIS-2020-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
04ALL | DISIS-2020-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | DISIS-2020-001 CF | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | DISIS-2020-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | DISIS-2020-001 CF | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2020-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
01ALL | DISIS-2020-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | DISIS-2020-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | DISIS-2020-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
03ALL | DISIS-2020-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | DISIS-2020-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
04ALL | DISIS-2020-001 CF | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
00ALL | DISIS-2020-001 | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_CION7384:::: |  | 234 | <90% | 103.87 |  |  |  | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
00ALL | DISIS-2020-001 | ERIS | Thermal | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 545 | <90% | 165.23 |  |  |  | Sidewinder to Andrews 345 kV Lidar Clearance Correction
00ALL | DISIS-2020-001 | ERIS | Thermal | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | 24SP, 27SP, 27WP | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 797 | <90% | 124.12 |  |  |  | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
00NR | DISIS-2020-001 CF | NRIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2020-001 | NRIS | Thermal | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 24SP, 27SP | 541198 PECULR 7 345 542968 STILWEL7 345 1 | 311 | 334 | <90% | 101.71 |  |  |  | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
00NR | DISIS-2020-001 | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 24SP | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | 311 | 334 | 95.17 | 109.61 |  |  |  | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2
00NR | DISIS-2020-001 CF | NRIS | Thermal | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 27SP, 27WP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 535 | 535 | <90% | 108.05 |  |  |  | Multi - Atlantic - Craig - West Gardener 345-115 kV
00NR | DISIS-2020-001 CF | NRIS | Thermal | 542965 W.GRDNR7 345 997280 WEST GARDN11 161 11 | 24SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 535 | 535 | <90% | 107.89 |  |  |  | Multi - Atlantic - Craig - West Gardener 345-115 kV
00NR | DISIS-2020-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 24SP, 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 334 | 334 | <90% | 107.68 |  |  |  | Multi - Atlantic - Craig - West Gardener 345-115 kV
00NR | DISIS-2020-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 997277 WEST GARDN11 161 11 | 27WP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 535 | 535 | <90% | 107.7 |  |  |  | Multi - Atlantic - Craig - West Gardener 345-115 kV
00NR | DISIS-2020-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 997280 WEST GARDN11 161 11 | 24SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 535 | 535 | <90% | 107.89 |  |  |  | Multi - Atlantic - Craig - West Gardener 345-115 kV
00NR | DISIS-2020-001 CF | NRIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | System Intact | 120 | 120 | <90% | 164.01 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
00NR | DISIS-2020-001 CF | NRIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | 120 | 120 | <90% | 175.68 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
00NR | DISIS-2020-001 CF | NRIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | 120 | 120 | <90% | 175.68 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
00NR | DISIS-2020-001 CF | NRIS | Thermal | 640277 MOORE 3 345 996875 MOORE T1 115 1 | 27WP | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1:: | 336 | 336 | 111.13 | 115.76 |  |  |  | Replace Mark Moore 345/115 kV Transformer
00NR | DISIS-2020-001 CF | NRIS | Thermal | 640278 SHELDON7 115 996875 MOORE T1 115 1 | 27WP | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1:: | 336 | 336 | 103.74 | 108.08 |  |  |  | Replace Mark Moore 345/115 kV Transformer
00NR | DISIS-2020-001 CF | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 27WP | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | 342 | 342 | 110.03 | 106.45 |  |  |  | Fargo 230 kV Terminal Upgrade
00NR | DISIS-2020-001 CF | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 27WP | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | 342 | 342 | 110.03 | 106.45 |  |  |  | Fargo 230 kV Terminal Upgrade
01ALL | DISIS-2020-001 | ERIS | Thermal | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 250 | 313 | 103.24 | 104.84 |  |  |  | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
01ALL | DISIS-2020-001 | ERIS | Thermal | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 250 | 313 | 105.48 | 107.11 |  |  |  | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
01ALL | DISIS-2020-001 | ERIS | Thermal | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 250 | 313 | 102.87 | 105.07 |  |  |  | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
01ALL | DISIS-2020-001 | ERIS | Thermal | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | 250 | 313 | 105.1 | 107.34 |  |  |  | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
01ALL | DISIS-2020-001 | ERIS | Thermal | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2020-001 CF | ERIS | Thermal | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
01NR | DISIS-2020-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | DISIS-2020-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
02ALL | DISIS-2020-001 | ERIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | System Intact | 120 | 120 | <90% | 164.63 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
02ALL | DISIS-2020-001 | ERIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | 120 | 120 | <90% | 175.67 |  |  |  | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
02ALL | DISIS-2020-001 | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 27WP | P23:345:MEC:LEHIGH:360::: | 956 | 956 | <90% | 100.65 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2020-001 | ERIS | Thermal | None | 27L | None | [7 empty] | None
02NR | DISIS-2020-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
02NR | DISIS-2020-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
03ALL | DISIS-2020-001 | ERIS | Thermal | None | 27SP, 27L, 27WP | None | [7 empty] | None
03ALL | DISIS-2020-001 CF | ERIS | Thermal | None | 27L, 27WP | None | [7 empty] | None
03NR | DISIS-2020-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
03NR | DISIS-2020-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
04ALL | DISIS-2020-001 | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 27WP | 510419 PRY-JCT4 138 764160 G20-092-TAP 138 1 |  | 188 | 83.45 | 110.29 |  |  |  | Catoosa Terminal Upgrade (Model Correction)
04ALL | DISIS-2020-001 | ERIS | Thermal | None | 24SP, 27L, 27SP | None | [7 empty] | None
04ALL | DISIS-2020-001 CF | ERIS | Thermal | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04NR | DISIS-2020-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
04NR | DISIS-2020-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
05ALL | DISIS-2020-001 | ERIS | Thermal | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | DISIS-2020-001 CF | ERIS | Thermal | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05NR | DISIS-2020-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
05NR | DISIS-2020-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
00ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2020-001 | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2020-001 CF | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27SP, 27WP, 27L | None | [7 empty] | None
01ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
01NR | DISIS-2020-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
01NR | DISIS-2020-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
02ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02NR | DISIS-2020-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
02NR | DISIS-2020-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
03ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
03ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27SP, 27L, 27WP | None | [7 empty] | None
05ALL | DISIS-2020-001 | ERIS | Stability | Instability and non-dampening oscillations | 25S, 25W | 527020 SIDEWINDER 7 345 527086 HOBBS 345 1 | [7 empty] | Build New Andrews to Road Runner 345 kV Line
05ALL | DISIS-2020-001 | ERIS | Stability | Instability | 25S, 25W | P12_BORDER_____7__TUCO_INT___7 | [7 empty] | Build New Beckham to Potter 345 kV Line
05ALL | DISIS-2020-001 | ERIS | Stability | Instability | 25S, 25W | P12_BORDER_____7__TUCO_INT___7 | [7 empty] | Build New Phantom to Crossroads to Potter 765 kV Line
05ALL | DISIS-2020-001 CF | ERIS | Stability | Instability | 25W | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | [7 empty] | Multi - Border - Woodward 345 kV Tap
05ALL | DISIS-2020-001 CF | ERIS | Stability | Instability | 25W | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | [7 empty] | Potter County 345/230 kV Transformer Ckt 2
03NR | DISIS-2020-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
03NR | DISIS-2020-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
04ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04NR | DISIS-2020-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
04NR | DISIS-2020-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
05ALL | DISIS-2020-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | DISIS-2020-001 CF | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05NR | DISIS-2020-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
05NR | DISIS-2020-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2020-002 | DISIS-2020-001 | 02 NEBRASKA | 143682 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 0 | 100% | 0 | 1
GEN-2020-002 | DISIS-2020-001 | 02 NEBRASKA | 143683 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 0 | 100% | 0 | 1
GEN-2020-003 | DISIS-2020-001 | 03 CENTRAL | 156901 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 1750000 | 100% | 1750000 | 1
GEN-2020-003 | DISIS-2020-001 | 03 CENTRAL | 156902 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 180000 | 100% | 180000 | 1
GEN-2020-007 | DISIS-2020-001 CF | 03 CENTRAL | 158640, 158641, 158645, 158646, 158648, 159064 | NRIS | Multi - Atlantic - Craig - West Gardener 345-115 kV | Contingent | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. Install two new 345/115 transformers at Atlantic 115 kV substation. Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic â€“ Eudora Township 115 kV line. | 0 | 0% | 99066200 | N/A
GEN-2020-007 | DISIS-2020-001 | 03 CENTRAL | 156903 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 30372474 | 100% | 30372474 | 1
GEN-2020-007 | DISIS-2020-001 | 03 CENTRAL | 156904 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 1782995 | 100% | 1782995 | 1
GEN-2020-007 | DISIS-2020-001 | 03 CENTRAL | 170587 | NRIS | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | Current Study | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | 6828057.9282 | 52.54% | 12994970 | 0.03601
GEN-2020-008 | DISIS-2020-001 | 03 CENTRAL | 156895 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 2521943 | 100% | 2521943 | 1
GEN-2020-008 | DISIS-2020-001 | 03 CENTRAL | 156896 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 3277798 | 100% | 3277798 | 1
GEN-2020-010 | DISIS-2020-001 | 04 SOUTHEAST | 156960 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 6050000 | 100% | 6050000 | 1
GEN-2020-010 | DISIS-2020-001 | 04 SOUTHEAST | 156961 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 517000 | 100% | 517000 | 1
GEN-2020-011 | DISIS-2020-001 | 02 NEBRASKA | 156881 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV *Updated cost not available | 20300000 | 100% | 20300000 | 1
GEN-2020-011 | DISIS-2020-001 | 02 NEBRASKA | 156882 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV *Updated cost not available | 1000000 | 100% | 1000000 | 1
GEN-2020-012 | DISIS-2020-001 | 04 SOUTHEAST | 156966 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 15222455 | 100% | 15222455 | 1
GEN-2020-012 | DISIS-2020-001 | 04 SOUTHEAST | 156967 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 2983138 | 100% | 2983138 | 1
GEN-2020-013 | DISIS-2020-001 CF | 02 NEBRASKA | 170588 | NRIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Contingent | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA *Updated cost not available | 0 | 0% | 14500000 | N/A
GEN-2020-013 | DISIS-2020-001 | 02 NEBRASKA | 156939 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV *Updated cost not available | 9200000 | 100% | 9200000 | 1
GEN-2020-013 | DISIS-2020-001 | 02 NEBRASKA | 156940 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV *Updated cost not available | 700000 | 100% | 700000 | 1
GEN-2020-013 | DISIS-2020-001 | 02 NEBRASKA | 170588 | ERIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Current Study | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA *Updated cost not available | 14500000 | 100% | 14500000 | 0.9999
GEN-2020-014 | DISIS-2020-001 | 01 NORTH | 144258 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-014 | DISIS-2020-001 | 01 NORTH | 144259 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-020 | DISIS-2020-001 | 04 SOUTHEAST | 156974 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 5511711 | 100% | 5511711 | 1
GEN-2020-020 | DISIS-2020-001 | 04 SOUTHEAST | 156993 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 24835359 | 100% | 24835359 | 1
GEN-2020-021 | DISIS-2020-001 | 01 NORTH | 156922 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 28072797 | 100% | 28072797 | 1
GEN-2020-021 | DISIS-2020-001 | 01 NORTH | 156923 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 4272447 | 100% | 4272447 | 1
GEN-2020-021 | DISIS-2020-001 | 01 NORTH | 170610 | ERIS | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Current Study | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | 44600000 | 100% | 44600000 | 0.1815
GEN-2020-025 | DISIS-2020-001 | 02 NEBRASKA | 156388 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-025 | DISIS-2020-001 | 02 NEBRASKA | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-028, GEN-2020-031 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-028, GEN-2020-031, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 0 | 0% | 0 | 1
GEN-2020-028 | DISIS-2020-001 | 02 NEBRASKA | 156389 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-028 | DISIS-2020-001 | 02 NEBRASKA | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-028, GEN-2020-031 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-028, GEN-2020-031, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 0 | 0% | 0 | 1
GEN-2020-031 | DISIS-2020-001 | 02 NEBRASKA | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-028, GEN-2020-031 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-028, GEN-2020-031, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 876856 | 100% | 876856 | 1
GEN-2020-031 | DISIS-2020-001 | 02 NEBRASKA | 156968 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (272.7/Thermal), into the Point of Interconnection (POI) at Substation 1363 161kV Substation | 5000000 | 100% | 5000000 | 1
GEN-2020-038 | DISIS-2020-001 | 02 NEBRASKA | 156970 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 6522000 | 100% | 6522000 | 1
GEN-2020-038 | DISIS-2020-001 | 02 NEBRASKA | 156971 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 1500000 | 100% | 1500000 | 1
GEN-2020-043 | DISIS-2020-001 | 02 NEBRASKA | 156390 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 100% | 0 | 1
GEN-2020-043 | DISIS-2020-001 | 02 NEBRASKA | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 33.33% | 0 | 1
GEN-2020-044 | DISIS-2020-001 | 02 NEBRASKA | 156391 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 100% | 0 | 1
GEN-2020-044 | DISIS-2020-001 | 02 NEBRASKA | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 33.33% | 0 | 1
GEN-2020-045 | DISIS-2020-001 | 02 NEBRASKA | 156392 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 100% | 0 | 1
GEN-2020-045 | DISIS-2020-001 | 02 NEBRASKA | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 0 | 33.33% | 0 | 1
GEN-2020-054 | DISIS-2020-001 | 04 SOUTHEAST | 156929 | ERIS | Lydia 345 kV Station GEN-2020-054 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar), into the Point of Interconnection (POI) at Lydia 345 kV Station | 4182988 | 100% | 4182988 | 1
GEN-2020-054 | DISIS-2020-001 | 04 SOUTHEAST | 156930 | ERIS | Lydia 345kV Station GEN-2020-054 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, into the Point of Interconnection (POI) at Lydia 345 kV Station | 5363867 | 100% | 5363867 | 1
GEN-2020-056 | DISIS-2020-001 | 03 CENTRAL | 144324 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 2177009 | 100% | 2177009 | 1
GEN-2020-056 | DISIS-2020-001 | 03 CENTRAL | 144325 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 309607 | 100% | 309607 | 1
GEN-2020-057 | DISIS-2020-001 | 03 CENTRAL | 156879 | ERIS | Atlantic 345 kV GEN-2020-057 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Battery/Storage), into the Point of Interconnection (POI) at Atlantic 345 kV | 3724978 | 100% | 3724978 | 1
GEN-2020-057 | DISIS-2020-001 | 03 CENTRAL | 156880 | ERIS | Atlantic 345 kV GEN-2020-057 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Battery/Storage), into the Point of Interconnection (POI) at Atlantic 345 kV | 1550523 | 100% | 1550523 | 1
GEN-2020-057 | DISIS-2020-001 CF | 03 CENTRAL | 158640, 158641, 158645, 158646, 158648, 159064 | NRIS | Multi - Atlantic - Craig - West Gardener 345-115 kV | Contingent | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. Install two new 345/115 transformers at Atlantic 115 kV substation. Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic â€“ Eudora Township 115 kV line. | 0 | 0% | 99066200 | N/A
GEN-2020-057 | DISIS-2020-001 | 03 CENTRAL | 170587 | NRIS | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | Current Study | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | 3083456.0359 | 23.73% | 12994970 | 0.0249
GEN-2020-057 | DISIS-2020-001 | 03 CENTRAL | 170612 | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 | Current Study | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 (2.98 miles) to a minimum rating of 400 MVA | 6217273 | 50% | 12434546 | 0.03986
GEN-2020-058 | DISIS-2020-001 | 03 CENTRAL | 156897 | ERIS | Atlantic 345 kV GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Atlantic 345 kV | 3724978 | 100% | 3724978 | 1
GEN-2020-058 | DISIS-2020-001 | 03 CENTRAL | 156898 | ERIS | Atlantic 345 kV GEN-2020-058 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Atlantic 345 kV | 1550523 | 100% | 1550523 | 1
GEN-2020-058 | DISIS-2020-001 CF | 03 CENTRAL | 158640, 158641, 158645, 158646, 158648, 159064 | NRIS | Multi - Atlantic - Craig - West Gardener 345-115 kV | Contingent | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. Install two new 345/115 transformers at Atlantic 115 kV substation. Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic â€“ Eudora Township 115 kV line. | 0 | 0% | 99066200 | N/A
GEN-2020-058 | DISIS-2020-001 | 03 CENTRAL | 170587 | NRIS | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | Current Study | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | 3083456.0359 | 23.73% | 12994970 | 0.0249
GEN-2020-058 | DISIS-2020-001 | 03 CENTRAL | 170612 | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 | Current Study | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 (2.98 miles) to a minimum rating of 400 MVA | 6217273 | 50% | 12434546 | 0.03986
GEN-2020-060 | DISIS-2020-001 | 05 SOUTHWEST | 156926 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 15953721 | 100% | 15953721 | 1
GEN-2020-060 | DISIS-2020-001 | 05 SOUTHWEST | 156927 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 3635206 | 100% | 3635206 | 1
GEN-2020-060 | DISIS-2020-001 | 05 SOUTHWEST | 170624/170625 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | 0 | 0% | 428620878 | 0.10435
GEN-2020-060 | DISIS-2020-001 | 05 SOUTHWEST | 170626 | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | 0 | 0% | 1690874827 | 0.20214
GEN-2020-060 | DISIS-2020-001 CF | 05 SOUTHWEST | 158630 | ERIS | Potter County 345/230 kV Transformer Ckt 2 | Contingent | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 0 | 0% | 11011685 | N/A
GEN-2020-060 | DISIS-2020-001 CF | 05 SOUTHWEST | 143182 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12410868 | N/A
GEN-2020-061 | DISIS-2020-001 | 03 CENTRAL | 156943 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 112911 | 100% | 112911 | 1
GEN-2020-061 | DISIS-2020-001 | 03 CENTRAL | 156944 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 0 | 100% | 0 | 1
GEN-2020-064 | DISIS-2020-001 | 03 CENTRAL | 156877 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-064 | DISIS-2020-001 | 03 CENTRAL | 156878 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 156909 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 26670716 | 100% | 26670716 | 1
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 156910 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 3369060 | 100% | 3369060 | 1
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 220754 | ERIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Contingent | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | 0 | 0% | 51355500 | 0.00641
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170624/170625 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | 0 | 0% | 428620878 | 0.17609
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170626 | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | 0 | 0% | 1690874827 | 0.45632
GEN-2020-065 | DISIS-2020-001 CF | 05 SOUTHWEST | 158630 | ERIS | Potter County 345/230 kV Transformer Ckt 2 | Contingent | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 0 | 0% | 11011685 | N/A
GEN-2020-065 | DISIS-2020-001 CF | 05 SOUTHWEST | 143182 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12410868 | N/A
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170597 | ERIS | Build New Andrews to Road Runner 345 kV Line | Current Study | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | 73524573 | 100% | 73524573 | 0.22857
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170603 | ERIS | Hobbs to Andrews Voltage Conversion | Current Study | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | 21014929 | 100% | 21014929 | 0.15274
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170607 | ERIS | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Current Study | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE | 2659649 | 100% | 2659649 | 0.79776
GEN-2020-065 | DISIS-2020-001 | 05 SOUTHWEST | 170606 | ERIS | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Current Study | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE | 888533 | 100% | 888533 | 0.20224
GEN-2020-067 | DISIS-2020-001 | 05 SOUTHWEST | 170624/170625 | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | 0 | 0% | 428620878 | 0.11201
GEN-2020-067 | DISIS-2020-001 | 05 SOUTHWEST | 170626 | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | 0 | 0% | 1690874827 | 0.28643
GEN-2020-067 | DISIS-2020-001 CF | 05 SOUTHWEST | 158630 | ERIS | Potter County 345/230 kV Transformer Ckt 2 | Contingent | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 0 | 0% | 11011685 | N/A
GEN-2020-067 | DISIS-2020-001 CF | 05 SOUTHWEST | 143182 | ERIS | Multi - Border - Woodward 345 kV Tap | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 0 | 0% | 12410868 | N/A
GEN-2020-067 | DISIS-2020-001 | 05 SOUTHWEST | 156979 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 3806792 | 100% | 3806792 | 1
GEN-2020-067 | DISIS-2020-001 | 05 SOUTHWEST | 156980 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (DISIS-2020-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 42711265 | 100% | 42711265 | 1
GEN-2020-072 | DISIS-2020-001 | 03 CENTRAL | 156986 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 14220207 | 100% | 14220207 | 1
GEN-2020-072 | DISIS-2020-001 | 03 CENTRAL | 156987 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 1718484 | 100% | 1718484 | 1
GEN-2020-078 | DISIS-2020-001 | 02 NEBRASKA | 143684 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 150000 | 100% | 150000 | 1
GEN-2020-078 | DISIS-2020-001 | 02 NEBRASKA | 143685 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 20600000 | 100% | 20600000 | 1
GEN-2020-079 | DISIS-2020-001 | 03 CENTRAL | 156951 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 13354013 | 100% | 13354013 | 1
GEN-2020-079 | DISIS-2020-001 | 03 CENTRAL | 156952 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 2612528 | 100% | 2612528 | 1
GEN-2020-081 | DISIS-2020-001 | 04 SOUTHEAST | 156975 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 6385335 | 100% | 6385335 | 1
GEN-2020-081 | DISIS-2020-001 | 04 SOUTHEAST | 156976 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 4264996 | 100% | 4264996 | 1
GEN-2020-083 | DISIS-2020-001 | 01 NORTH | 156905 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 7520000 | 100% | 7520000 | 1
GEN-2020-083 | DISIS-2020-001 | 01 NORTH | 156906 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 370000 | 100% | 370000 | 1
GEN-2020-083 | DISIS-2020-001 CF | 01 NORTH | 156282 | NRIS | Fargo 230 kV Terminal Upgrade | Contingent | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 0 | 0% | 3119998 | N/A
GEN-2020-084 | DISIS-2020-001 | 02 NEBRASKA | 156949 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | 5000000 | 100% | 5000000 | 1
GEN-2020-084 | DISIS-2020-001 | 02 NEBRASKA | 156950 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | 2800000 | 100% | 2800000 | 1
GEN-2020-084 | DISIS-2020-001 | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. *Updated cost not available | 4785709 | 100% | 4785709 | 0.67848
GEN-2020-087 | DISIS-2020-001 | 04 SOUTHEAST | 156889 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 5106556 | 100% | 5106556 | 1
GEN-2020-087 | DISIS-2020-001 | 04 SOUTHEAST | 156890 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 24551778 | 100% | 24551778 | 1
GEN-2020-088 | DISIS-2020-001 | 03 CENTRAL | 156915 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 3138366 | 100% | 3138366 | 1
GEN-2020-088 | DISIS-2020-001 | 03 CENTRAL | 156916 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 1049681 | 100% | 1049681 | 1
GEN-2020-090 | DISIS-2020-001 | 03 CENTRAL | 156988 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 27979220 | 100% | 27979220 | 1
GEN-2020-090 | DISIS-2020-001 | 03 CENTRAL | 156989 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 815780 | 100% | 815780 | 1
GEN-2020-091 | DISIS-2020-001 | 01 NORTH | 156941 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 2423402 | 100% | 2423402 | 1
GEN-2020-091 | DISIS-2020-001 | 01 NORTH | 156942 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 2890308 | 100% | 2890308 | 1
GEN-2020-092 | DISIS-2020-001 | 04 SOUTHEAST | 156947 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 15175233 | 100% | 15175233 | 1
GEN-2020-092 | DISIS-2020-001 | 04 SOUTHEAST | 156948 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 3151953 | 100% | 3151953 | 1
GEN-2020-092 | DISIS-2020-001 | 04 SOUTHEAST | 170575 | ERIS | Catoosa Terminal Upgrade (Model Correction) | Model Correction | Replace switch, jumpers, and CTs at Catoosa 138 kV to achieve a minimum rating of 218 MVA | 0 | 100% | 0 | 0.00506
GEN-2020-094 | DISIS-2020-001 | 02 NEBRASKA | 156931 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 23535000 | 100% | 23535000 | 1
GEN-2020-094 | DISIS-2020-001 | 02 NEBRASKA | 156932 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 24147000 | 100% | 24147000 | 1
GEN-2020-094 | DISIS-2020-001 CF | 02 NEBRASKA | 156456 | NRIS | Replace Mark Moore 345/115 kV Transformer | Contingent | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | 0 | 0% | 8300000 | N/A
691655866
Note on J30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 0% due to IGIA
Note on J32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 0% due to IGIA
Note on J33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Changed to 100% as shared gens were paid at IGIA

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Contingent | DISIS-2020-001 CF | Steady State | 01 NORTH | 2022 ITP | NRIS | Fargo 230 kV Terminal Upgrade | 156282 | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | XEL/WAPA | 4602200% | 3119998
Current Study | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | 170610 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | WAPA | 80 | 44600000
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | 156905 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 80 | 7520000
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | 156906 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 80 | 370000
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | 156922 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 60 | 28072797
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | 156923 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 60 | 4272447
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | 144259 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | 144258 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | 156941 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 60 | 2423402
Interconnection | DISIS-2020-001 | Steady State | 01 NORTH | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | 156942 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 60 | 2890308
Contingent | DISIS-2020-001 CF | Steady State | 02 NEBRASKA | DISIS-2020-001 | NRIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | 170588 | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA *Updated cost not available | NPPD | 0 | 14500000
Contingent | DISIS-2020-001 CF | Steady State | 02 NEBRASKA | DISIS-2017-002 | NRIS | Replace Mark Moore 345/115 kV Transformer | 156456 | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | NPPD | 0 | 8300000
Current Study | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | 170588 | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA *Updated cost not available | NPPD | 0 | 14500000
Current Study | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | 158605 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. *Updated cost not available | OPPD | 24 | 4785709
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | 143683 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | 143682 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | 156881 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV *Updated cost not available | NPPD | 0 | 20300000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | 156882 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV *Updated cost not available | NPPD | 0 | 1000000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | 156390 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | 156394 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | 156391 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | 156392 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | 156931 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 48 | 23535000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | 156932 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 48 | 24147000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | 156939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV *Updated cost not available | NPPD | 0 | 9200000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | 156940 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV *Updated cost not available | NPPD | 0 | 700000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | 156949 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | OPPD | 48 | 5000000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | 156950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV (Sharing a GEN Tie line with GEN-2018-043) | OPPD | 36 | 2800000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | 143685 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 48 | 20600000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | 143684 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 24 | 150000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | 156388 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | 156389 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | 156968 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (272.7/Thermal), into the Point of Interconnection (POI) at Substation 1363 161kV Substation | OPPD | 36 | 5000000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | 156970 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 6522000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | 156971 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 1500000
Interconnection | DISIS-2020-001 | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-028, GEN-2020-031 Interconnection (DISIS-2020-001) (OPPD) | 156393 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-028, GEN-2020-031, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 0 | 0
Contingent | DISIS-2020-001 CF | Steady State | 03 CENTRAL | 2023 ITP | NRIS | Multi - Atlantic - Craig - West Gardener 345-115 kV | 158640, 158641, 158645, 158646, 158648, 159064 | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. Install two new 345/115 transformers at Atlantic 115 kV substation. Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic â€“ Eudora Township 115 kV line. | KCPL | 4574800% | 99066200
Current Study | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | NRIS | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 | 170612 | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2 (2.98 miles) to a minimum rating of 400 MVA | KCPL | 48 | 12434546
Current Study | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | NRIS | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 | 170587 | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | KCPL | 48 | 12994970
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | 156877 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EMDE | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | 156878 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EMDE | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Atlantic 345 kV GEN-2020-057 Interconnection (Non-shared NU) (KCPL) | 156879 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Battery/Storage), into the Point of Interconnection (POI) at Atlantic 345 kV | KCPL | 56 | 3724978
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Atlantic 345 kV GEN-2020-057 Interconnection (TOIF) (KCPL) | 156880 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Battery/Storage), into the Point of Interconnection (POI) at Atlantic 345 kV | KCPL | 56 | 1550523
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Atlantic 345 kV GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | 156897 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Atlantic 345 kV | KCPL | 56 | 3724978
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Atlantic 345 kV GEN-2020-058 Interconnection (TOIF) (KCPL) | 156898 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Atlantic 345 kV | KCPL | 56 | 1550523
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | 156895 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 36 | 2521943
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | 156896 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 36 | 3277798
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | 156901 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 30 | 1750000
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | 156902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 30 | 180000
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | 156903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 56 | 30372474
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | 156904 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 56 | 1782995
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | 156915 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EMDE | 36 | 3138366
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | 156916 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EMDE | 36 | 1049681
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | 156943 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 18 | 112911
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | 156944 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | 156951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EMDE | 36 | 13354013
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | 156952 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EMDE | 36 | 2612528
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | 144325 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 18 | 309607
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | 144324 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 18 | 2177009
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | 156986 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 48 | 14220207
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | 156987 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 48 | 1718484
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (NEET) | 156988 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | NEET | 44 | 27979220
Interconnection | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (NEET) | 156989 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | NEET | 44 | 815780
Model Correction | DISIS-2020-001 | Steady State | 03 CENTRAL | DISIS-2020-001 | NRIS | STILWEL5 to HICKMAN5 161 kV Line 1 Rating Update | TBD | Update the existing STILWEL5 to HICKMAN5 161 kV Line 1 to a rating of 311/334 MVA SN/SE | KCPL | 0 | 0
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | 156889 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEPW | 42 | 5106556
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | 156890 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEPW | 42 | 24551778
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Lydia 345 kV Station GEN-2020-054 Interconnection (TOIF) (AEP) | 156929 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar), into the Point of Interconnection (POI) at Lydia 345 kV Station | AEPW | 36 | 4182988
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Lydia 345kV Station GEN-2020-054 Interconnection (DISIS-2020-001) (AEP) | 156930 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, into the Point of Interconnection (POI) at Lydia 345 kV Station | AEPW | 36 | 5363867
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | 156947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEPW | 36 | 15175233
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | 156948 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEPW | 36 | 3151953
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | 156960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 60 | 6050000
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | 156961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 60 | 517000
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | 156966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEPW | 36 | 15222455
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | 156967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEPW | 36 | 2983138
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | 156993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEPW | 42 | 24835359
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | 156974 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEPW | 42 | 5511711
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | 156975 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEPW | 36 | 6385335
Interconnection | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | 156976 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEPW | 36 | 4264996
Model Correction | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Catoosa Terminal Upgrade (Model Correction) | 170575 | Replace switch, jumpers, and CTs at Catoosa 138 kV to achieve a minimum rating of 218 MVA | AEPW | 36 | 0
Model Correction | DISIS-2020-001 | Steady State | 04 SOUTHEAST | DISIS-2020-001 | ERIS | Sunnyside to Rocky Point 138 kV Line Rating Update | TBD | Model correction. Sunnyside to Rocky Point 138 kV line (10.25 miles) summer normal rating updated to 268 MVA and summer emergency rating updated to 308 MVA. | OKGE | - | 0
Contingent | DISIS-2020-001 | Steady State | 05 SOUTHWEST | 2023 ITP | ERIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | 220754 | Build two new 15 mile circuits from Anadarko to Gracemont 138 kV with SN/SE ratings of 478 MVA | OKGE/WFEC | 4675200% | 51355500
Contingent | DISIS-2020-001 | Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Build New Beckham to Potter 345 kV Line | 170624/170625 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | SPS/OKGE | 36 | 428620878
Contingent | DISIS-2020-001 | Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | 170626 | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | SPS | 36 | 1690874827
Contingent | DISIS-2020-001 CF | Stability | 05 SOUTHWEST | 2023 ITP | ERIS | Potter County 345/230 kV Transformer Ckt 2 | 158630 | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | SPS | 4710200% | 11011685
Contingent | DISIS-2020-001 CF | Stability | 05 SOUTHWEST | 2020 ITP | ERIS | Multi - Border - Woodward 345 kV Tap | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEPW/OKGE | 36 | 12410868
Current Study | DISIS-2020-001 | Steady State/Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Andrews to Road Runner 345 kV Line | 170597 | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | SPS | 0 | 73524573
Current Study | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Hobbs to Andrews Voltage Conversion | 170603 | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | SPS | 0 | 21014929
Current Study | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Sidewinder to Andrews 345 kV Lidar Clearance Correction | 170606 | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE | SPS | 0 | 888533
Current Study | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | 170607 | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE | SPS | 0 | 2659649
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | 156909 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 0 | 26670716
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | 156910 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 0 | 3369060
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | 156926 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 0 | 15953721
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | 156927 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 0 | 3635206
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | 156979 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 0 | 3806792
Interconnection | DISIS-2020-001 | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (DISIS-2020-001) (SPS) | 156980 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 0 | 42711265
3010038966

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 27L and 27SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
ASGI-2020-001 | 03 CENTRAL | ERIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.03446 | TBD (36 month lead time) | 1455934 | 1455934
ASGI-2020-001 | 03 CENTRAL | ERIS | TBD | 156851 | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.03446 | TBD (36 month lead time) | 41157960 | 41157960
ASGI-2020-001 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03354 | 4602300% | 24319368 | 24319368
ASGI-2020-001 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | DISIS-2017-002 | Yes | Yes | 0.06305 | TBD (36 month lead time) | TBD | TBD
ASGI-2020-003 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04191 | 4574800% | 28123307 | 0
ASGI-2020-003 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03504 | 4602300% | 24319368 | 24319368
GEN-2020-002 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.05586 | 4638700% | 64071687 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0986 | 4638700% | 2070042 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.12225 | 4638700% | 1786830 | 0
GEN-2020-011 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.09793 | 4638700% | 2070042 | 0
GEN-2020-013 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.09982 | 4638700% | 2070042 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.06956 | 4638700% | 64071687 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.17011 | 4638700% | 2070042 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.15585 | 4638700% | 1786830 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.06956 | 4638700% | 64071687 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | TBD | TBD | Farber – Sumner County No. 10 Belle Plain 138 kV Rebuild | Farber – Sumner County No. 10 Belle Plain 138 kV Rebuild | Rebuild 10.3 miles of 138 kV from Farber to Summer County No. 10 Belle Plain | 2024 ITP | Yes | Yes | 0.30545 | TBD | 11639947 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | TBD | TBD | Farber – Sumner County No. 10 Belle Plain 138 kV Rebuild | Farber – Sumner County No. 10 Belle Plain 138 kV Rebuild | Rebuild 10.3 miles of 138 kV from Farber to Summer County No. 10 Belle Plain | 2024 ITP | Yes | Yes | 0.30152 | TBD | 11639947 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.04343 | 4635700% | 1203344 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.0403 | 4635700% | 1203344 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 220774 | 157880 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | REBUILD OSAGE - WEBB CITY - SHIDLER 138 KV CKT 1 TO RATING OF 286/286 MVA | 2023 ITP | Yes | Yes | 0.04343 | 4635700% | 28880257 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 220774 | 157880 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Webb City Tap - Osage 138 kV Ckt 1 Rebuild (OGE) | REBUILD OSAGE - WEBB CITY - SHIDLER 138 KV CKT 1 TO RATING OF 286/286 MVA | 2023 ITP | Yes | Yes | 0.0403 | 4635700% | 28880257 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05404 | 4574800% | 28123307 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03938 | 4565800% | 647852 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05031 | 4593800% | 121709542 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03778 | 4593800% | 121709542 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05031 | 4593800% | 5915803 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03778 | 4593800% | 5915803 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05031 | 4593100% | 3909824 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03778 | 4593100% | 3909824 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07501 | 4602200% | 1130397 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11974 | 4602200% | 1130397 | 0
GEN-2020-003 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07501 | 4602200% | 401187 | 0
GEN-2020-003 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11974 | 4602200% | 401187 | 0
GEN-2020-007 | 03 CENTRAL | NRIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 2024 ITP | Yes | Yes | 0.03726 | TBD | 786451 | 0
GEN-2020-007 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.12338 | 4574800% | 28123307 | 0
GEN-2020-007 | 03 CENTRAL | NRIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.15038 | 4574800% | 28123307 | 0
GEN-2020-007 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03255 | 4602300% | 24319368 | 24319368
GEN-2020-007 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07544 | 4602200% | 1130397 | 0
GEN-2020-007 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04693 | 4602200% | 1130397 | 0
GEN-2020-007 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07544 | 4602200% | 401187 | 0
GEN-2020-007 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04693 | 4602200% | 401187 | 0
GEN-2020-007 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.05085 | 4602200% | 1534495 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | TBD | TBD | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Upgrade terminal equipment at Cudahy 115 kV substation to increase minimum summer/emergency rating to 135 MVA | Transmission Owner Internal Project | Yes | Yes | 0.03845 | TBD (36 month lead time) | 250000 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05448 | 4593900% | 12410868 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05448 | 4614300% | 8323241 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03805 | 4565800% | 647852 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03223 | 4568800% | 16516041 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03223 | 4565800% | 7099323 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.03237 | 4568800% | 38537430 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03237 | 4565800% | 5170350 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03237 | 4565800% | 32342389 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07574 | 4602200% | 1130397 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07574 | 4602200% | 401187 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04783 | 4710200% | 10545000 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.04783 | 4710200% | 11707581 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04783 | 4710200% | 5577000 | 0
GEN-2020-008 | 03 CENTRAL | ERIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04783 | 4710200% | 11011685 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.042 | 4653900% | 540691 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.05631 | 4653900% | 540691 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0715 | 4644600% | 9932652 | 9932652
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.05631 | 4638600% | 15333000 | 15333000
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.06558 | 4644600% | 9932652 | 9932652
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.06124 | 4644600% | 9932652 | 9932652
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03719 | 4638600% | 15333000 | 15333000
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03273 | 4638600% | 15333000 | 15333000
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03517 | 4644600% | 9932652 | 9932652
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03517 | 4644600% | 9932652 | 9932652
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03083 | 4644600% | 9932652 | 9932652
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 730200 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12864 | 4638700% | 730200 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 730200 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12864 | 4638700% | 730200 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 5846250 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 5846250 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12864 | 4638700% | 5846250 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 1107600 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.12864 | 4638700% | 1107600 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1291 | 4638700% | 1107600 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.17011 | 4638700% | 2070042 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.15585 | 4638700% | 1786830 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.06956 | 4638700% | 64071687 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.17011 | 4638700% | 2070042 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.15585 | 4638700% | 1786830 | 0
GEN-2020-038 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.31401 | 4638700% | 64071687 | 0
GEN-2020-038 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.36473 | 4638700% | 2070042 | 0
GEN-2020-038 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.32126 | 4638700% | 1786830 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.04877 | 4638700% | 64071687 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.16768 | 4638700% | 2070042 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.13959 | 4638700% | 1786830 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.04877 | 4638700% | 64071687 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.16768 | 4638700% | 2070042 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.13959 | 4638700% | 1786830 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.04877 | 4638700% | 64071687 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.16768 | 4638700% | 2070042 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.13959 | 4638700% | 1786830 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12864 | 4638700% | 1107600 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03186 | 4574800% | 28123307 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.08087 | 4593900% | 12410868 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08087 | 4614300% | 8323241 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.12397 | 4593900% | 12410868 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09036 | 4593900% | 12410868 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12397 | 4614300% | 8323241 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09036 | 4614300% | 8323241 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03321 | 4593900% | 12410868 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03321 | 4614300% | 8323241 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03224 | 4593900% | 12410868 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03224 | 4614300% | 8323241 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09631 | 4593900% | 12410868 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09631 | 4614300% | 8323241 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09631 | 4593900% | 12410868 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06271 | 4593900% | 12410868 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09631 | 4614300% | 8323241 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06271 | 4614300% | 8323241 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210586 | 122722 | Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV | Dover Switch - O'Keene 138 kV Ckt 1 Terminal Upgrades | Upgrade any necessary terminal equipment, increase clearances, and replace conductor to achieve a summer emergency rating of 136 MVA | 2020 ITP | Yes | Yes | 0.04488 | 4602200% | 910000 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210586 | 122722 | Multi - Dover Switch - O'Keene and Aspen - Mooreland - Pic 138 kV | Dover Switch - O'Keene 138 kV Ckt 1 Terminal Upgrades | Upgrade any necessary terminal equipment, increase clearances, and replace conductor to achieve a summer emergency rating of 136 MVA | 2020 ITP | Yes | Yes | 0.03052 | 4602200% | 910000 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03513 | 4629500% | 1170000 | 1170000
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03291 | 4629500% | 1170000 | 1170000
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04145 | 4565800% | 647852 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.0609 | 4638700% | 64071687 | 0
GEN-2020-078 | 02 NEBRASKA | NRIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.09107 | 4638700% | 64071687 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.16626 | 4638700% | 2070042 | 0
GEN-2020-078 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.1251 | 4638700% | 2070042 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.13936 | 4638700% | 1786830 | 0
GEN-2020-078 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.17061 | 4638700% | 1786830 | 0
GEN-2020-084 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.06587 | 4638700% | 64071687 | 0
GEN-2020-084 | 02 NEBRASKA | NRIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.09604 | 4638700% | 64071687 | 0
GEN-2020-084 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.25418 | 4638700% | 2070042 | 0
GEN-2020-084 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.26583 | 4638700% | 2070042 | 0
GEN-2020-084 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.12671 | 4638700% | 1786830 | 0
GEN-2020-084 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.15796 | 4638700% | 1786830 | 0
GEN-2020-094 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.09663 | 4638700% | 2070042 | 0
GEN-2020-094 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03946 | 4638700% | 2070042 | 0
GEN-2020-094 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06491 | 4638700% | 1786830 | 0
GEN-2020-094 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.10006 | 4638700% | 1786830 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 210619 | 144284 | Line - Kearney NE - Tower 115 kV | Kearney 115 kV Terminal Equipment | Install 115 kV terminal equipment at Kearney 115 kV sub to support a new line from Tower 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.03212 | 4580900% | 4510103 | 4510103
GEN-2020-014 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.12944 | TBD | 10061320 | 10061320
GEN-2020-014 | 01 NORTH | NRIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.06423 | TBD | 10061320 | 10061320
GEN-2020-014 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12944 | 4737300% | 9455440 | 0
GEN-2020-014 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.06423 | 4737300% | 9455440 | 0
GEN-2020-014 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12036 | 4737300% | 9263038 | 0
GEN-2020-014 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.0671 | 4737300% | 9263038 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04847 | 4638700% | 2070042 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05368 | 4638700% | 1786830 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.05077 | 4566600% | 770086 | 0
GEN-2020-014 | 01 NORTH | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04389 | 4574800% | 28123307 | 0
GEN-2020-014 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04404 | 4675200% | 224639813 | 0
GEN-2020-014 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04025 | 4675200% | 254838000 | 0
GEN-2020-014 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04404 | 4675200% | 16186000 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04025 | 4675200% | 842000 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.15373 | 4562600% | 18251841 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.12912 | 4562600% | 18251841 | 0
GEN-2020-014 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05043 | 4602300% | 24319368 | 24319368
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.11239 | 4635600% | 82718831 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.08173 | 4635600% | 82718831 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.10544 | 4635600% | 18932308 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.08173 | 4635600% | 18932308 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.10544 | 4635600% | 385021 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.08173 | 4635600% | 385021 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.10544 | 4635600% | 214157775 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.0771 | 4635600% | 214157775 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.10544 | 4635600% | 10502349 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.0771 | 4635600% | 10502349 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.11239 | 4635600% | 5085047 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.08173 | 4635600% | 5085047 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210581 | 122745 | Multi - Watford City 230/115 kV | Watford City 230/115 kV Transformer Ckt 1 (KV1A) | Replace the 230/115 kV transformer Ckt 1 at Watford City to achieve a summer emergency rating of 208 MVA | 2020 ITP | Yes | Yes | 0.48636 | 4547300% | 3941163 | 0
GEN-2020-014 | 01 NORTH | NRIS | 210581 | 122746 | Multi - Watford City 230/115 kV | Watford City 230/115 kV Transformer Ckt 2 (KV2A | Upgrade any necessary terminal equipment at Watford City for the 230/115 kV transformer Ckt 2 to achieve a summer emergency rating of 208 MVA | 2020 ITP | Yes | Yes | 0.48636 | 4547300% | 173041 | 0
GEN-2020-014 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04326 | 4602200% | 243120 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06818 | 4565800% | 647852 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03933 | 4568800% | 16516041 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03933 | 4565800% | 7099323 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03753 | 4565800% | 32342389 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03525 | 4568800% | 16516041 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03525 | 4565800% | 7099323 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.08845 | 4568800% | 38537430 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.09828 | 4568800% | 38537430 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08845 | 4565800% | 5170350 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09828 | 4565800% | 5170350 | 0
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.08845 | 4565800% | 32342389 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.09828 | 4565800% | 32342389 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.06173 | 4565800% | 647852 | 0
GEN-2020-020 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03827 | 4565800% | 647852 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04776 | 4568800% | 16516041 | 0
GEN-2020-021 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.03394 | TBD | 10061320 | 10061320
GEN-2020-021 | 01 NORTH | NRIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | No | 0.13507 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2020-021 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.03394 | 4737300% | 9455440 | 0
GEN-2020-021 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.03297 | 4737300% | 9455440 | 0
GEN-2020-021 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.06497 | 4737300% | 9263038 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04032 | 4638700% | 2070042 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04855 | 4638700% | 1786830 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.04755 | 4566600% | 770086 | 0
GEN-2020-021 | 01 NORTH | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04309 | 4574800% | 28123307 | 0
GEN-2020-021 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06356 | 4675200% | 224639813 | 0
GEN-2020-021 | 01 NORTH | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0441 | 4675200% | 224639813 | 0
GEN-2020-021 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06379 | 4675200% | 254838000 | 0
GEN-2020-021 | 01 NORTH | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0476 | 4675200% | 254838000 | 0
GEN-2020-021 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06356 | 4675200% | 16186000 | 0
GEN-2020-021 | 01 NORTH | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0476 | 4675200% | 16186000 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.06379 | 4675200% | 842000 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.0476 | 4675200% | 842000 | 0
GEN-2020-021 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05506 | 4602300% | 24319368 | 24319368
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.03096 | 4635600% | 82718831 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.06295 | 4635600% | 82718831 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.04302 | 4635600% | 18932308 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.07484 | 4635600% | 18932308 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.04302 | 4635600% | 385021 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.07484 | 4635600% | 385021 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.04302 | 4635600% | 214157775 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.07484 | 4635600% | 214157775 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.04302 | 4635600% | 10502349 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.07484 | 4635600% | 10502349 | 0
GEN-2020-021 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.03096 | 4635600% | 5085047 | 0
GEN-2020-021 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.06295 | 4635600% | 5085047 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 210619 | 144283 | Line - Kearney NE - Tower 115 kV | Tower 115 kV Terminal Equipment | Install terminal equipment at Tower 115 kV sub to support new line from Kearney 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.03212 | 4580900% | 3077037 | 3077037
GEN-2020-013 | 02 NEBRASKA | ERIS | 210619 | 144284 | Line - Kearney NE - Tower 115 kV | Kearney 115 kV Terminal Equipment | Install 115 kV terminal equipment at Kearney 115 kV sub to support a new line from Tower 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.03869 | 4580900% | 4510103 | 4510103
GEN-2020-013 | 02 NEBRASKA | NRIS | 210619 | 144284 | Line - Kearney NE - Tower 115 kV | Kearney 115 kV Terminal Equipment | Install 115 kV terminal equipment at Kearney 115 kV sub to support a new line from Tower 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.04636 | 4580900% | 4510103 | 4510103
GEN-2020-013 | 02 NEBRASKA | ERIS | 210619 | 143705 | Line - Kearney NE - Tower 115 kV | Kearney NE - Tower 115 kV Ckt 1 New Line | Build a new 115 kV 10 mile line from Kearney to Tower with a minimum summer emergency rating of 160 MVA | DPA-2021-February-1278 | Yes | Yes | 0.03869 | 4580900% | 11915911 | 11915911
GEN-2020-013 | 02 NEBRASKA | ERIS | 210619 | 144283 | Line - Kearney NE - Tower 115 kV | Tower 115 kV Terminal Equipment | Install terminal equipment at Tower 115 kV sub to support new line from Kearney 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.03869 | 4580900% | 3077037 | 3077037
GEN-2020-013 | 02 NEBRASKA | NRIS | 210619 | 144283 | Line - Kearney NE - Tower 115 kV | Tower 115 kV Terminal Equipment | Install terminal equipment at Tower 115 kV sub to support new line from Kearney 115 kV sub. | DPA-2021-February-1278 | Yes | Yes | 0.04636 | 4580900% | 3077037 | 3077037
GEN-2020-002 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05348 | 4574800% | 28123307 | 0
GEN-2020-011 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03302 | 4574800% | 28123307 | 0
GEN-2020-013 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03599 | 4574800% | 28123307 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05932 | 4574800% | 28123307 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05932 | 4574800% | 28123307 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05932 | 4574800% | 28123307 | 0
GEN-2020-038 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.06036 | 4574800% | 28123307 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05895 | 4574800% | 28123307 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05895 | 4574800% | 28123307 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05895 | 4574800% | 28123307 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05313 | 4574800% | 28123307 | 0
GEN-2020-084 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05146 | 4574800% | 28123307 | 0
GEN-2020-094 | 02 NEBRASKA | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05609 | 4574800% | 28123307 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03572 | 4675200% | 224639813 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04366 | 4675200% | 254838000 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04366 | 4675200% | 16186000 | 0
GEN-2020-011 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04366 | 4675200% | 842000 | 0
GEN-2020-013 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03754 | 4675200% | 224639813 | 0
GEN-2020-013 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03963 | 4675200% | 254838000 | 0
GEN-2020-013 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03963 | 4675200% | 16186000 | 0
GEN-2020-013 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03963 | 4675200% | 842000 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0303 | 4602300% | 24319368 | 24319368
GEN-2020-011 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04307 | 4602300% | 18617823 | 18617823
GEN-2020-011 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.14272 | 4602300% | 24319368 | 24319368
GEN-2020-011 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09165 | 4602300% | 24319368 | 24319368
GEN-2020-011 | 02 NEBRASKA | NRIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.04259 | 4602300% | 5468352 | 5468352
GEN-2020-011 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.04307 | 4602300% | 1173160 | 1173160
GEN-2020-011 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04307 | 4602300% | 5928037 | 5928037
GEN-2020-013 | 02 NEBRASKA | NRIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04045 | 4602300% | 18617823 | 18617823
GEN-2020-013 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.14252 | 4602300% | 24319368 | 24319368
GEN-2020-013 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.09144 | 4602300% | 24319368 | 24319368
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04776 | 4565800% | 7099323 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.04557 | 4565800% | 32342389 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.0597 | 4565800% | 647852 | 0
GEN-2020-054 | 04 SOUTHEAST | NRIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03625 | 4565800% | 647852 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04653 | 4568800% | 16516041 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04653 | 4565800% | 7099323 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.04439 | 4565800% | 32342389 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03481 | 4565800% | 647852 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04147 | 4568800% | 16516041 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04147 | 4565800% | 7099323 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.12871 | 4568800% | 38537430 | 0
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12871 | 4565800% | 5170350 | 0
GEN-2020-056 | 03 CENTRAL | ERIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 2023 ITP | Yes | Yes | 0.47597 | 4656800% | 593064 | 0
GEN-2020-056 | 03 CENTRAL | NRIS | 220751 | 157186 | Device - Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Ellsworth Tap - Great Bend 115 kV Ckt 1 Structure Upgrade | Upgrade 25 structures of the 30.2 mile 115 kV line from Ellsworth Tap substation to Great Bend substation | 2023 ITP | Yes | Yes | 0.47861 | 4656800% | 593064 | 0
GEN-2020-056 | 03 CENTRAL | ERIS |  |  | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | DISIS-2018-001 | Yes | Yes | 0.06153 | TBD (36 month lead time) | 240000 | 240000
GEN-2020-056 | 03 CENTRAL | NRIS |  |  | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Great Bend Tap to Seward 115 kV Terminal Equipment Upgrade | Upgrade terminal equipment at Great Bend Tap to Seward 115 kV substation to increase minimum rating to 109 MVA | DISIS-2018-001 | Yes | Yes | 0.0526 | TBD (36 month lead time) | 240000 | 240000
GEN-2020-056 | 03 CENTRAL | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03026 | 4565800% | 647852 | 0
GEN-2020-056 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11766 | 4602200% | 1130397 | 0
GEN-2020-056 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11766 | 4602200% | 401187 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 220770 | 158648 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic 345/115 kV Transformer (115 kV) | Install two new 345/115 transformer at Atlantic 115 kV substation | 2023 ITP | Yes | Yes | 0.05872 | 4574800% | 15340917 | 0
GEN-2020-057 | 03 CENTRAL | NRIS | 220770 | 158648 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic 345/115 kV Transformer (115 kV) | Install two new 345/115 transformer at Atlantic 115 kV substation | 2023 ITP | Yes | Yes | 0.05838 | 4574800% | 15340917 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 220770 | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Yes | Yes | 0.04417 | 4574800% | 17693519 | 0
GEN-2020-057 | 03 CENTRAL | NRIS | 220770 | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Yes | Yes | 0.03392 | 4574800% | 17693519 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.56933 | 4574800% | 28123307 | 0
GEN-2020-057 | 03 CENTRAL | NRIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.54132 | 4574800% | 28123307 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 220771 | 159064 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Terminal Equipment 345 kV Transformer(345 kV) | Install 345 kV terminal equipment to support 345/115 transformer at Atlantic 345 kV substation | 2023 ITP | Yes | Yes | 0.05872 | 4574800% | 742772 | 0
GEN-2020-057 | 03 CENTRAL | NRIS | 220771 | 159064 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Terminal Equipment 345 kV Transformer(345 kV) | Install 345 kV terminal equipment to support 345/115 transformer at Atlantic 345 kV substation | 2023 ITP | Yes | Yes | 0.05838 | 4574800% | 742772 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 220771 | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Yes | Yes | 0.04417 | 4574800% | 29532119 | 0
GEN-2020-057 | 03 CENTRAL | NRIS | 220771 | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Yes | Yes | 0.03392 | 4574800% | 29532119 | 0
GEN-2020-057 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04177 | 4602300% | 24319368 | 24319368
GEN-2020-057 | 03 CENTRAL | NRIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | UPGRADE TERMINAL EQUIPMENT AT CRAIG - LENEXA 161KV CKT 2 LINE FOR SUMMER RATING OF 316/356 MVA, UPGRADE TERMINAL EQUIPMENT AT CRAIG - LENEXA 161KV CKT 2 LINE FOR WINTER/LIGHT RATING OF 372/407 MVA | 2023 ITP | Yes | Yes | 0.0401 | 4617400% | 1329162 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 220770 | 158648 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic 345/115 kV Transformer (115 kV) | Install two new 345/115 transformer at Atlantic 115 kV substation | 2023 ITP | Yes | Yes | 0.05872 | 4574800% | 15340917 | 0
GEN-2020-058 | 03 CENTRAL | NRIS | 220770 | 158648 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic 345/115 kV Transformer (115 kV) | Install two new 345/115 transformer at Atlantic 115 kV substation | 2023 ITP | Yes | Yes | 0.05838 | 4574800% | 15340917 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 220770 | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Yes | Yes | 0.04417 | 4574800% | 17693519 | 0
GEN-2020-058 | 03 CENTRAL | NRIS | 220770 | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Yes | Yes | 0.03392 | 4574800% | 17693519 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.56933 | 4574800% | 28123307 | 0
GEN-2020-058 | 03 CENTRAL | NRIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.54132 | 4574800% | 28123307 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 220771 | 159064 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Terminal Equipment 345 kV Transformer(345 kV) | Install 345 kV terminal equipment to support 345/115 transformer at Atlantic 345 kV substation | 2023 ITP | Yes | Yes | 0.05872 | 4574800% | 742772 | 0
GEN-2020-058 | 03 CENTRAL | NRIS | 220771 | 159064 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Terminal Equipment 345 kV Transformer(345 kV) | Install 345 kV terminal equipment to support 345/115 transformer at Atlantic 345 kV substation | 2023 ITP | Yes | Yes | 0.05838 | 4574800% | 742772 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 220771 | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Yes | Yes | 0.04417 | 4574800% | 29532119 | 0
GEN-2020-058 | 03 CENTRAL | NRIS | 220771 | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Yes | Yes | 0.03392 | 4574800% | 29532119 | 0
GEN-2020-058 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04177 | 4602300% | 24319368 | 24319368
GEN-2020-058 | 03 CENTRAL | NRIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | UPGRADE TERMINAL EQUIPMENT AT CRAIG - LENEXA 161KV CKT 2 LINE FOR SUMMER RATING OF 316/356 MVA, UPGRADE TERMINAL EQUIPMENT AT CRAIG - LENEXA 161KV CKT 2 LINE FOR WINTER/LIGHT RATING OF 372/407 MVA | 2023 ITP | Yes | Yes | 0.0401 | 4617400% | 1329162 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.05603 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.2517 | 4576700% | 6000000 | 6000000
GEN-2020-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Frankford - Quaker 115 kV Rebuild | Frankford - Quaker 115 kV Rebuild | Rebuild 2 miles of 115 kV from Frankford to Quaker | 2024 ITP | Yes | Yes | 0.07025 | TBD | 2368639 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210574 | 122727 | Line - Allen - Lubbock South 115kV | Allen - Lubbock South 115 kV Ckt 1 Rebuild | Rebuild 5.98 miles of 115 kV line from Allen to Lubbock and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA. | 2020 ITP | Yes | Yes | 0.06932 | 4564100% | 2503874 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210574 | 122725 | Line - Allen - Quaker 115kV | Allen - Quaker 115 kV Ckt 1 Rebuild | Rebuild 3.6 miles 115 kV line from Allen to Quaker and upgrade any necessary terminal equipment to achieve a summer emergency rating of 300 MVA | 2020 ITP | Yes | Yes | 0.06932 | 4564100% | 1259112 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.2517 | 4574700% | 23820158 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.10306 | 4593900% | 12410868 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.10306 | 4614300% | 8323241 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04203 | 4568800% | 16516041 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04203 | 4565800% | 7099323 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.08097 | 4568800% | 38537430 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08097 | 4565800% | 5170350 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.08097 | 4565800% | 32342389 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | TBD | 170510 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild the AEPW portion of the SWEETWT6 to WHEELER6 230 kV line CKT1 (5 miles) to a minimum rating of 459 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.07314 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03399 | 4602200% | 1130397 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03399 | 4602200% | 401187 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 210642 | 112401 | Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 2021 ITP | Yes | Yes | 0.19615 | 4471300% | 0 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 380 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.07088 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2020-060 | 05 SOUTHWEST | ERIS |  | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.15935 | TBD | 800000 | 800000
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.0857 | 4710200% | 10545000 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.0857 | 4710200% | 11707581 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.0857 | 4710200% | 5577000 | 0
GEN-2020-060 | 05 SOUTHWEST | ERIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.0857 | 4710200% | 11011685 | 0
GEN-2020-061 | 03 CENTRAL | ERIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.0548 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2020-061 | 03 CENTRAL | NRIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.03771 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2020-061 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04271 | 4602300% | 24319368 | 24319368
GEN-2020-061 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | DISIS-2017-002 | Yes | Yes | 0.05134 | TBD (36 month lead time) | TBD | TBD
GEN-2020-064 | 03 CENTRAL | ERIS | TBD | TBD | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 miles of 161 kV from Aurora H.T. to Monett | 2024 ITP | Yes | Yes | 0.10876 | TBD | 16004214 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | TBD | TBD | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Rebuild 9.9 miles of 161 kV from Branson North - Branson Northwest - North Branson - Reeds Spring | 2024 ITP | Yes | Yes | 0.04024 | TBD | 17108010 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04271 | 4593800% | 121709542 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04271 | 4593800% | 5915803 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04271 | 4593100% | 3909824 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | TBD | TBD | N Reeds Spring - S Reeds Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 miles of 161 kV from N Reeds Spring to S Reeds Spring | 2024 ITP | Yes | Yes | 0.04018 | TBD | 2673366 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08249 | 4602200% | 1130397 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08249 | 4602200% | 401187 | 0
GEN-2020-064 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.03031 | 4602200% | 1534495 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.24237 | 4576700% | 6000000 | 6000000
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.24237 | 4574700% | 23820158 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09964 | 4593900% | 12410868 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09964 | 4614300% | 8323241 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.10432 | 4615700% | 196135074 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.10432 | 4580700% | 18707251 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.10432 | 4580700% | 19630748 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0415 | 4568800% | 16516041 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.0415 | 4565800% | 7099323 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.08272 | 4568800% | 38537430 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08272 | 4565800% | 5170350 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.08272 | 4565800% | 32342389 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03443 | 4602200% | 1130397 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03443 | 4602200% | 401187 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 210642 | 112401 | Sub - Lubbock South - Jones 230 kV Ckt 1 & 2 Terminal Upgrades | Lubbock South - Jones 230kV Ckt 2 Terminal Upgrades | Increase clearances and upgrade any necessary terminal equipment at Jones and/or Lubbock South 230 kV station | 2021 ITP | Yes | Yes | 0.03454 | 4471300% | 0 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS |  | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.07403 | TBD | 800000 | 800000
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09281 | 4710200% | 10545000 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09281 | 4710200% | 5577000 | 0
GEN-2020-065 | 05 SOUTHWEST | ERIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.09281 | 4710200% | 9643705 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.23568 | 4576700% | 6000000 | 6000000
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.23568 | 4574700% | 23820158 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09612 | 4593900% | 12410868 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09612 | 4614300% | 8323241 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.07448 | 4615700% | 196135074 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.07448 | 4580700% | 18707251 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.07448 | 4580700% | 19630748 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.06505 | 4568800% | 38537430 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06505 | 4565800% | 5170350 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.06505 | 4565800% | 32342389 | 0
GEN-2020-067 | 05 SOUTHWEST | ERIS | TBD | 170510 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild SWEETWT6 to WHEELER6 230 kV Line 1 | Rebuild the AEPW portion of the SWEETWT6 to WHEELER6 230 kV line CKT1 (5 miles) to a minimum rating of 459 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.07748 | TBD (36 month lead time) | 12000000 | 12000000
GEN-2020-067 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 380 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.06616 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2020-013 | 02 NEBRASKA | NRIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.0401 | 4556600% | 5468352 | 5468352
GEN-2020-013 | 02 NEBRASKA | NRIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.04045 | 4602300% | 1173160 | 1173160
GEN-2020-013 | 02 NEBRASKA | NRIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.04045 | 4602300% | 5928037 | 5928037
GEN-2020-025 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03171 | 4602300% | 24319368 | 24319368
GEN-2020-028 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03171 | 4602300% | 24319368 | 24319368
GEN-2020-031 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03171 | 4602300% | 24319368 | 24319368
GEN-2020-078 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03437 | 4602300% | 24319368 | 24319368
GEN-2020-084 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03809 | 4602300% | 24319368 | 24319368
GEN-2020-094 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.08241 | 4602300% | 24319368 | 24319368
GEN-2020-094 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.06804 | 4602300% | 24319368 | 24319368
GEN-2020-002 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.18119 | 4748300% | 2849669 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.18119 | 4638800% | 114179 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 2849669 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 6114594 | 0
GEN-2020-025 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4638800% | 114179 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 2849669 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 6114594 | 0
GEN-2020-028 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4638800% | 114179 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 2849669 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4748300% | 6114594 | 0
GEN-2020-031 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.09921 | 4638800% | 114179 | 0
GEN-2020-072 | 03 CENTRAL | ERIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.14416 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2020-072 | 03 CENTRAL | NRIS | TBD | TBD | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Archie 161 kV Terminal Equipment Upgrade (DISIS-2017-002) | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.16056 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2020-072 | 03 CENTRAL | ERIS | TBD | 156851 | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.14416 | TBD (36 month lead time) | 41157960 | 41157960
GEN-2020-072 | 03 CENTRAL | NRIS | TBD | 156851 | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Archie to G17-108-TAP 161 kV Rebuild (DISIS-2017-002) | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.16056 | TBD (36 month lead time) | 41157960 | 41157960
GEN-2020-072 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03207 | 4602300% | 24319368 | 24319368
GEN-2020-072 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03347 | 4602200% | 1130397 | 0
GEN-2020-072 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03347 | 4602200% | 401187 | 0
GEN-2020-072 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.05405 | 4602200% | 1534495 | 0
GEN-2020-072 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | DISIS-2017-002 | Yes | Yes | 0.2355 | TBD (36 month lead time) | TBD | TBD
GEN-2020-072 | 03 CENTRAL | NRIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton to achieve a minimum rating of 450 MVA (owned by AECI, will be addressed in the AFS) | DISIS-2017-002 | Yes | Yes | 0.26034 | TBD (36 month lead time) | TBD | TBD
GEN-2020-075 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.12871 | 4565800% | 32342389 | 0
GEN-2020-081 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.04566 | 4565800% | 647852 | 0
GEN-2020-081 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03792 | 4568800% | 16516041 | 0
GEN-2020-081 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.03792 | 4565800% | 7099323 | 0
GEN-2020-081 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.03617 | 4565800% | 32342389 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210616 | 122858 | Multi - Minco - Pleasant Valley - Draper 345 kV | Cimarron - Draper 345 kV Terminal Upgrades #2 | Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA | 2020 ITP | Yes | Yes | 0.03481 | 4565800% | 647852 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04147 | 4568800% | 16516041 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210616 | 143176 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper 345 kV Terminal Equipment | Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. | 2020 ITP | Yes | Yes | 0.04147 | 4565800% | 7099323 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.12871 | 4568800% | 38537430 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 2849669 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 6114594 | 0
GEN-2020-043 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4638800% | 114179 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 2849669 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 6114594 | 0
GEN-2020-044 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4638800% | 114179 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 2849669 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4748300% | 6114594 | 0
GEN-2020-045 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03649 | 4638800% | 114179 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.04016 | 4748300% | 2849669 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | TBD | TBD | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 miles of 161 kV from Aurora H.T. to Monett | 2024 ITP | Yes | Yes | 0.0806 | TBD | 16004214 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | TBD | TBD | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Rebuild 9.9 miles of 161 kV from Branson North - Branson Northwest - North Branson - Reeds Spring | 2024 ITP | Yes | Yes | 0.03058 | TBD | 17108010 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0384 | 4574800% | 28123307 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03723 | 4593800% | 121709542 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03723 | 4593800% | 5915803 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03723 | 4593100% | 3909824 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | TBD | TBD | N Reeds Spring - S Reeds Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 miles of 161 kV from N Reeds Spring to S Reeds Spring | 2024 ITP | Yes | Yes | 0.03052 | TBD | 2673366 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0887 | 4602200% | 1130397 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0887 | 4602200% | 401187 | 0
GEN-2020-079 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.08299 | 4602200% | 1534495 | 0
GEN-2020-079 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.0456 | 4602200% | 1534495 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210670 | 133085 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco - Pleasant Valley 345 kV Ckt 1 | Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. | 2020 ITP | Yes | Yes | 0.13853 | 4568800% | 38537430 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12871 | 4565800% | 5170350 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210616 | 122848 | Multi - Minco - Pleasant Valley - Draper 345 kV | Minco 345 kV Terminal Equipment | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.13853 | 4565800% | 5170350 | 0
GEN-2020-087 | 04 SOUTHEAST | ERIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.12871 | 4565800% | 32342389 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210616 | 122849 | Multi - Minco - Pleasant Valley - Draper 345 kV | Pleasant Valley 345/138 kV Substation (345 kV) | Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. | 2020 ITP | Yes | Yes | 0.13853 | 4565800% | 32342389 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03323 | 4599100% | 6741332 | 6741332
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03323 | 4586800% | 6580002 | 6580002
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03323 | 4589900% | 2195001 | 2195001
GEN-2020-083 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.12112 | TBD | 10061320 | 10061320
GEN-2020-083 | 01 NORTH | NRIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.15178 | TBD | 10061320 | 10061320
GEN-2020-083 | 01 NORTH | ERIS | TBD | 170494 | Build Strandahl to Black Tail 115 kV line | Build Strandahl to Black Tail 115 kV line | Build approximately 15 mile of new 115kV line from Strandahl to Black Tail | DISIS-2018-002/2019-001 | Yes | Yes | 0.03676 | TBD (36 month lead time) | 18000000 | 18000000
GEN-2020-083 | 01 NORTH | NRIS | TBD | 170494 | Build Strandahl to Black Tail 115 kV line | Build Strandahl to Black Tail 115 kV line | Build approximately 15 mile of new 115kV line from Strandahl to Black Tail | DISIS-2018-002/2019-001 | Yes | Yes | 0.03722 | TBD (36 month lead time) | 18000000 | 18000000
GEN-2020-083 | 01 NORTH | NRIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | No | 0.04208 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2020-083 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12112 | 4737300% | 9455440 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.15178 | 4737300% | 9455440 | 0
GEN-2020-083 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.11504 | 4737300% | 9263038 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12627 | 4737300% | 9263038 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04921 | 4638700% | 2070042 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05186 | 4638700% | 1786830 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.13934 | 4647800% | 2539625 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.13934 | 4647800% | 264000 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220742 | 157949 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Yankton Junction 115 kV Ckt 1 Terminal Upgrade | Upgrade any necessary terminal equipment at Yankton Junction 115 kV substation on the Yankton Junction to Gavins Point 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.13934 | 4574700% | 393298 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220742 | 157892 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron 'B' Tap 115 kV Ckt 1 Rebuild (NWE) | Rebuild 0.2 mile Ckt 1 line from Huron 115 kV substation to Huron 'B' Tap 115 kV substation | 2023 ITP | Yes | Yes | 0.03656 | TBD | 207080 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220742 | 157891 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron - Huron West Park 115 kV Ckt 1 Rebuild (NWE) | Rebuild 10.4 mile Ckt 1 line from Huron 115 kV substation to Huron West Park 115 kV substation | 2023 ITP | Yes | Yes | 0.05415 | TBD | 11554745 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220742 | 157724 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron B Tap 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron B Tap 115 kV substation on the Huron B Tap to Huron 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.05415 | TBD | 393298 | 0
GEN-2020-083 | 01 NORTH | NRIS | 220742 | 157721 | Line - Huron 'B' Tap 115 kV - Huron 115 kV - Huron West Park 115 kV Rebuild | Huron West Park 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Huron West Park 115 kV substation on the Huron West Park to Huron 'B' Tap 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.03656 | TBD | 393298 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.05006 | 4566600% | 770086 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.06434 | 4566600% | 770086 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.05006 | 4590100% | 66041 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.05006 | 4590100% | 323364 | 0
GEN-2020-083 | 01 NORTH | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03842 | 4574800% | 28123307 | 0
GEN-2020-083 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04554 | 4675200% | 224639813 | 0
GEN-2020-083 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04158 | 4675200% | 254838000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04554 | 4675200% | 16186000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04158 | 4675200% | 842000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.16113 | 4562600% | 18251841 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.15995 | 4562600% | 18251841 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.15518 | 4562600% | 6394630 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.15713 | 4562600% | 6394630 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210663 | 144163 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Folvag 115 kV Terminal Equipment | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | 2021 ITP | Yes | Yes | 0.03886 | 4565700% | 500000 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210663 | 144163 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | Folvag 115 kV Terminal Equipment | Install terminal equipment at Folvag 115 kV sub to accommodate new 115 kV line from NE Williston 115 kV sub. | 2021 ITP | Yes | Yes | 0.03925 | 4565700% | 500000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210663 | 144177 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston - Folvag 115 kV New Line | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | 2021 ITP | Yes | Yes | 0.03886 | 4565700% | 8700000 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210663 | 144177 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston - Folvag 115 kV New Line | Build a new 4.5 mile 115 kV line from NE Williston to Folvag. | 2021 ITP | Yes | Yes | 0.03925 | 4565700% | 8700000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210663 | 144178 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston 115 kV Terminal Equipment | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | 2021 ITP | Yes | Yes | 0.03886 | 4565700% | 500000 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210663 | 144178 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | NE Williston 115 kV Terminal Equipment | Install terminal equipment at NE Williston 115 kV sub to accommodate new 115 kV line from Folvag 115 kV sub. | 2021 ITP | Yes | Yes | 0.03925 | 4565700% | 500000 | 0
GEN-2020-083 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05313 | 4602300% | 24319368 | 24319368
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.13016 | 4635600% | 82718831 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.13676 | 4635600% | 82718831 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.12972 | 4635600% | 18932308 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.13676 | 4635600% | 18932308 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.12972 | 4635600% | 385021 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.13676 | 4635600% | 385021 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.12972 | 4635600% | 214157775 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.13791 | 4635600% | 214157775 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.12972 | 4635600% | 10502349 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.13791 | 4635600% | 10502349 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.13016 | 4635600% | 5085047 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.13676 | 4635600% | 5085047 | 0
GEN-2020-083 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04246 | 4602200% | 243120 | 0
GEN-2020-083 | 01 NORTH | NRIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.03055 | 4602200% | 243120 | 0
GEN-2020-078 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.04016 | 4638800% | 114179 | 0
GEN-2020-013 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1 | Rebuild the existing HOLDREG7 to G20-013-TAP 115 kV line 1 (19 miles) to a minimum rating of 215 MVA | DISIS-2020-001 | Yes | No | 0.99689 | TBD (36 month lead time) | 14500000 | 14500000
GEN-2020-084 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | DISIS-2020-001 | Yes | No | 0.76173 | TBD (36 month lead time) | 1101824 | 1101824
GEN-2020-011 | 02 NEBRASKA | NRIS | TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Yes | Yes | 0.04032 | TBD (36 month lead time) | 8300000 | 8300000
GEN-2020-013 | 02 NEBRASKA | NRIS | TBD | 156456 | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer | Replace Mark Moore 345/115 kV Transformer to achieve a minimum rating of 400 MVA | DISIS-2017-002 | Yes | Yes | 0.038 | TBD (36 month lead time) | 8300000 | 8300000
GEN-2020-011 | 02 NEBRASKA | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04501 | 4602200% | 1130397 | 0
GEN-2020-011 | 02 NEBRASKA | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04501 | 4602200% | 401187 | 0
GEN-2020-013 | 02 NEBRASKA | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03836 | 4602200% | 1130397 | 0
GEN-2020-013 | 02 NEBRASKA | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03836 | 4602200% | 401187 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05631 | 4605200% | 5300000 | 5300000
GEN-2020-012 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03719 | 4605200% | 5300000 | 5300000
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03273 | 4605200% | 5300000 | 5300000
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0361 | 4593800% | 121709542 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0361 | 4593800% | 5915803 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0361 | 4593100% | 3909824 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0755 | 4593800% | 121709542 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0755 | 4593800% | 5915803 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0755 | 4593100% | 3909824 | 0
GEN-2020-020 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03679 | 4593800% | 121709542 | 0
GEN-2020-020 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03679 | 4593800% | 5915803 | 0
GEN-2020-020 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03679 | 4593100% | 3909824 | 0
GEN-2020-054 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03628 | 4593800% | 121709542 | 0
GEN-2020-054 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03628 | 4593800% | 5915803 | 0
GEN-2020-054 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03628 | 4593100% | 3909824 | 0
GEN-2020-081 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 4593800% | 121709542 | 0
GEN-2020-081 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 4593800% | 5915803 | 0
GEN-2020-081 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 4593100% | 3909824 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07271 | 4593800% | 121709542 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07271 | 4593800% | 5915803 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07271 | 4593100% | 3909824 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06594 | 4593800% | 121709542 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06594 | 4593800% | 5915803 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | TBD | TBD | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 miles of 161 kV from Aurora H.T. to Monett | 2024 ITP | Yes | Yes | 0.1991 | TBD | 16004214 | 0
GEN-2020-088 | 03 CENTRAL | NRIS | TBD | TBD | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.5 miles of 161 kV from Aurora H.T. to Monett | 2024 ITP | Yes | Yes | 0.09588 | TBD | 16004214 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | TBD | TBD | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Rebuild 9.9 miles of 161 kV from Branson North - Branson Northwest - North Branson - Reeds Spring | 2024 ITP | Yes | Yes | 0.03058 | TBD | 17108010 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0372 | 4593800% | 121709542 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0372 | 4593800% | 5915803 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0372 | 4593100% | 3909824 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | TBD | TBD | N Reeds Spring - S Reeds Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 miles of 161 kV from N Reeds Spring to S Reeds Spring | 2024 ITP | Yes | Yes | 0.07043 | TBD | 2673366 | 0
GEN-2020-088 | 03 CENTRAL | NRIS | TBD | TBD | N Reeds Spring - S Reeds Spring 161 kV Rebuild | N Reeds Spring - S Reeds Spring 161 kV Rebuild | Rebuild 1.5 miles of 161 kV from N Reeds Spring to S Reeds Spring | 2024 ITP | Yes | Yes | 0.03227 | TBD | 2673366 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07618 | 4602200% | 1130397 | 0
GEN-2020-088 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07618 | 4602200% | 401187 | 0
GEN-2020-088 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.06261 | 4602200% | 1534495 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220770 | 158640 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 115 kV | Build a new 115 kV substation at the new intersection of West Gardner-Craig and Atlantic-Eudora Township. | 2023 ITP | Yes | Yes | 0.03137 | 4574800% | 17693519 | 0
GEN-2020-090 | 03 CENTRAL | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05499 | 4574800% | 28123307 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.07634 | 4574800% | 28123307 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220771 | 158646 | Multi - Atlantic- Craig - West Gardener 345/115 kV | West Gardner - Craig 345 kV | Extend the existing West Gardner - Craig 345 kV line 10.3 miles to intersect with the Atlantic – Eudora Township 115 kV line. | 2023 ITP | Yes | Yes | 0.03137 | 4574800% | 29532119 | 0
GEN-2020-090 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14971 | 4602200% | 1130397 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.19455 | 4602200% | 1130397 | 0
GEN-2020-090 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14971 | 4602200% | 401187 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.19455 | 4602200% | 401187 | 0
GEN-2020-090 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.20589 | 4602200% | 1534495 | 0
GEN-2020-090 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.24028 | 4602200% | 1534495 | 0
GEN-2020-091 | 01 NORTH | ERIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.13126 | TBD | 10061320 | 10061320
GEN-2020-091 | 01 NORTH | NRIS |  | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace Broadland 345/230kV transformer to 471 MVA minimum rating | DISIS-2017-001 | Yes | Yes | 0.06628 | TBD | 10061320 | 10061320
GEN-2020-091 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.13126 | 4737300% | 9455440 | 0
GEN-2020-091 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.06628 | 4737300% | 9455440 | 0
GEN-2020-091 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.12097 | 4737300% | 9263038 | 0
GEN-2020-091 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.06823 | 4737300% | 9263038 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04958 | 4638700% | 2070042 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05206 | 4638700% | 1786830 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210648 | 122734 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Oahe 230 kV Terminal Upgrades (WAPA) | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 2021 ITP | Yes | Yes | 0.05116 | 4566600% | 770086 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.05116 | 4590100% | 66041 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.05116 | 4590100% | 323364 | 0
GEN-2020-091 | 01 NORTH | ERIS | 220771 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03849 | 4574800% | 28123307 | 0
GEN-2020-091 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0466 | 4675200% | 224639813 | 0
GEN-2020-091 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04284 | 4675200% | 254838000 | 0
GEN-2020-091 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0466 | 4675200% | 16186000 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04284 | 4675200% | 842000 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.20552 | 4562600% | 18251841 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.20285 | 4562600% | 18251841 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04037 | 4562600% | 6394630 | 0
GEN-2020-091 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05283 | 4602300% | 24319368 | 24319368
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.11054 | 4635600% | 82718831 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.07853 | 4635600% | 82718831 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.0995 | 4635600% | 18932308 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.07853 | 4635600% | 18932308 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.0995 | 4635600% | 385021 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.07853 | 4635600% | 385021 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.0995 | 4635600% | 214157775 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.06953 | 4635600% | 214157775 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.0995 | 4635600% | 10502349 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.06953 | 4635600% | 10502349 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.11054 | 4635600% | 5085047 | 0
GEN-2020-091 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.07853 | 4635600% | 5085047 | 0
GEN-2020-091 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04337 | 4602200% | 243120 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06594 | 4593100% | 3909824 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS |  | 158555 | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 170 MVA | DISIS-2018-001 | Yes | Yes | 0.03089 | TBD (30 month lead time) | 5006798 | 5006798
GEN-2020-020 | 04 SOUTHEAST | NRIS | TBD | 158555 | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 170 MVA | DISIS-2018-001 | Yes | Yes | 0.03519 | TBD (30 month lead time) | 5006798 | 5006798
GEN-2020-010 | 04 SOUTHEAST | NRIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.0576 | 4580700% | 24000 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04004 | 4602200% | 1130397 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03406 | 4602200% | 1130397 | 0
GEN-2020-010 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04004 | 4602200% | 401187 | 0
GEN-2020-010 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03406 | 4602200% | 401187 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04618 | 4602200% | 1130397 | 0
GEN-2020-012 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04618 | 4602200% | 401187 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04001 | 4602200% | 1130397 | 0
GEN-2020-087 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04001 | 4602200% | 401187 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0701 | 4602200% | 1130397 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03087 | 4602200% | 1130397 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0701 | 4602200% | 401187 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03087 | 4602200% | 401187 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.05007 | 4602200% | 1534495 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a summer emergency rating of 870 MVA. | 2023 ITP | Yes | Yes | 0.03648 | 4602200% | 1534495 | 0
GEN-2020-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Tulsa North 345/138 kV Ckt 2 Transformer | Tulsa North 345/138 kV Ckt 2 Transformer | Add a second 345/138 kV transformer at Tulsa North | 2024 ITP | Yes | Yes | 0.05441 | TBD | 18206020 | 0
GEN-2020-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Tulsa North 345/138 kV Ckt 2 Transformer | Tulsa North 345/138 kV Ckt 2 Transformer | Add a second 345/138 kV transformer at Tulsa North | 2024 ITP | Yes | Yes | 0.0405 | TBD | 18206020 | 0
GEN-2020-020 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.04634 | 4608200% | 5250000 | 0
GEN-2020-020 | 04 SOUTHEAST | NRIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.03738 | 4608200% | 5250000 | 0
GEN-2020-054 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.03626 | 4608200% | 5250000 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 220743 | 157384 | XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade | Fremont 115/69 kV Transformer Ckt 2 (115 kV) | Install 115 kV terminal equipment to support 115/69 transformer at Fremont 115 kV substation | 2023 ITP | Yes | Yes | 0.0436 | 4675200% | 300000 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 220743 | 157383 | XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade | Sub 976 115/69 kV Transformer Ckt 2 (69 kV) | Install new 115/69 transformer at Fremont 115 kV substation | 2023 ITP | Yes | Yes | 0.0436 | 4675200% | 5700000 | 0
GEN-2020-002 | 02 NEBRASKA | ERIS | 220744 | 158445 | XFR - Fremont 115/69 kV & Sub 976 Terminal Upgrade | Sub 976 69 kV Terminal Equipment | Install 69 kV terminal equipment at Sub 976 to support a new 115/69 kV transformer | 2023 ITP | Yes | Yes | 0.0436 | 4675200% | 165695 | 0

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | DISIS-2020-001 | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.06846 | 101.71 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.06515 | 101.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.10309 | 103.42 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.07962 | 108.05 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542965 W.GRDNR7 345 997280 WEST GARDN11 161 11 | 535 | 535 | 0.09991 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.04128 | 107.68 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-007 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.03888 | 107.44 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-007 | TO->FROM | 542966 WGARDNR5 161 997277 WEST GARDN11 161 11 | 535 | 535 | 0.07962 | 107.7 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-007 | TO->FROM | 542966 WGARDNR5 161 997280 WEST GARDN11 161 11 | 535 | 535 | 0.09991 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.67 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.66 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 164.64 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 162.25 | P11:69:NPPD:ORLEANS8:2:4:: | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 106.46 | 764447 G20-013-SS2 115 764448 G20-013-SS3 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 106.46 | 764444 G20-013-XFM3 34.5 764448 G20-013-SS3 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 106.46 | 764441 G20-013-XFM2 34.5 764447 G20-013-SS2 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 106.46 | 764435 GEN-2020-013 115 764446 G20-013-SS1 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99988 | 106.46 | 764438 G20-013-XFM1 34.5 764446 G20-013-SS1 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.66 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.66 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.9999 | 163.12 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.9999 | 160.81 | P11:69:NPPD:ORLEANS8:2:4:: | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.65 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.65 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.9999 | 163.21 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 02ALL | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.9999 | 160.85 | P11:69:NPPD:ORLEANS8:2:4:: | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.64 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.64 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99675 | 162.46 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.65 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.65 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99691 | 162.57 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.68 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 1 | 175.68 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99687 | 105.87 | 764447 G20-013-SS2 115 764448 G20-013-SS3 115 1 | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-013 | TO->FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 | 120 | 0.99687 | 164.01 | Base Case | TDF Impact | Rebuild the HOLDREG7 to G20-013-TAP 115kV Line 1
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.83 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.84 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.83 | POI 640510_1 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.76 | POI 640510_4 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.75 | POI 640510_5 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.69 | POI 640510_7 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.83 | POI 640510_8 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.09 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.11 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.09 | POI 640510_1 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.03 | POI 640510_4 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.02 | POI 640510_5 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 106.96 | POI 640510_7 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | FROM->TO | 652506 FTTHOMP3 345 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.09 | POI 640510_8 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 105.05 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 105.07 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 105.05 | POI 640510_1 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.97 | POI 640510_4 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.97 | POI 640510_5 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 104.89 | POI 640510_7 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996646 FT2 KU1B 230 1 | 250 | 313 | 0.26284 | 105.05 | POI 640510_8 | TDF Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.32 | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.34 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.32 | POI 640510_1 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.24 | POI 640510_4 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.24 | POI 640510_5 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.16 | POI 640510_7 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 01ALL | 1 | 27L | GEN-2020-021 | TO->FROM | 652507 FTTHOMP4 230 996647 FT2 KU1A 230 1 | 250 | 313 | 0.26852 | 107.32 | POI 640510_8 | Cumulative Impact | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3
Thermal | DISIS-2020-001 | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.04698 | 101.71 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.04338 | 101.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 311 | 334 | 0.05991 | 109.61 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | TDF Impact | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.17062 | 103.42 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.14717 | 108.05 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542965 W.GRDNR7 345 997280 WEST GARDN11 161 11 | 535 | 535 | 0.16747 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.07239 | 107.68 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-057 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.06998 | 107.44 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-057 | TO->FROM | 542966 WGARDNR5 161 997277 WEST GARDN11 161 11 | 535 | 535 | 0.14717 | 107.7 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-057 | TO->FROM | 542966 WGARDNR5 161 997280 WEST GARDN11 161 11 | 535 | 535 | 0.16747 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.04698 | 101.71 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 311 | 334 | 0.04338 | 101.48 | 541198 PECULR 7 345 542968 STILWEL7 345 1 | TDF Impact | Rebuild the STILWEL5 to REDEL 5 161 kV line 1
Thermal | DISIS-2020-001 | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 311 | 334 | 0.05991 | 109.61 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 | TDF Impact | Rebuild the CRAIG 5 to LENEXA 5 161 kV line 2
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.17062 | 103.42 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997277 WEST GARDN11 161 11 | 535 | 535 | 0.14717 | 108.05 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542965 W.GRDNR7 345 997280 WEST GARDN11 161 11 | 535 | 535 | 0.16747 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.07239 | 107.68 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27SP | GEN-2020-058 | FROM->TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 334 | 334 | 0.06998 | 107.44 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-058 | TO->FROM | 542966 WGARDNR5 161 997277 WEST GARDN11 161 11 | 535 | 535 | 0.14717 | 107.7 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 CF | 00NR | 1 | 24SP | GEN-2020-058 | TO->FROM | 542966 WGARDNR5 161 997280 WEST GARDN11 161 11 | 535 | 535 | 0.16747 | 107.89 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | TDF Impact | Multi - Atlantic - Craig - West Gardener 345-115 kV
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05806 | 103.19 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05794 | 103.87 | P42:345:OKGE:SB_CION7384:::: | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05827 | 102.13 | P42:345:OKGE:SB_MICO7301:::: | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05854 | 100.93 | P42:345:OKGE:SB_MICO7312:::: | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05827 | 102.13 | Potential P4 Event - POI 514801_0 | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05854 | 100.93 | Potential P4 Event - POI 514801_1 | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.05806 | 103.19 | Potential P4 Event - POI 514801_3 | Cumulative Impact | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 112.79 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 | TDF Impact | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
Thermal | DISIS-2020-001 | 00ALL | 1 | 27SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 113.21 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 | TDF Impact | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
Thermal | DISIS-2020-001 | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 |  | 797 | 1 | 124.12 | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 | TDF Impact | Sidewinder to Hobbs 345 kV Lidar Clearance Correction
Thermal | DISIS-2020-001 | 00ALL | 1 | 24SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 545 | 1 | 165.23 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | TDF Impact | Sidewinder to Andrews 345 kV Lidar Clearance Correction
Thermal | DISIS-2020-001 | 00ALL | 1 | 27SP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 545 | 1 | 164.79 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | TDF Impact | Sidewinder to Andrews 345 kV Lidar Clearance Correction
Thermal | DISIS-2020-001 | 00ALL | 1 | 27WP | GEN-2020-065 | FROM->TO | 527020 SIDEWINDER 7 345 528604 ANDREWS 6 345 1 |  | 606 | 1 | 163.01 | 527020 SIDEWINDER 7 345 527896 HOBBS_INT 7 345 1 | TDF Impact | Sidewinder to Andrews 345 kV Lidar Clearance Correction
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 24SP | GEN-2020-065 | " | Non-Converged |  |  | 0.83727 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 24SP | GEN-2020-065 | " | Non-Converged |  |  | 0.83727 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Hobbs to Andrews Voltage Conversion
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 27SP | GEN-2020-065 | " | Non-Converged |  |  | 0.8354 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 27SP | GEN-2020-065 | " | Non-Converged |  |  | 0.8354 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Hobbs to Andrews Voltage Conversion
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 27WP | GEN-2020-065 | " | Non-Converged |  |  | 0.83556 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Build New Andrews to Road Runner 345 kV Line
Non-Converged | DISIS-2020-001 | 00ALL | 0 | 27WP | GEN-2020-065 | " | Non-Converged |  |  | 0.83556 |  | 527020 SIDEWINDER 7 230 527894 HOBBS_INT 6 230 1 | TDF Impact | Hobbs to Andrews Voltage Conversion
Thermal | DISIS-2020-001 CF | 05ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 02ALL | 1 | 27WP | GEN-2020-084 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.68236 | 100.65 | P23:345:MEC:LEHIGH:360::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-083 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07185 | 105.99 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-083 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07201 | 106.45 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-083 | TO->FROM | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 342 | 342 | 0.07201 | 106.45 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 | TDF Impact | Fargo 230 kV Terminal Upgrade
Thermal | DISIS-2020-001 | 04ALL | 1 | 27WP | GEN-2020-092 | FROM->TO | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 |  | 188 | 0.2597 | 110.29 | 510419 PRY-JCT4 138 764160 G20-092-TAP 138 1 | TDF Impact | Catoosa Terminal Upgrade (Model Correction)
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-094 | FROM->TO | 640277 MOORE 3 345 996875 MOORE T1 115 1 | 336 | 336 | 0.03009 | 115.76 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1:: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Thermal | DISIS-2020-001 CF | 00NR | 1 | 27WP | GEN-2020-094 | TO->FROM | 640278 SHELDON7 115 996875 MOORE T1 115 1 | 336 | 336 | 0.03009 | 108.08 | P12:345:LES:L8589::WAGENER.103&ROKEBY.CKT1:: | TDF Impact | Replace Mark Moore 345/115 kV Transformer
Non-Converged | DISIS-2020-001 | 00NR | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 00NR | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 00NR | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 01ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 01ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 01ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 01ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 01ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 01ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 01ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 01NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 01NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 02ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 02ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 02ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 02ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 02ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 02NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 02NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 03ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 03ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 03ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 03ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 03ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 03NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 03NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 04ALL | 1 | 24SP | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 04ALL | 1 | 27SP | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 04ALL | 1 | 27L | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 04ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 05ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 05ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 05ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 05ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 05ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 05ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 05ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 05ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 | 05NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 00NR | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 00NR | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 00NR | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 01ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 01ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 01ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 01ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 01ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 01ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 01ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 01ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 01NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 01NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 02ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 02ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 02ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 02ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 02ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 02ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 02ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 02ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 02NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 02NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 03ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 03ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 03ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 03ALL | 1 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 03NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 03NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 04ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 04ALL | 1 | 24SP | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 04ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 04ALL | 1 | 27L | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 04ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 04ALL | 1 | 27WP | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 04ALL | 1 | 27SP | N/A | FROM -> TO | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 04ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 04NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 05ALL | 0 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 05ALL | 1 | 24SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 05ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 05ALL | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 05ALL | 0 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 05ALL | 1 | 27SP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 05ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2020-001 CF | 05NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2020-001 CF | 05NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None

## All Voltage
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME | Upgrade Name
Voltage | DISIS-2020-001 | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 01ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 01ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 01ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 01ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 01NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 02ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 02ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 02NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 03NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 | 05NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00NR | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00NR | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 00NR | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 01ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 01ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 01ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 01ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 01NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 02ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 02ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 02NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 03ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 03ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 03NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 04ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 04NR | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 05ALL | 2 | 27L | N/A | None | [7 empty] | None | None
Voltage | DISIS-2020-001 CF | 05NR | 2 | 27L | N/A | None | [7 empty] | None | None

## Stability Analysis Results
Group | Study Name | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | GLNDCT2G (661101) loses synchronism following fault clearance. The issue is also observed in the base case and is not impacted by any CQ requests. | The issue is resolved by removal of reclosing action. This mitigation is also required in the base case.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON units (608891, 608894, 608895, 608897, 608898) | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on GRE-MCHENRY7115.00 (615348) 115 kV Bus a. Apply fault at the GRE-MCHENRY7115.00 (615348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.2. NEW FRONT W (615145) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.7. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in GARISN4G (652460) and GARISN5G (652461). | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.)
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | FTPECK4G (652414) and FTPECK5G (652415) lose synchronism following fault clearance. The issue is also observed in the base case with no impact from the CQ units. | The issue is resolved by removal of reclosing action. This mitigation is also required in the base case.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.3. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.4. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.5. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON units (608891, 608894, 608895, 608897, 608898) | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips OAKTREE WIND (660013). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on NORTHBEND4 230.00 (652516) 230 kV Bus a. Apply fault at the NORTHBEND4 230.00 (652516) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency and voltage protection trips GRPR11 (645065), GRPR12 (645066), GRPR21 (645067), and GRPR22 (645068). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to GEN-2018-069 (763043) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | PS_RCP.A-BEG (659431) and PS_RCP.B-BEG (659432) loses synchronism following fault Clearance. The issue is also observed in the base case. | Reduce the clearing time to 6 cycles. The same critical clearing time was observed in the base case.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | LEWIS72G (661104) loses synchronism following fault clearance. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.)
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on MAURINE 2 345.00 (800121) 345 kV Bus a. Apply fault at the MAURINE 2 345.00 (800121) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips G19-037 (763706). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on RAUN 3 (635200) 345.0 kV Bus a. Apply fault at the RAUN 3 (635200) 345.0 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_064 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_065 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_066 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_067 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_068 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_069 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_070 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_071 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_072 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_073 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to NUNDRWD4 (652484) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_074 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_076 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_078 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_079 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_080 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_081 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_082 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply Fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NELSON 7 115.00 (652440) 115 kV Bus a. Apply Fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.6. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.3. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BALDWIN_-PP4230.00 (659365) 230 kV Bus a. Apply Fault at the BALDWIN_-PP4230.00 (659365) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.2. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.3. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.4. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.5. BALDWIN_-PP4 (659365) 230.0 kV to BALDWIN_-PP9 (659367) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CABINCR7 115.00 (661033) 115 kV Bus a. Apply Fault at the CABINCR7 115.00 (661033) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. CABINCR7 (661033) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 b.3. BAKER 7 (661005) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.5. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.6. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on POPLAR 7 115.00 (661075) 115 kV Bus a. Apply Fault at the POPLAR 7 115.00 (661075) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply Fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 b.4. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.5. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 b.5. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply Fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.4. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply Fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.2. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z b.3. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 b.4. OKOBOJO-ER8 (655334) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.5. MOS-SLY2-ER8 (655373) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.6. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.7. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.5. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.6. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 b.6. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.7. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD7 (652408) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.7. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.8. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.9. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.3. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on PEMBROOK-ER869.000 (655339) 69 kV Bus a. Apply Fault at the PEMBROOK-ER869.000 (655339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 b.7. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.8. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.9. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.10. PEMBROOK-ER8 (655339) 69.0 kV to NBCS_09_-PPR (659277) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 b.5. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.6. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.7. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.8. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on SQUAWGAP-BE7115.00 (659191) 115 kV Bus a. Apply Fault at the SQUAWGAP-BE7115.00 (659191) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.4. SKAAR___-MK7 (655860) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.7. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on ND.PW1__-BE934.500 (659325) 34.5 kV Bus a. Apply Fault at the ND.PW1__-BE934.500 (659325) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.6. ND.PW1__-BE7 (659190) 115.0 kV to ND.PW1__-BE9 (659325) 34.5 kV Two Winding #1 b.7. ND.PW1__-BE9 (659325) 34.5 kV to ND.PW1__-BEW (659194) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.9. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.5. TIOGA4 7 (661085) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on STANLEY7 115.00 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.5. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ANSON 7 115.00 (603200) 115 kV Bus a. Apply Fault at the ANSON 7 115.00 (603200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.5. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on COURT FDR2 934.500 (606098) 34.5 kV Bus a. Apply Fault at the COURT FDR2 934.500 (606098) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.3. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.4. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.7. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.8. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.13. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.18. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.20. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.21. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.22. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.23. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.24. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.25. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.26. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OAKES 4 230.00 (620362) 230 kV Bus a. Apply Fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.7. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.7. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply Fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.5. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RUSHMORE-RM7115.00 (655763) 115 kV Bus a. Apply Fault at the RUSHMORE-RM7115.00 (655763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.5. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.6. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.6. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.7. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | GLNDCT2G (661101) loses synchronism following fault clearance. | The issue is resolved by removal of reclosing action.
01 NORTH | DISIS-2020-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | FTPECK4G (652414) and FTPECK5G (652415) lose synchronism following fault clearance. | The issue is resolved by removal of reclosing action.
01 NORTH | DISIS-2020-001 | 25S | Base | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | PS_RCP.A-BEG (659431) and PS_RCP.B-BEG (659432) loses synchronism following fault Clearance. | Reduce the clearing time to 6 cycles.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on GRE-MCHENRY7115.00 (615348) 115 kV Bus a. Apply fault at the GRE-MCHENRY7115.00 (615348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.2. NEW FRONT W (615145) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.7. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in GARISN4G (652460) and GARISN5G (652461). | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.)
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | FTPECK4G (652414) and FTPECK5G (652415) lose synchronism following fault clearance. The issue is also observed in the base case with no impact from the CQ units. | The issue is resolved by removal of reclosing action. This mitigation is also required in the base case.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips TWAURA2 (659488) and TWAURA3 (659488). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.3. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.4. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.5. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on NORTHBEND4 230.00 (652516) 230 kV Bus a. Apply fault at the NORTHBEND4 230.00 (652516) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency and voltage protection trips GRPR11 (645065), GRPR12 (645066), GRPR21 (645067), and GRPR22 (645068). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to GEN-2018-069 (763043) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | PS_RCP.A-BEG (659431) and PS_RCP.B-BEG (659432) loses synchronism following fault Clearance. The issue is also observed in the base case. | Reduce the clearing time to 6 cycles. The same critical clearing time was observed in the base case.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on MAURINE 2 345.00 (800121) 345 kV Bus a. Apply fault at the MAURINE 2 345.00 (800121) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips BISON units (608891, 608894, 608895, 608897, 608898) | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on RAUN 3 (635200) 345.0 kV Bus a. Apply fault at the RAUN 3 (635200) 345.0 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_064 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_065 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_066 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_067 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_068 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_069 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips G17-048 (588873). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_070 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_071 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_072 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | No | No | No | No | No | No | No | The dynamic controllers of ASHGEN (615124, 657737, 657964, 657985) generating site cause a Non-Convergence that result in the simulation crashing. The disabling of these controllers allow the simulation to proceed and no issues are observed. The same observation was made in the base case and the CQ units were not found to impact the issue. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_073 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to NUNDRWD4 (652484) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_074 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_076 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_078 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_079 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_080 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_081 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_082 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply Fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NELSON 7 115.00 (652440) 115 kV Bus a. Apply Fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.6. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.3. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BALDWIN_-PP4230.00 (659365) 230 kV Bus a. Apply Fault at the BALDWIN_-PP4230.00 (659365) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.2. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.3. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.4. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.5. BALDWIN_-PP4 (659365) 230.0 kV to BALDWIN_-PP9 (659367) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CABINCR7 115.00 (661033) 115 kV Bus a. Apply Fault at the CABINCR7 115.00 (661033) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. CABINCR7 (661033) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 b.3. BAKER 7 (661005) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.5. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.6. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on POPLAR 7 115.00 (661075) 115 kV Bus a. Apply Fault at the POPLAR 7 115.00 (661075) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | No | Yes | Yes | Yes | Yes | Voltage at the generator site MPC03839 (67022) rises above 1.2 p.u. following fault clearance settling below the 1.1 p.u.. The issue is also observed in the base case. | The issue is related to the controllers on the MPC units and it is limited to generating station internal elements. No mitigation required.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply Fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 b.4. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.5. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 b.5. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply Fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.4. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply Fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.2. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z b.3. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 b.4. OKOBOJO-ER8 (655334) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.5. MOS-SLY2-ER8 (655373) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.6. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.7. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.5. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.6. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 b.6. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.7. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD7 (652408) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.7. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.8. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.9. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.3. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on PEMBROOK-ER869.000 (655339) 69 kV Bus a. Apply Fault at the PEMBROOK-ER869.000 (655339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 b.7. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.8. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.9. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.10. PEMBROOK-ER8 (655339) 69.0 kV to NBCS_09_-PPR (659277) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 b.5. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.6. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.7. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.8. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on SQUAWGAP-BE7115.00 (659191) 115 kV Bus a. Apply Fault at the SQUAWGAP-BE7115.00 (659191) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.4. SKAAR___-MK7 (655860) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.7. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on ND.PW1__-BE934.500 (659325) 34.5 kV Bus a. Apply Fault at the ND.PW1__-BE934.500 (659325) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.6. ND.PW1__-BE7 (659190) 115.0 kV to ND.PW1__-BE9 (659325) 34.5 kV Two Winding #1 b.7. ND.PW1__-BE9 (659325) 34.5 kV to ND.PW1__-BEW (659194) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.9. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.5. TIOGA4 7 (661085) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on STANLEY7 115.00 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.5. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ANSON 7 115.00 (603200) 115 kV Bus a. Apply Fault at the ANSON 7 115.00 (603200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.5. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on COURT FDR2 934.500 (606098) 34.5 kV Bus a. Apply Fault at the COURT FDR2 934.500 (606098) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.3. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.4. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.7. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.8. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.13. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.18. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.20. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.21. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.22. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.23. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.24. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.25. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.26. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OAKES 4 230.00 (620362) 230 kV Bus a. Apply Fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.7. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.7. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply Fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.5. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | No | Yes | Yes | High voltage observed at MI CTYE (652411) following the fault. The issue is also observed in the base case. | Operational steady state fixes (transformer taps/voltage setpoints/switching shunts/etc.) and switching out the cap bank at MI CITY following the loss of the HVDC tie
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips GEN-2017-175 (762241 and 762244). | Protection disabled with no impact to stability.
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RUSHMORE-RM7115.00 (655763) 115 kV Bus a. Apply Fault at the RUSHMORE-RM7115.00 (655763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.5. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.6. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.6. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.7. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | FTPECK4G (652414) and FTPECK5G (652415) lose synchronism following fault clearance. | The issue is resolved by removal of reclosing action.
01 NORTH | DISIS-2020-001 | 25W | Base | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | PS_RCP.A-BEG (659431) and PS_RCP.B-BEG (659432) loses synchronism following fault Clearance. | Reduce the clearing time to 6 cycles.
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on GRE-MCHENRY7115.00 (615348) 115 kV Bus a. Apply fault at the GRE-MCHENRY7115.00 (615348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.2. NEW FRONT W (615145) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.7. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.3. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.4. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.5. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on NORTHBEND4 230.00 (652516) 230 kV Bus a. Apply fault at the NORTHBEND4 230.00 (652516) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to GEN-2018-069 (763043) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on MAURINE 2 345.00 (800121) 345 kV Bus a. Apply fault at the MAURINE 2 345.00 (800121) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on RAUN 3 (635200) 345.0 kV Bus a. Apply fault at the RAUN 3 (635200) 345.0 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_064 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_065 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_066 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_067 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_068 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_069 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_070 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_071 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_072 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_073 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to NUNDRWD4 (652484) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_074 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_076 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_078 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_079 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_080 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_081 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P1_REGIONAL_FAULT_082 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply Fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NELSON 7 115.00 (652440) 115 kV Bus a. Apply Fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.6. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.3. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BALDWIN_-PP4230.00 (659365) 230 kV Bus a. Apply Fault at the BALDWIN_-PP4230.00 (659365) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.2. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.3. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.4. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.5. BALDWIN_-PP4 (659365) 230.0 kV to BALDWIN_-PP9 (659367) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CABINCR7 115.00 (661033) 115 kV Bus a. Apply Fault at the CABINCR7 115.00 (661033) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. CABINCR7 (661033) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 b.3. BAKER 7 (661005) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.5. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.6. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on POPLAR 7 115.00 (661075) 115 kV Bus a. Apply Fault at the POPLAR 7 115.00 (661075) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply Fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 b.4. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.5. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 b.5. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply Fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.4. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply Fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.2. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z b.3. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 b.4. OKOBOJO-ER8 (655334) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.5. MOS-SLY2-ER8 (655373) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.6. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.7. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.5. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.6. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 b.6. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.7. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD7 (652408) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.7. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.8. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.9. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.3. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on PEMBROOK-ER869.000 (655339) 69 kV Bus a. Apply Fault at the PEMBROOK-ER869.000 (655339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 b.7. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.8. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.9. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.10. PEMBROOK-ER8 (655339) 69.0 kV to NBCS_09_-PPR (659277) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 b.5. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.6. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.7. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.8. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on SQUAWGAP-BE7115.00 (659191) 115 kV Bus a. Apply Fault at the SQUAWGAP-BE7115.00 (659191) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.4. SKAAR___-MK7 (655860) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.7. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on ND.PW1__-BE934.500 (659325) 34.5 kV Bus a. Apply Fault at the ND.PW1__-BE934.500 (659325) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.6. ND.PW1__-BE7 (659190) 115.0 kV to ND.PW1__-BE9 (659325) 34.5 kV Two Winding #1 b.7. ND.PW1__-BE9 (659325) 34.5 kV to ND.PW1__-BEW (659194) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.9. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.5. TIOGA4 7 (661085) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on STANLEY7 115.00 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.5. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ANSON 7 115.00 (603200) 115 kV Bus a. Apply Fault at the ANSON 7 115.00 (603200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.5. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on COURT FDR2 934.500 (606098) 34.5 kV Bus a. Apply Fault at the COURT FDR2 934.500 (606098) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.3. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.4. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.7. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.8. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.13. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.18. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.20. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.21. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.22. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.23. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.24. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.25. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.26. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OAKES 4 230.00 (620362) 230 kV Bus a. Apply Fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.7. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.7. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply Fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.5. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RUSHMORE-RM7115.00 (655763) 115 kV Bus a. Apply Fault at the RUSHMORE-RM7115.00 (655763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.5. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.6. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.6. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.7. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25S | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_001 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_002 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_003 | 3 Phase fault on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_004 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_005 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_006 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_007 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_008 | 3 Phase fault on GRE-MCHENRY7115.00 (615348) 115 kV Bus a. Apply fault at the GRE-MCHENRY7115.00 (615348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_009 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_010 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_011 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_012 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_013 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_014 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_015 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_016 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_017 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_018 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_020 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_021 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_022 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_023 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_024 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_025 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_026 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VELVA TAP (605634) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.2. NEW FRONT W (615145) 115.0 kV to GRE-MCHENRY7 (615348) 115.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_027 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_028 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_029 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_030 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_031 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_032 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_033 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_034 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_035 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_036 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_037 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_038 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_039 | 3 Phase fault on MAX_____-CP7115.00 (655690) 115 kV Bus a. Apply fault at the MAX_____-CP7115.00 (655690) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.2. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.4. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.5. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_040 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_041 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_042 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_043 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_044 | 3 Phase fault on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_045 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.6. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.7. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_046 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_047 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_048 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_049 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_050 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_051 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_052 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_053 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_054 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_055 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 b.7. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_056 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_057 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_058 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_059 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_060 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_061 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_062 | 3 Phase fault on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_063 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_064 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_065 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_066 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_067 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_068 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_069 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_070 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_071 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_072 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.4. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_073 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_074 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_075 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_076 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.3. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_077 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.3. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_078 | 3 Phase fault on ALEXANDR-MK7115.00 (655892) 115 kV Bus a. Apply fault at the ALEXANDR-MK7115.00 (655892) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 b.2. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_079 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_080 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.2. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_081 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 b.2. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 b.3. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_082 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_083 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_084 | 3 Phase fault on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.2. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_085 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_086 | 3 Phase fault on OSBORN -MW7115.00 (655919) 115 kV Bus a. Apply fault at the OSBORN -MW7115.00 (655919) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.2. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_087 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_088 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_089 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_090 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_091 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_092 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_093 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_094 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.2. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_095 | 3 Phase fault on CULBSN.E-BE7115.00 (659262) 115 kV Bus a. Apply fault at the CULBSN.E-BE7115.00 (659262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.4. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_096 | 3 Phase fault on E.SIDNEY-LY7115.00 (659186) 115 kV Bus a. Apply fault at the E.SIDNEY-LY7115.00 (659186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.2. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.3. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_097 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.3. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.4. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.5. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_098 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_099 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_100 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_101 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_102 | 3 Phase fault on GLENDIVE7 115.00 (652200) 115 kV Bus a. Apply fault at the GLENDIVE7 115.00 (652200) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVE7 (652200) 115.0 kV to GLENDCT7 (661032) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_103 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_104 | 3 Phase fault on GLENDIVEP2T7115.00 (652212) 115 kV Bus a. Apply fault at the GLENDIVEP2T7115.00 (652212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_105 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_106 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_107 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_108 | 3 Phase fault on FTTHOMP8 69.000 (652276) 69 kV Bus a. Apply fault at the FTTHOMP8 69.000 (652276) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP8 (652276) 69.0 kV to MOS-AMES-ER8 (655153) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_109 | 3 Phase fault on WARD 4 230.00 (652296) 230 kV Bus a. Apply fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_110 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_111 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_112 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_113 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_114 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_115 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_116 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_117 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_118 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_119 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_120 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_121 | 3 Phase fault on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_122 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_123 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV to OASIS___-MK7 (655879) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_124 | 3 Phase fault on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_125 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_126 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_127 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_128 | 3 Phase fault on KILDEER7 115.00 (652419) 115 kV Bus a. Apply fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_129 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_130 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_131 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_132 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_133 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_134 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_135 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_136 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_137 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_138 | 3 Phase fault on BELFELD4 230.00 (652425) 230 kV Bus a. Apply fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_139 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_140 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_141 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_142 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_143 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_144 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_145 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_146 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_147 | 3 Phase fault on NELSON 7 115.00 (652440) 115 kV Bus a. Apply fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_148 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_149 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_150 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_151 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_152 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_153 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_154 | 3 Phase fault on GARRISN7 115.00 (652442) 115 kV Bus a. Apply fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_155 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_156 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_157 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_158 | 3 Phase fault on DENBIGH TAP7115.00 (652464) 115 kV Bus a. Apply fault at the DENBIGH TAP7115.00 (652464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_159 | 3 Phase fault on HILKEN 4 230.00 (652466) 230 kV Bus a. Apply fault at the HILKEN 4 230.00 (652466) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_160 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_161 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_162 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_163 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_164 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_165 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_166 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_167 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_168 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_169 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_170 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_171 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_172 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_173 | 3 Phase fault on NORTHBEND4 230.00 (652516) 230 kV Bus a. Apply fault at the NORTHBEND4 230.00 (652516) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_174 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_175 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_176 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_177 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_178 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_179 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_180 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_181 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON_G-BE7 (659275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_182 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_183 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_184 | 3 Phase fault on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_185 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_186 | 3 Phase fault on WESSINGTON 4230.00 (652607) 230 kV Bus a. Apply fault at the WESSINGTON 4230.00 (652607) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_187 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_188 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to BEAVRHIL-GW4 (659535) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_189 | 3 Phase fault on MINGUSVILLE4230.00 (652616) 230 kV Bus a. Apply fault at the MINGUSVILLE4230.00 (652616) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGUSVILLE4 (652616) 230.0 kV to GEN-2018-069 (763043) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_190 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_191 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_192 | 3 Phase fault on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_193 | 3 Phase fault on CRANDALL-ER7115.00 (655411) 115 kV Bus a. Apply fault at the CRANDALL-ER7115.00 (655411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_194 | 3 Phase fault on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_195 | 3 Phase fault on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_196 | 3 Phase fault on HELMUT -LY7115.00 (655790) 115 kV Bus a. Apply fault at the HELMUT -LY7115.00 (655790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_197 | 3 Phase fault on BLUEBUTE-MK7115.00 (655832) 115 kV Bus a. Apply fault at the BLUEBUTE-MK7115.00 (655832) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBUTE-MK7 (655832) 115.0 kV to VEEDER -MK7 (655849) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_198 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to GRASSYBT-MK7 (655834) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_199 | 3 Phase fault on GRSYBTTP-MK7115.00 (655833) 115 kV Bus a. Apply fault at the GRSYBTTP-MK7115.00 (655833) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_200 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to TIMBERCK-MK7 (655844) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_201 | 3 Phase fault on INDIANHL-MK7115.00 (655838) 115 kV Bus a. Apply fault at the INDIANHL-MK7115.00 (655838) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANHL-MK7 (655838) 115.0 kV to NRTINDHL-MK7 (655850) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_202 | 3 Phase fault on ARNEGARD-MK7115.00 (655841) 115 kV Bus a. Apply fault at the ARNEGARD-MK7115.00 (655841) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNEGARD-MK7 (655841) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_203 | 3 Phase fault on HAYBUTTE-MK7115.00 (655842) 115 kV Bus a. Apply fault at the HAYBUTTE-MK7115.00 (655842) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYBUTTE-MK7 (655842) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_204 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_205 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to ALEXANDR-MK7 (655892) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_206 | 3 Phase fault on TIMBERCK-MK7115.00 (655844) 115 kV Bus a. Apply fault at the TIMBERCK-MK7115.00 (655844) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBERCK-MK7 (655844) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_207 | 3 Phase fault on F9______-MK7115.00 (655846) 115 kV Bus a. Apply fault at the F9______-MK7115.00 (655846) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. F9______-MK7 (655846) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_208 | 3 Phase fault on BERG -MK7115.00 (655848) 115 kV Bus a. Apply fault at the BERG -MK7115.00 (655848) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG -MK7 (655848) 115.0 kV to BBCOMPTP-MK7 (655873) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_209 | 3 Phase fault on VEEDER -MK7115.00 (655849) 115 kV Bus a. Apply fault at the VEEDER -MK7115.00 (655849) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VEEDER -MK7 (655849) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_210 | 3 Phase fault on BEARCREK-MK7115.00 (655853) 115 kV Bus a. Apply fault at the BEARCREK-MK7115.00 (655853) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEARCREK-MK7 (655853) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_211 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_212 | 3 Phase fault on STNJOHNY-MK7115.00 (655856) 115 kV Bus a. Apply fault at the STNJOHNY-MK7115.00 (655856) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNJOHNY-MK7 (655856) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_213 | 3 Phase fault on HORSECRK-MK7115.00 (655861) 115 kV Bus a. Apply fault at the HORSECRK-MK7115.00 (655861) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HORSECRK-MK7 (655861) 115.0 kV to CARTWRIT-MK7 (655863) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_214 | 3 Phase fault on G9______-MK7115.00 (655871) 115 kV Bus a. Apply fault at the G9______-MK7115.00 (655871) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G9______-MK7 (655871) 115.0 kV to G9TAP___-MK7 (655872) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_215 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to BBCMPRSS-MK7 (655874) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_216 | 3 Phase fault on BBCOMPTP-MK7115.00 (655873) 115 kV Bus a. Apply fault at the BBCOMPTP-MK7115.00 (655873) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BBCOMPTP-MK7 (655873) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_217 | 3 Phase fault on SCHAFR_T-MK7115.00 (655880) 115 kV Bus a. Apply fault at the SCHAFR_T-MK7115.00 (655880) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCHAFR_T-MK7 (655880) 115.0 kV to FNCYBTAP-MK7 (655899) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_218 | 3 Phase fault on DAP_____-MK7115.00 (655881) 115 kV Bus a. Apply fault at the DAP_____-MK7115.00 (655881) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAP_____-MK7 (655881) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_219 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to GALAXY -MK7 (655883) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_220 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to DEMCKSLK-MK7 (655884) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_221 | 3 Phase fault on GALAXYTP-MK7115.00 (655882) 115 kV Bus a. Apply fault at the GALAXYTP-MK7115.00 (655882) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GALAXYTP-MK7 (655882) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_222 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_223 | 3 Phase fault on DUNNCNTR-MK7115.00 (655893) 115 kV Bus a. Apply fault at the DUNNCNTR-MK7115.00 (655893) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNNCNTR-MK7 (655893) 115.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_224 | 3 Phase fault on FNCYBTAP-MK7115.00 (655899) 115 kV Bus a. Apply fault at the FNCYBTAP-MK7115.00 (655899) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNCYBTAP-MK7 (655899) 115.0 kV to KUMMERDG-MK7 (659388) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_225 | 3 Phase fault on RBNSNLAK-MW7115.00 (655905) 115 kV Bus a. Apply fault at the RBNSNLAK-MW7115.00 (655905) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_226 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_227 | 3 Phase fault on FINSTAD -MW7115.00 (655906) 115 kV Bus a. Apply fault at the FINSTAD -MW7115.00 (655906) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_228 | 3 Phase fault on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_229 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_230 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_232 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_233 | 3 Phase fault on JUDSON -MW7115.00 (655925) 115 kV Bus a. Apply fault at the JUDSON -MW7115.00 (655925) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUDSON -MW7 (655925) 115.0 kV to SW.WLSTN-MW7 (655926) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_234 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_235 | 3 Phase fault on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_236 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_237 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_238 | 3 Phase fault on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_239 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_240 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_241 | 3 Phase fault on NE.WLSTN-MW7115.00 (655937) 115 kV Bus a. Apply fault at the NE.WLSTN-MW7115.00 (655937) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE.WLSTN-MW7 (655937) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_242 | 3 Phase fault on MONT -MW7115.00 (655940) 115 kV Bus a. Apply fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_243 | 3 Phase fault on TYRONE -MW7115.00 (655956) 115 kV Bus a. Apply fault at the TYRONE -MW7115.00 (655956) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_244 | 3 Phase fault on EASTFORK-MW7115.00 (655957) 115 kV Bus a. Apply fault at the EASTFORK-MW7115.00 (655957) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_245 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_246 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_247 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_248 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_249 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_250 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_251 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_252 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_253 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_254 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_255 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_256 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_257 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_258 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_259 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_260 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_261 | 3 Phase fault on CULBRTSN-UM7115.00 (659112) 115 kV Bus a. Apply fault at the CULBRTSN-UM7115.00 (659112) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_262 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_263 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_264 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_265 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_266 | 3 Phase fault on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_267 | 3 Phase fault on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT4-5-BE7 (659154) 115.0 kV to LC_SWY.S-BE7 (659346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_268 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_269 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_270 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_271 | 3 Phase fault on KOCH_OIL-BE7115.00 (659180) 115 kV Bus a. Apply fault at the KOCH_OIL-BE7115.00 (659180) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_272 | 3 Phase fault on BICNTNIL-BE7115.00 (659181) 115 kV Bus a. Apply fault at the BICNTNIL-BE7115.00 (659181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_273 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_274 | 3 Phase fault on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_275 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_276 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_277 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_278 | 3 Phase fault on HEADRESS-CM7115.00 (659259) 115 kV Bus a. Apply fault at the HEADRESS-CM7115.00 (659259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_279 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_280 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_281 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_282 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_283 | 3 Phase fault on LC_CT1-3-BE7115.00 (659348) 115 kV Bus a. Apply fault at the LC_CT1-3-BE7115.00 (659348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_CT1-3-BE7 (659348) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_284 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_285 | 3 Phase fault on LC_SWY.N-BE7115.00 (659349) 115 kV Bus a. Apply fault at the LC_SWY.N-BE7115.00 (659349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_SWY.N-BE7 (659349) 115.0 kV to PATENTGT-MK7 (659391) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_286 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_287 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_288 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_289 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_290 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_291 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_292 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_293 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_294 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_295 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_296 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_297 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_298 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_299 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_300 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_301 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_302 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_303 | 3 Phase fault on BELFELD3 345.00 (652424) 345 kV Bus a. Apply fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_304 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_305 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_306 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_307 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_308 | 3 Phase fault on MAURINE 2 345.00 (800121) 345 kV Bus a. Apply fault at the MAURINE 2 345.00 (800121) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_309 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_310 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_311 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_312 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_313 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_314 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_315 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_316 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_317 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_318 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_319 | 3 Phase fault on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_320 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_321 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_322 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_323 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_324 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_325 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_326 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_327 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_328 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_329 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_330 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_331 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_332 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_333 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_334 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_335 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_336 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_337 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_338 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_339 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_340 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_341 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_342 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_343 | 3 Phase fault on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EFORK_-BE334 (659600) 345.0 kV to EASTFORK-MW7 (655957) 115.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_344 | 3 Phase fault on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 7 (652401) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_345 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_346 | 3 Phase fault on DAWSONC7 115.00 (652404) 115 kV Bus a. Apply fault at the DAWSONC7 115.00 (652404) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC7 (652404) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_347 | 3 Phase fault on WATFORD7 115.00 (652408) 115 kV Bus a. Apply fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD7 (652408) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_348 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_349 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_350 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_351 | 3 Phase fault on LC_GAS_P-MK7115.00 (655889) 115 kV Bus a. Apply fault at the LC_GAS_P-MK7115.00 (655889) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LC_GAS_P-MK7 (655889) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_352 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINSTAD345 (659060) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_353 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_354 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_355 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_356 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_357 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_358 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_359 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_360 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_361 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_LOCAL_FAULT_362 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_001 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_002 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_003 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_004 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_005 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_006 | 3 Phase fault on BISON 3 345.00 (601067) 345 kV Bus a. Apply fault at the BISON 3 345.00 (601067) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_007 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_008 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_009 | 3 Phase fault on HANKSON4 230.00 (620327) 230 kV Bus a. Apply fault at the HANKSON4 230.00 (620327) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_010 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_011 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_012 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_013 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_014 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_015 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_016 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_017 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_018 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR1TE (657949) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_019 | 3 Phase fault on PRAIRIE3 345.00 (657946) 345 kV Bus a. Apply fault at the PRAIRIE3 345.00 (657946) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PRAIRIE3 (657946) 345.0 kV to PRAIRIE4 (657755) 230.0 kV to PRAIR2TE (657950) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_020 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_021 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_022 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_023 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_024 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_025 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_026 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BISON 3 (601067) 345.0 kV to BUFFALO3 (620358) 345.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 b.5. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_027 | 3 Phase fault on OAKES 4 230.00 (620362) 230 kV Bus a. Apply fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.4. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.5. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.8. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.9. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_028 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_029 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to G82RPHT1 (667085) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_030 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 b.4. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_031 | 3 Phase fault on GRANITF4 230.00 (652550) 230 kV Bus a. Apply fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_032 | 3 Phase fault on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.2. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_033 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_034 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_035 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_036 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_037 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_038 | 3 Phase fault on BIGSTON4 230.00 (620314) 230 kV Bus a. Apply fault at the BIGSTON4 230.00 (620314) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_039 | 3 Phase fault on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAIR-ER4 (655465) 230.0 kV to BLAIR-ER8 (655466) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_040 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_041 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_042 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_043 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_044 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_045 | 3 Phase fault on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_046 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_047 | 3 Phase fault on PEACE GARD 5230.00 (602057) 230 kV Bus a. Apply fault at the PEACE GARD 5230.00 (602057) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEACE GARD 5 (602057) 230.0 kV to RUGBY 4 (620379) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_048 | 3 Phase fault on TWIN BRKS 3 345.00 (620416) 345 kV Bus a. Apply fault at the TWIN BRKS 3 345.00 (620416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TWIN BRKS 3 (620416) 345.0 kV to BSSOUTH3 (620417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_049 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to DEUEL CO 3 (620480) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_050 | 3 Phase fault on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BSSOUTH3 (620417) 345.0 kV to ASTORIA 3 (620483) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_051 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_052 | 3 Phase fault on RAUN 3 (635200) 345.0 kV Bus a. Apply fault at the RAUN 3 (635200) 345.0 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_053 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_054 | 3 Phase fault on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_055 | 3 Phase fault on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_056 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_057 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_058 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_059 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_060 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_061 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_062 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_063 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_064 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to DEERCREK-BE3 (659286) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_065 | 3 Phase fault on MPC4300 POI 345.00 (657110) 345 kV Bus a. Apply fault at the MPC4300 POI 345.00 (657110) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC4300 POI (657110) 345.0 kV to PRAIRIE3 (657946) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_066 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_067 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_068 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_069 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_070 | 3 Phase fault on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO 9X (620858) 41.6 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_071 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_072 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_073 | 3 Phase fault on UNDERWOOD 2 345.00 (800120) 345 kV Bus a. Apply fault at the UNDERWOOD 2 345.00 (800120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. UNDERWOOD 2 (800120) 345.0 kV to NUNDRWD4 (652484) 230.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_074 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_075 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_076 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_077 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_078 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_079 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_080 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_081 | 3 Phase fault on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MI CTYE4 (652411) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P1_REGIONAL_FAULT_082 | 3 Phase fault on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUNDRWD4 (652484) 230.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SNAKECR7 115.00 (652590) 115 kV Bus a. Apply Fault at the SNAKECR7 115.00 (652590) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to SNAKECR7 (652590) 115.0 kV Transmission Circuit #1 b.2. SNAKECR7 (652590) 115.0 kV to DOUGLS.C-CP7 (655661) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on NELSON 7 115.00 (652440) 115 kV Bus a. Apply Fault at the NELSON 7 115.00 (652440) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.11. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.6. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to MAURINE 2 (800121) 345.0 kV Transmission Circuit #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.5. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on S.HEART_-RR4230.00 (659309) 230 kV Bus a. Apply Fault at the S.HEART_-RR4230.00 (659309) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.3. S.HEART_-RR4 (659309) 230.0 kV to S.HEART_-RR7 (659306) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND_2 (659429) 345.0 kV Transmission Circuit #1 b.5. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BALDWIN_-PP4230.00 (659365) 230 kV Bus a. Apply Fault at the BALDWIN_-PP4230.00 (659365) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.2. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.3. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.4. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.5. BALDWIN_-PP4 (659365) 230.0 kV to BALDWIN_-PP9 (659367) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on CABINCR7 115.00 (661033) 115 kV Bus a. Apply Fault at the CABINCR7 115.00 (661033) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. CABINCR7 (661033) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 b.3. BAKER 7 (661005) 115.0 kV to KEYXLPS14 7 (661034) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.4. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.5. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.6. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.4. BEULAH 7 (661008) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #z b.5. BEULAH 7 (661008) 115.0 kV to COYOTE 7 (661018) 115.0 kV Transmission Circuit #1 b.6. BEULAH 7 (661008) 115.0 kV to COYOTETAP 7 (661057) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on GLENDCT7 115.00 (661032) 115 kV Bus a. Apply Fault at the GLENDCT7 115.00 (661032) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDCT7 (661032) 115.0 kV to CABINCR7 (661033) 115.0 kV Transmission Circuit #1 b.2. GLENDCT7 (661032) 115.0 kV to GLNDCT2G (661101) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on POPLAR 7 115.00 (661075) 115 kV Bus a. Apply Fault at the POPLAR 7 115.00 (661075) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CULBRTSN-UM7 (659112) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 b.2. HEADRESS-CM7 (659259) 115.0 kV to POPLAR 7 (661075) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY4 (615347) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. HARVEY 4 (620290) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.6. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.7. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on DICKINSN-BE4230.00 (659124) 230 kV Bus a. Apply Fault at the DICKINSN-BE4230.00 (659124) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. HEBRON 4 (652468) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.3. DICKINSN-BE4 (659124) 230.0 kV to DICKINSN-BE7 (659125) 115.0 kV to DK.KW1A_-BE9 (659197) 13.8 kV Three Winding #1 b.4. DICKINSN-BE4 (659124) 230.0 kV to DICKINS2-BE7 (659195) 115.0 kV to DK.KW1A_-BE9 (659196) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on NWMDNTAP-MG7115.00 (655752) 115 kV Bus a. Apply Fault at the NWMDNTAP-MG7115.00 (655752) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NWMDNTAP-MG7 (655752) 115.0 kV to BASIN___-BE7 (659109) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to BASIN___-BE4 (659199) 230.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 b.4. DEVAUL -MG7 (655747) 115.0 kV to NEWSALEM-MG7 (655748) 115.0 kV Transmission Circuit #1 b.5. NEWSALEM-MG7 (655748) 115.0 kV to NWMDNTAP-MG7 (655752) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on CIRCLE 7 115.00 (652401) 115 kV Bus a. Apply Fault at the CIRCLE 7 115.00 (652401) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to REDWATER-MC7 (659542) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVE7 (652200) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.2. GLENDIVEP2T7 (652212) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 7 (652401) 115.0 kV to DAWSONC7 (652404) 115.0 kV Transmission Circuit #1 b.4. DAWSONC7 (652404) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. DAWSONC7 (652404) 115.0 kV to DAWSONC4 (652403) 230.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY9 (652322) 41.6 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.5. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTPECK 4 230.00 (652405) 230 kV Bus a. Apply Fault at the FTPECK 4 230.00 (652405) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on ECKLUND1-PP934.500 (659322) 34.5 kV Bus a. Apply Fault at the ECKLUND1-PP934.500 (659322) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 b.7. ECKLUND1-PP9 (659322) 34.5 kV to WILTON_1-PPW (659294) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.2. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on RICHLAND-BE7115.00 (659151) 115 kV Bus a. Apply Fault at the RICHLAND-BE7115.00 (659151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.2. HELMUT -LY7 (655790) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.3. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.4. RICHLAND-BE7 (659151) 115.0 kV to LEWIS 7 (661056) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 b.5. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on WOLFPT 7 115.00 (652409) 115 kV Bus a. Apply Fault at the WOLFPT 7 115.00 (652409) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 7 (652401) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #1 b.3. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 b.4. WOLFPT 7 (652409) 115.0 kV to HEADRESS-CM7 (659259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.4. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on SULLYBT-ER4 230.00 (655487) 230 kV Bus a. Apply Fault at the SULLYBT-ER4 230.00 (655487) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.2. SULLYBT-ER4 (655487) 230.0 kV to SB.LS-WK-ER4 (655510) 230.0 kV Transmission Circuit #z b.3. SULLYBT-ER4 (655487) 230.0 kV to SULLYBT-ER8 (655488) 69.0 kV Two Winding #1 b.4. OKOBOJO-ER8 (655334) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.5. MOS-SLY2-ER8 (655373) 69.0 kV to SULLYBT-ER8 (655488) 69.0 kV Transmission Circuit #1 b.6. SB.LS-WK-ER4 (655510) 230.0 kV to WHITLOCK_-RM (655765) 230.0 kV Transmission Circuit #1 b.7. WHITLOCK_-RM (655765) 230.0 kV to GLENHAM4 (661038) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on MEDORA__-UM4230.00 (659247) 230 kV Bus a. Apply Fault at the MEDORA__-UM4230.00 (659247) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.5. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to S.HEART_-RR4 (659309) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DAGLUM__-BE4 (659448) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD29 (652220) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.7. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.8. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 b.5. FAIRVIEW 7 (652651) 115.0 kV to GEN-2020-083 (765070) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.3. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.7. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on KILDEER7 115.00 (652419) 115 kV Bus a. Apply Fault at the KILDEER7 115.00 (652419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to KILLDEER-MK7 (655891) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on HALLIDAY-UM7115.00 (659248) 115 kV Bus a. Apply Fault at the HALLIDAY-UM7115.00 (659248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KILDEER7 (652419) 115.0 kV to NBCS_05_-PPR (659129) 13.8 kV Two Winding #1 b.2. KILDEER7 (652419) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.3. HALLIDAY-MK7 (655894) 115.0 kV to HALLIDAY-UM7 (659248) 115.0 kV Transmission Circuit #1 b.4. HALLIDAY-UM7 (659248) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.5. LETCHER7 (652609) 115.0 kV to ROSWELL-ER7 (655417) 115.0 kV Transmission Circuit #1 b.6. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on FALLON 7 115.00 (652407) 115 kV Bus a. Apply Fault at the FALLON 7 115.00 (652407) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLENDIVEP2T7 (652212) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.2. TERRY TAP (652394) 115.0 kV to FALLON 7 (652407) 115.0 kV Transmission Circuit #1 b.3. FALLON 7 (652407) 115.0 kV to FALLON 8 (652213) 69.0 kV to FALLON 9 (652214) 12.5 kV Three Winding #1 b.6. TERRY TAP (652394) 115.0 kV to SHIRLEY TAP (652395) 115.0 kV Transmission Circuit #1 b.7. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on WATFORD7 115.00 (652408) 115 kV Bus a. Apply Fault at the WATFORD7 115.00 (652408) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.3. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 b.4. WATFORD7 (652408) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.6. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.5. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.7. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.8. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 b.9. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.KU2A_-BE9 (659204) 13.8 kV to BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV Three Winding #1 b.2. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.3. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 b.3. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 b.4. CCR.KV3A-BE9 (659318) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #1 b.5. CCR.KV4A-BE9 (659319) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.3. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.5. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply Fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. STATELIN-MW7 (655924) 115.0 kV to PIONEER2-BE7 (659430) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on PIONEER1-BE7115.00 (659347) 115 kV Bus a. Apply Fault at the PIONEER1-BE7115.00 (659347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to PIONEER1-BE7 (659347) 115.0 kV Transmission Circuit #z b.2. PIONER_1-BEG (659147) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.3. PIONER_2-BEG (659158) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 b.4. PIONEE_3-BEG (659159) 13.8 kV to PIONEER1-BE7 (659347) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STATELIN-MW7 (655924) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes following active power oscillations at the GEN-2018-067 generator site (763024 and 763027). This issue is also observed in the base case and is not impacted by the CQ units. | Black Tail to Strandahl 115 kV Line
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on STRNDAHL-MW7115.00 (655941) 115 kV Bus a. Apply Fault at the STRNDAHL-MW7115.00 (655941) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.3. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. STRNDAHL-MW7 (655941) 115.0 kV to GEN-2018-067 (763021) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on BARRBUTE-MW7115.00 (655915) 115 kV Bus a. Apply Fault at the BARRBUTE-MW7115.00 (655915) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRBUTE-MW7 (655915) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. BARRBUTE-MW7 (655915) 115.0 kV to GRENORA_-UM7 (659145) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. CHRRYCRK-MK7 (655840) 115.0 kV to ARNEGARD-MK7 (655841) 115.0 kV Transmission Circuit #1 b.3. CHRRYCRK-MK7 (655840) 115.0 kV to DPLWCTAP-MK7 (655876) 115.0 kV Transmission Circuit #1 b.4. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.5. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on PEMBROOK-ER869.000 (655339) 69 kV Bus a. Apply Fault at the PEMBROOK-ER869.000 (655339) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 b.4. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.5. ABERDN SIEB7 (660001) 115.0 kV to ABR PEAKER (660062) 13.8 kV Two Winding #1 b.6. ABERDN SIEB7 (660001) 115.0 kV to ABR SIEBRCHT (660421) 34.5 kV Two Winding #1 b.7. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.8. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.9. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 b.10. PEMBROOK-ER8 (655339) 69.0 kV to NBCS_09_-PPR (659277) 12.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on VOLTAIR -CP7115.00 (655643) 115 kV Bus a. Apply Fault at the VOLTAIR -CP7115.00 (655643) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-MCHENRY7 (615348) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.3. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 b.4. VOLTAIR -CP7 (655643) 115.0 kV to NEAL____-CP9 (655602) 41.6 kV Two Winding #1 b.5. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on TOWNER 7 115.00 (652453) 115 kV Bus a. Apply Fault at the TOWNER 7 115.00 (652453) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RUGBY 7 (652452) 115.0 kV to TOWNER 7 (652453) 115.0 kV Transmission Circuit #1 b.2. TOWNER 7 (652453) 115.0 kV to DENBIGH TAP7 (652464) 115.0 kV Transmission Circuit #1 b.3. TOWNER 7 (652453) 115.0 kV to BOTNU.SE-CP7 (655651) 115.0 kV Transmission Circuit #1 b.4. DENBIGH TAP7 (652464) 115.0 kV to VOLTAIR -CP7 (655643) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on VANHOOK -MW7115.00 (655920) 115 kV Bus a. Apply Fault at the VANHOOK -MW7115.00 (655920) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.NEWTWN-MW7 (655907) 115.0 kV to BIGBEND -MW7 (655960) 115.0 kV Transmission Circuit #1 b.2. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.3. E.NEWTWN-MW7 (655907) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.4. PARSHALL-MW7 (655908) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE7115.00 (659182) 115 kV Bus a. Apply Fault at the CHARL_CK-BE7115.00 (659182) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. KILDEER7 (652419) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.3. GRSYBTTP-MK7 (655833) 115.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Transmission Circuit #1 b.4. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.5. CHARL_CK-BE7 (659182) 115.0 kV to FOUREYES-RR7 (659185) 115.0 kV Transmission Circuit #1 b.6. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.7. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.8. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CCR.KV2A-BE9 (659211) 13.8 kV to CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV Three Winding #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on SQUAWGAP-BE7115.00 (659191) 115 kV Bus a. Apply Fault at the SQUAWGAP-BE7115.00 (659191) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BICNTNIL-BE7 (659181) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 b.3. BICNTNIL-BE7 (659181) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.4. SKAAR___-MK7 (655860) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.5. KOCH_OIL-BE7 (659180) 115.0 kV to SQUAWGAP-BE7 (659191) 115.0 kV Transmission Circuit #1 b.6. KOCH_OIL-BE7 (659180) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 b.7. RICHLAND-BE7 (659151) 115.0 kV to E.SIDNEY-LY7 (659186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on BELFELD4 230.00 (652425) 230 kV Bus a. Apply Fault at the BELFELD4 230.00 (652425) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD4 (652425) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 b.3. MINGUSVILLE4 (652616) 230.0 kV to MEDORA__-UM4 (659247) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD4 (652425) 230.0 kV to DICKINSN-BE4 (659124) 230.0 kV Transmission Circuit #1 b.2. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on ND.PW1__-BE934.500 (659325) 34.5 kV Bus a. Apply Fault at the ND.PW1__-BE934.500 (659325) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELSON 7 (652440) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.2. GARRISN7 (652442) 115.0 kV to MAX_____-CP7 (655690) 115.0 kV Transmission Circuit #1 b.3. MAX_____-CP9 (655691) 41.6 kV to MAX_____-CP7 (655690) 115.0 kV Two Winding #1 b.4. MALLARD7 (603023) 115.0 kV to NELSON 7 (652440) 115.0 kV Transmission Circuit #1 b.5. NELSON 7 (652440) 115.0 kV to ND.PW1__-BE7 (659190) 115.0 kV Transmission Circuit #z b.6. ND.PW1__-BE7 (659190) 115.0 kV to ND.PW1__-BE9 (659325) 34.5 kV Two Winding #1 b.7. ND.PW1__-BE9 (659325) 34.5 kV to ND.PW1__-BEW (659194) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on LC_CT4-5-BE7115.00 (659154) 115 kV Bus a. Apply Fault at the LC_CT4-5-BE7115.00 (659154) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.8. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_4-BEG (659162) 13.8 kV Two Winding #1 b.9. LC_CT4-5-BE7 (659154) 115.0 kV to LONESM_5-BEG (659163) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JDS.KU6A-BE9 (659335) 13.8 kV to JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV Three Winding #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BIGBND14 230.00 (652540) 230 kV Bus a. Apply Fault at the BIGBND14 230.00 (652540) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. BIGBND14 (652540) 230.0 kV to BGBND12G (652542) 13.8 kV Two Winding #1 b.3. BIGBND14 (652540) 230.0 kV to BGBND34G (652543) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on BIGBND24 230.00 (652541) 230 kV Bus a. Apply Fault at the BIGBND24 230.00 (652541) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. BIGBND24 (652541) 230.0 kV to BGBND56G (652544) 13.8 kV Two Winding #1 b.3. BIGBND24 (652541) 230.0 kV to BGBND78G (652545) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.2. FTPECK 4 (652405) 230.0 kV to FTPECK 7 (652406) 115.0 kV Two Winding #1 b.3. FTPECK 4 (652405) 230.0 kV to FTPECK4G (652414) 13.8 kV Two Winding #1 b.4. FTPECK 4 (652405) 230.0 kV to FTPECK5G (652415) 13.8 kV Two Winding #1 b.5. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on FTPECK 7 115.00 (652406) 115 kV Bus a. Apply Fault at the FTPECK 7 115.00 (652406) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTPECK 7 (652406) 115.0 kV to FTPECK3G (652410) 13.8 kV Two Winding #1 b.2. FTPECK 7 (652406) 115.0 kV to WOLFPT 7 (652409) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on CROCKER_-BE3345.00 (659165) 345 kV Bus a. Apply Fault at the CROCKER_-BE3345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. CROCKER_-BE3 (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to G20-021-TAP (764220) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on BLKTLTAP-MW7115.00 (655931) 115 kV Bus a. Apply Fault at the BLKTLTAP-MW7115.00 (655931) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLKTLTAP-MW7 (655931) 115.0 kV to TYRONE -MW7 (655956) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. BLKTLTAP-MW7 (655931) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.4. BLKTLTAP-MW7 (655931) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on EFORK_-BE334345.00 (659600) 345 kV Bus a. Apply Fault at the EFORK_-BE334345.00 (659600) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.2. TYRONE -MW7 (655956) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.3. EASTFORK-MW7 (655957) 115.0 kV to FOLVAG -MW7 (655958) 115.0 kV Transmission Circuit #1 b.4. EASTFORK-MW7 (655957) 115.0 kV to EFORK_-BE334 (659600) 345.0 kV to EASTFORKTERT (659601) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.3. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TRADEWND-UA3 (659479) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to BURKE___-PP3 (659404) 345.0 kV Transmission Circuit #1 b.2. TND.KU3A-BE9 (659338) 13.8 kV to TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on WAYSIDE4 230.00 (640404) 230 kV Bus a. Apply Fault at the WAYSIDE4 230.00 (640404) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAYSIDE4 (640404) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #1 b.2. STEGALL4 (652573) 230.0 kV to STEGALL-LNX3 (652873) 230.0 kV Transmission Circuit #z b.3. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.4. WAYSIDE7 (640405) 115.0 kV to WAYSIDE4 (640404) 230.0 kV to WAYSIDE9 (640406) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply Fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.5. TIOGA4 7 (661085) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on STANLEY7 115.00 (661080) 115 kV Bus a. Apply Fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.4. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.5. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ANSON 7 115.00 (603200) 115 kV Bus a. Apply Fault at the ANSON 7 115.00 (603200) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.5. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. BRKNGCO3 (601031) 345.0 kV to BRKNGCO7 (603192) 115.0 kV to BRCKNGS9 8 (605667) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on BUFFALO3 345.00 (620358) 345 kV Bus a. Apply Fault at the BUFFALO3 345.00 (620358) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CSLTNET7 (620180) 115.0 kV to BUFFALO7 (620258) 115.0 kV Transmission Circuit #1 b.2. BUFFALO3 (620358) 345.0 kV to BUFFALO7 (620258) 115.0 kV to BUFFALO9 (620158) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on COURT FDR2 934.500 (606098) 34.5 kV Bus a. Apply Fault at the COURT FDR2 934.500 (606098) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO3 (620358) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 b.3. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #1 b.4. JAMESTN3 (620369) 345.0 kV to JAMSTWN7 (620269) 115.0 kV to JAMSTN 9 (620169) 41.6 kV Three Winding #2 b.7. COURTENAY W7 (603286) 115.0 kV to JAMSTWN7 (620269) 115.0 kV Transmission Circuit #1 b.8. JAMSTWN7 (620269) 115.0 kV to SPIRITWD 7 (620270) 115.0 kV Transmission Circuit #1 b.9. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.12. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.13. SPIRITWD 7 (620270) 115.0 kV to GRE-SPRITWDG (615015) 13.8 kV Two Winding #1 b.14. SPIRITWD 7 (620270) 115.0 kV to SPIRITWOOD 9 (620171) 41.6 kV Two Winding #1 b.15. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 b.16. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.17. JAMESPK7 (620272) 115.0 kV to JAMESPK9 (620172) 41.6 kV Two Winding #1 b.18. EDGE SS9 (620159) 41.6 kV to JAMESPK9 (620172) 41.6 kV Transmission Circuit #1 b.19. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.20. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.21. COURT B1 9 (606095) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.22. COURT B2 9 (606096) 34.5 kV to COURTENAY W7 (603286) 115.0 kV Two Winding #1 b.23. COURT B1 9 (606095) 34.5 kV to COURT FDR1 9 (606097) 34.5 kV Transmission Circuit #1 b.24. J262 COURT W (600162) 0.6 kV to COURT FDR1 9 (606097) 34.5 kV Two Winding #1 b.25. COURT B2 9 (606096) 34.5 kV to COURT FDR2 9 (606098) 34.5 kV Transmission Circuit #1 b.26. J263 COURT W (600163) 0.6 kV to COURT FDR2 9 (606098) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on BSSOUTH3 345.00 (620417) 345 kV Bus a. Apply Fault at the BSSOUTH3 345.00 (620417) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS2 34.5 (620321) 34.5 kV Three Winding #2 b.4. BSSOUTH3 (620417) 345.0 kV to BSSOUTH4 (620322) 230.0 kV to BSS1 34.5 (620320) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITTL_MS-BE4 (659265) 230.0 kV to LITTL_MS-BE7 (659263) 115.0 kV Two Winding #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to RHAME___-BE4 (659266) 230.0 kV Transmission Circuit #1 b.3. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.4. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.5. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on BAKER 4 230.00 (661004) 230 kV Bus a. Apply Fault at the BAKER 4 230.00 (661004) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. LITTL_MS-BE4 (659265) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.3. BAKER 4 (661004) 230.0 kV to BAKER 7 (661005) 115.0 kV to BAKER 9 (661901) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on OAKES 4 230.00 (620362) 230 kV Bus a. Apply Fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.2. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 b.7. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.6. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.5. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to DAWSONC4 (652403) 230.0 kV Transmission Circuit #1 b.2. DAWSONC4 (652403) 230.0 kV to FTPECK 4 (652405) 230.0 kV Transmission Circuit #1 b.3. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.4. DAWSONC4 (652403) 230.0 kV to MINGUSVILLE4 (652616) 230.0 kV Transmission Circuit #1 b.5. DAWSONC4 (652403) 230.0 kV to DAWSONC7 (652404) 115.0 kV to DAWSONC9 (652211) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on DAWSONC4 230.00 (652403) 230 kV Bus a. Apply Fault at the DAWSONC4 230.00 (652403) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.2. WAYSIDE4 (640404) 230.0 kV to NUNDRWD4 (652484) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD10 (652266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.7. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. BIGSTON4 (620314) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.7. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on BISON___-GE4230.00 (659351) 230 kV Bus a. Apply Fault at the BISON___-GE4230.00 (659351) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.4. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.5. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.6. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on MAURINE4 230.00 (652497) 230 kV Bus a. Apply Fault at the MAURINE4 230.00 (652497) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.2. MAURINE4 (652497) 230.0 kV to BISON___-GE4 (659351) 230.0 kV Transmission Circuit #1 b.3. MAURINE 2 (800121) 345.0 kV to MAURINE4 (652497) 230.0 kV Two Winding #1 b.4. MAURINE4 (652497) 230.0 kV to MAURINE7 (652480) 115.0 kV to MAURINE9 (652247) 13.8 kV Three Winding #1 b.6. BISON___-GE4 (659351) 230.0 kV to HETINGR4 (661047) 230.0 kV Transmission Circuit #1 b.7. BISON___-GE7 (659350) 115.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.8. BISON___-GE8 (659352) 69.0 kV to BISON___-GE4 (659351) 230.0 kV Two Winding #1 b.9. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. DAWSONC4 (652403) 230.0 kV to MI CTYE4 (652411) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on MT WEST4 230.00 (652450) 230 kV Bus a. Apply Fault at the MT WEST4 230.00 (652450) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYW4 (652402) 230.0 kV to MT WEST4 (652450) 230.0 kV Transmission Circuit #x1 b.2. MI CTYW4 (652402) 230.0 kV to MILES_DC-BED (659249) 230.0 kV Transmission Circuit #x1 b.3. MT WEST4 (652450) 230.0 kV to NB WEST4 (652585) 230.0 kV Transmission Circuit #x1 b.4. MT WEST4 (652450) 230.0 kV to RAPID_DC-BED (659304) 230.0 kV Transmission Circuit #x1 b.5. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on MI CTYE4 230.00 (652411) 230 kV Bus a. Apply Fault at the MI CTYE4 230.00 (652411) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to BAKER 4 (661004) 230.0 kV Transmission Circuit #1 b.2. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on MI CTYE7 115.00 (652412) 115 kV Bus a. Apply Fault at the MI CTYE7 115.00 (652412) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MI CTYE4 (652411) 230.0 kV to MI CTYE7 (652412) 115.0 kV to MI CTYE9 (652217) 13.8 kV Three Winding #1 b.4. SHIRLEY TAP (652395) 115.0 kV to MI CTYE7 (652412) 115.0 kV Transmission Circuit #1 b.5. MI CTYE8 (652219) 60.0 kV to MILESCITYTG (661099) 60.0 kV Transmission Circuit #1 b.6. MI CTYE8 (652219) 60.0 kV to MI CTYE7 (652412) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 b.2. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 b.3. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to CROCKER_-BE3 (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.2. MNVLTAP4 (602009) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.3. GRE-WILLMAR4 (619975) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.5. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.6. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF9 (652297) 13.8 kV Three Winding #1 b.8. GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV to GRANITF29 (652292) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. NORTHBEND4 (652516) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.9. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.10. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.11. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.4. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.7. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.8. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.9. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.10. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.9. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.10. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF29 (652292) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. GRANITF4 (652550) 230.0 kV to MORRIS 4 (652554) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on GRANITF4 230.00 (652550) 230 kV Bus a. Apply Fault at the GRANITF4 230.00 (652550) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF9 (652297) 13.8 kV to GRANITF4 (652550) 230.0 kV to GRANITF7 (652551) 115.0 kV Three Winding #1 b.2. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.3. MINVALT4 (602008) 230.0 kV to GRANITF4 (652550) 230.0 kV Transmission Circuit #1 b.4. GRANITF4 (652550) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply Fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on RUSHMORE-RM7115.00 (655763) 115 kV Bus a. Apply Fault at the RUSHMORE-RM7115.00 (655763) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. NUNDRWD7 (652485) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.5. RAPIDCY7 (652490) 115.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Transmission Circuit #1 b.6. RUSHMORE-RM8 (655764) 69.0 kV to RUSHMORE-RM7 (655763) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on NUNDRWD7 115.00 (652485) 115 kV Bus a. Apply Fault at the NUNDRWD7 115.00 (652485) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.4. ELSWRTH7 (652477) 115.0 kV to NUNDRWD7 (652485) 115.0 kV Transmission Circuit #1 b.5. NUNDRWD7 (652485) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.6. WALL 7 (652492) 115.0 kV to WICKSVL7 (652493) 115.0 kV Transmission Circuit #1 b.7. PHILIP 7 (652487) 115.0 kV to WALL 7 (652492) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on DRYCREEK-BE4230.00 (659376) 230 kV Bus a. Apply Fault at the DRYCREEK-BE4230.00 (659376) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RCDC.DUM-BE4 (659268) 230.0 kV to RCDC.E__-BE4 (659271) 230.0 kV Transmission Circuit #1 b.2. RCDC.E__-BE4 (659271) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #z b.3. NUNDRWD4 (652484) 230.0 kV to DRYCREEK-BE4 (659376) 230.0 kV Transmission Circuit #1 b.4. DRYCREEK-BE4 (659376) 230.0 kV to DRYCREEK-BE7 (659377) 115.0 kV to DC.KV11A-BE9 (659378) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.3. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-048 (588870) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.3. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 b.4. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.5. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 NORTH | DISIS-2020-001 CF | 25W | Transfer | GROUP1_P4_REGIONAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on 4&MORTON 7 115.00 (650205) 115 kV Bus a. Apply fault at the 4&MORTON 7 115.00 (650205) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to 19&ALVO 7 (650215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on 27FLETCHER7 115.00 (650228) 115 kV Bus a. Apply fault at the 27FLETCHER7 115.00 (650228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and G19-041-GEN1 (763728). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and G19-041-GEN1 (763728). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and G19-041-GEN1 (763728). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and G19-041-GEN1 (763728). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and G19-041-GEN1 (763728). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLECREEK 7 (640465) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.2. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.3. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 b.4. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1299 5 (646299) 161.0 kV Load #O0 b.4. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037-TAP (762712) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on S928 8 69.000 (647928) 69 kV Bus a. Apply fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on FREM F 8 69.000 (647426) 69 kV Bus a. Apply fault at the FREM F 8 69.000 (647426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM F 8 (647426) 69.0 kV to S992 8 (647992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on FREM C 8 69.000 (647423) 69 kV Bus a. Apply fault at the FREM C 8 69.000 (647423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM C 8 (647423) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on FREM E 8 69.000 (647425) 69 kV Bus a. Apply fault at the FREM E 8 69.000 (647425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM E 8 (647425) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on S942 8 69.000 (647942) 69 kV Bus a. Apply fault at the S942 8 69.000 (647942) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S942 8 (647942) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV remove bus # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on RENNER 7 115.00 (603274) 115 kV Bus a. Apply fault at the RENNER 7 115.00 (603274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_382 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_383 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_384 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_385 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_386 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_388 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_391 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_392 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_393 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_394 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_395 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_396 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_397 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_398 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_399 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_400 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_401 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_402 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_403 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_404 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_405 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_406 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_409 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G1_1 (541546), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_410 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_411 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_412 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_413 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_414 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_417 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_418 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_419 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_420 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_421 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_422 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_423 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_424 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_425 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_426 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_427 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_428 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_429 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_430 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_431 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_432 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_433 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_434 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_435 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_436 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_437 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_438 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_439 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_440 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_441 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_442 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_443 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_444 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_445 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_446 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_447 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_448 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_449 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_450 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_451 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_452 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_453 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_454 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_455 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_456 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_457 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_458 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_459 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_460 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_461 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_462 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_463 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_464 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_465 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_466 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_467 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_468 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_469 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_470 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_471 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_472 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_473 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_474 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_475 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_476 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_477 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_478 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_479 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_480 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_481 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_482 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_483 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_484 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_485 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_486 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_487 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_488 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_489 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_490 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_491 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_492 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_493 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_494 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_495 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_496 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_497 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_498 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_499 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_500 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | No | No | No | No | Unstable power response with failed voltage recovery was observed at the Grand Prairie units (645065, 645066, 645067, and 645068). This issue was also present in the base case, with no CQ units contributing to it. | The issue is resolved by removal of reclosing action. This mitigation is also required in the base case.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_502 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_503 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_505 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_506 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_507 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_508 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_509 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_510 | 3 Phase fault on S1220 5 161.00 (646220) 161 kV Bus a. Apply fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1220 5 (646220) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_511 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_512 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_513 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_514 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_515 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_516 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_517 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1299 5 (646299) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_518 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_519 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_520 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_521 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_522 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_523 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_524 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_525 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_526 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_527 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_528 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_529 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_530 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_531 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_532 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_533 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_534 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_535 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_536 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_537 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_538 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_539 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_540 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_541 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_542 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_543 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_544 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_545 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_546 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_547 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_548 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_549 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_550 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_552 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_553 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_554 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_555 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_556 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_557 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_558 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_559 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_560 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_561 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_562 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_563 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_564 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_565 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_566 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_567 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_568 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_569 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_570 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_571 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_572 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_573 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_574 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_575 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_576 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_577 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_578 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_579 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_580 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_581 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_582 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_583 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_584 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_585 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_586 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_587 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550), and LAKERD1_1 (541171). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 b.5. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 b.4. AINSWRT9 (640053) 34.5 kV to AINSWRT7 (640051) 115.0 kV Two Winding #1 b.5. AINSWRT7 (640051) 115.0 kV to AINSWRT8 (640052) 69.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to CANADY1G (640005) 13.8 kV Two Winding #1 b.2. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.3. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.4. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 b.5. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COZAD 7 115.00 (640144) 115 kV Bus a. Apply Fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.3. COZAD 7 (640144) 115.0 kV to COZAD 8 (640145) 69.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 b.4. COZAD 7 (640144) 115.0 kV to COZAD 9 (640146) 34.5 kV to COZAD T1 9 (643043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply Fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.2. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.3. LXNGTN 7 (640256) 115.0 kV to LEXNGTN8 (640257) 69.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 b.4. LXNGTN 7 (640256) 115.0 kV to LEXNGTN9 (640258) 34.5 kV to LEXINGTONT19 (643094) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply Fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 b.4. LOWELL 7 (640261) 115.0 kV to LOWELL 8 (640262) 69.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TOWER 7 115.00 (640383) 115 kV Bus a. Apply Fault at the TOWER 7 115.00 (640383) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.2. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.3. TOWER 9 (640385) 12.5 kV to TOWER 7 (640383) 115.0 kV Two Winding #1 b.4. TOWER 7 (640383) 115.0 kV to TOWER A9 (640384) 34.5 kV to TOWER T2 9 (643154) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. VALENTN7 (640392) 115.0 kV to VALTN.W7 (640394) 115.0 kV Transmission Circuit #1 b.4. VALENTN7 (640392) 115.0 kV to VALENTN9 (640393) 34.5 kV to VALENTINET19 (643160) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.4. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.5. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.8. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.2. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.4. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.5. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply Fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY1G (645011) 18.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply Fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY2G (645012) 23.0 kV to Generator #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1361 5 161.00 (646361) 161 kV Bus a. Apply Fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator #4 b.3. SARPY 5G (645035) 13.8 kV to Generator #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1278 5 (646278) 161.0 kV to Load #O0 b.2. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.9. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.7. S1260 5 (646260) 161.0 kV to load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to Load #O0 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1298 5 (646298) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G19-070-GEN1 (763991). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G19-070-GEN1 (763991). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: NEWHRVST W (635332). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B1 9 (635401) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to RICHLAND W (637024) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: HGHLND W2 (635408). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to Load #M2 b.2. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.4. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.4. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.5. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on TBGS_A 7 115.00 (650277) 115 kV Bus a. Apply Fault at the TBGS_A 7 115.00 (650277) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on TBGS_B 7 115.00 (650278) 115 kV Bus a. Apply Fault at the TBGS_B 7 115.00 (650278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.7. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to HALLAM3G (640021) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to SHELDN1G (640019) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SHELDN2G (640020) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.3. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.5. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on S900 8 69.000 (647900) 69 kV Bus a. Apply Fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.4. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.5. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 b.7. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.6. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on 991TP 8 69.000 (647091) 69 kV Bus a. Apply Fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on FREM B 8 69.000 (647422) 69 kV Bus a. Apply Fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.3. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 b.4. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 b.5. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on S937 8 69.000 (647937) 69 kV Bus a. Apply Fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S937 8 (647937) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 b.2. S937 8 (647937) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G19-070-GEN1 (763991). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply Fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SBRIDGE T8 (635227) 69.0 kV to NEAL N 8 (635204) 69.0 kV Transmission Circuit #1 b.2. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply Fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply Fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOSPER 7 (640194) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply Fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply Fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.1 7 (640240) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on STUART 7 115.00 (640367) 115 kV Bus a. Apply Fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STUART 7 (640367) 115.0 kV to ATKINSN7 (640058) 115.0 kV Transmission Circuit #1 b.2. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S914A 8 (647014) 69.0 kV Transmission Circuit #1 b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY4 (640102) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply Fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.LK7 (640244) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 b.2. JOHN.LK7 (640244) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.2. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1210 5 (646210) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply Fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 5 (650169) 161.0 kV to S1214 5 (646214) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on CANADAY7 115.00 (640103) 115 kV Bus a. Apply Fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALENTN7 (640392) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. VALENTN7 (640392) 115.0 kV to HARMONY7 (640210) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on AXTELL 7 (640066) 115 kV Bus a. Apply Fault at the AXTELL 7 (640066) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on JOHN.2 7 (640242) 115 kV Bus a. Apply Fault at the JOHN.2 7 (640242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.2 7 (640242) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on S909 8 (647909) 69 kV Bus a. Apply Fault at the S909 8 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on AINSWRT7 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on S1347 5 (646347) 161 kV Bus a. Apply Fault at the S1347 5 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES1 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES2 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES3 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. TBGS 1G (650001) 13.8 kV to Generator #1 b.4. TBGS 2G (650002) 13.8 kV to Generator #2 b.5. TBGS 3G (650003) 13.8 kV to Generator #3 b.6. TBGS 4G (650004) 13.8 kV to Generator #4 b.7. TBGS LFG G (650010) 4.2 kV to Generator #10 b.8. TBGS 1G (650001) 13.8 kV to Load #S1 b.9. TBGS 2G (650002) 13.8 kV to Load #S1 b.10. TBGS 3G (650003) 13.8 kV to Load #S1 b.11. TBGS 4G (650004) 13.8 kV to Load #S1 b.12. TBGS 1G (650001) 13.8 kV to remove bus # b.13. TBGS 2G (650002) 13.8 kV to remove bus # b.14. TBGS 3G (650003) 13.8 kV to remove bus # b.15. TBGS 4G (650004) 13.8 kV to remove bus # b.16. TBGS LFG G (650010) 4.2 kV to remove bus # b.17. TBGS_A 7 (650277) 115.0 kV to remove bus # b.18. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES4 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES5 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 1G (650001) 13.8 kV to Generator #1 b.3. TBGS 2G (650002) 13.8 kV to Generator #2 b.4. TBGS 3G (650003) 13.8 kV to Generator #3 b.5. TBGS 1G (650001) 13.8 kV to Load #S1 b.6. TBGS 2G (650002) 13.8 kV to Load #S1 b.7. TBGS 3G (650003) 13.8 kV to Load #S1 b.8. TBGS 1G (650001) 13.8 kV to remove bus # b.9. TBGS 2G (650002) 13.8 kV to remove bus # b.10. TBGS 3G (650003) 13.8 kV to remove bus # b.11. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES6 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES7 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_LES8 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 2G (650002) 13.8 kV to Generator #2 b.3. TBGS 3G (650003) 13.8 kV to Generator #3 b.4. TBGS 4G (650004) 13.8 kV to Generator #4 b.5. TBGS LFG G (650010) 4.2 kV to Generator #10 b.6. TBGS 1G (650001) 13.8 kV to Generator #1 b.7. TBGS 1G (650001) 13.8 kV to Load #S1 b.8. TBGS 2G (650002) 13.8 kV to Load #S1 b.9. TBGS 3G (650003) 13.8 kV to Load #S1 b.10. TBGS 1G (650001) 13.8 kV to remove bus # b.11. TBGS 2G (650002) 13.8 kV to remove bus # b.12. TBGS 3G (650003) 13.8 kV to remove bus # b.13. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW10 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW11 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW12 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW13 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW14 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW15 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW16 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW17 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW5 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW6 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW7 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW8 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW9 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD1 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD2 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD3 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.4. COOPER1G (640009) 22.0 kV to Generator #1 b.5. COOPER1G (640009) 22.0 kV to Load #S1 b.6. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD4 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD5 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD6 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD7 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD1 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD10 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD11 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD12 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD13 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD14 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD15 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to remove bus # b.2. S1217T19 (648217) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD16 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD17 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 b.4. S1305 5 (646305) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD18 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to Load #O0 b.5. S1210 5 (646210) 161.0 kV to Load #OW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD19 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.3. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.5. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.7. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.8. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.9. S1297 9 (649297) 13.8 kV to Load #O0 b.10. S1297 9 (649297) 13.8 kV to remove bus # b.11. S1297 9 (649297) 13.8 kV to Generator #1 b.12. S3451 3 (645451) 345.0 kV to remove bus # b.13. S3451T39 (648251) 13.8 kV to remove bus # b.14. S3451T49 (648351) 13.8 kV to remove bus # b.15. S1297 5 (646297) 161.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD2 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD20 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S1297 9 (649297) 13.8 kV to Generator #1 b.3. S1297 9 (649297) 13.8 kV to Load #O0 b.4. S1297 9 (649297) 13.8 kV to remove bus # b.5. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.6. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.7. S1237 5 (646237) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.9. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.10. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.11. S3451T49 (648351) 13.8 kV to remove bus # b.12. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.13. S1297 5 (646297) 161.0 kV to remove bus # b.14. S3451T39 (648251) 13.8 kV to remove bus # b.15. S3451 3 (645451) 345.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD21 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.4. S939 8 (647939) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.5. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.6. S3459T39 (648259) 13.8 kV to remove bus # b.7. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.9. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.10. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.11. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.13. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.14. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.15. S921 8 (647921) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.16. S937 8 (647937) 69.0 kV to remove bus # b.17. S909 8 (647909) 69.0 kV to remove bus # b.18. S1209T19 (648209) 13.8 kV to remove bus # b.19. S3459 3 (645459) 345.0 kV to remove bus # b.20. S3459T69 (648359) 13.8 kV to remove bus # b.21. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD22 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1220 5 (646220) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.3. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.5. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.6. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.7. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. S1211T19 (648211) 13.8 kV to remove bus # b.9. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.10. S950 8 (647950) 69.0 kV to remove bus # b.11. S1250T19 (648250) 13.8 kV to remove bus # b.12. N OMA 4G (645024) 15.0 kV to Generator #4 b.13. N OMA 4G (645024) 15.0 kV to remove bus # b.14. N OMA 5G (645025) 20.0 kV to Generator #5 b.15. N OMA 5G (645025) 20.0 kV to remove bus # b.16. S1299 5 (646299) 161.0 kV to remove bus # b.17. S1286 5 (646286) 161.0 kV to remove bus # b.18. S1211 5 (646211) 161.0 kV to remove bus # b.19. S1297 9 (649297) 13.8 kV to Generator #1 b.20. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.21. NO5 AUX9 (645125) 4.2 kV to Load #S1 b.22. S1211T39 (645127) 13.8 kV to Load #S1 b.23. S1211T39 (645127) 13.8 kV to Load #S2 b.24. S1211T39 (645127) 13.8 kV to Load #S3 b.25. S1211T39 (645127) 13.8 kV to Load #S4 b.26. S1211T39 (645127) 13.8 kV to Load #S5 b.27. S1211T49 (645128) 13.8 kV to Load #S1 b.28. S1211T49 (645128) 13.8 kV to Load #S2 b.29. S1211T49 (645128) 13.8 kV to Load #S3 b.30. S1211T49 (645128) 13.8 kV to Load #S4 b.31. S1211T49 (645128) 13.8 kV to Load #S5 b.32. S1250 5 (646250) 161.0 kV to Load #O0 b.33. S1297 9 (649297) 13.8 kV to Load #O0 b.34. NO4 AUX9 (645124) 2.4 kV to remove bus # b.35. NO5 AUX9 (645125) 4.2 kV to remove bus # b.36. S1211T39 (645127) 13.8 kV to remove bus # b.37. S1211T49 (645128) 13.8 kV to remove bus # b.38. S1297 5 (646297) 161.0 kV to remove bus # b.39. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD23 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.3. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.4. S1206T19 (648206) 13.8 kV to remove bus # b.5. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.8. S3456T49 (648256) 13.8 kV to remove bus # b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S938 8 (647938) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S924 8 (647924) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.12. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.13. S1206T29 (648306) 13.8 kV to remove bus # b.14. SARPY 3G (645033) 13.8 kV to Generator #3 b.15. SARPY 3G (645033) 13.8 kV to remove bus # b.16. SCBSD G (645030) 4.2 kV to remove bus # b.17. SARPY 4G (645034) 13.8 kV to Generator #4 b.18. SARPY 4G (645034) 13.8 kV to remove bus # b.19. SARPY 5G (645035) 13.8 kV to Generator #5 b.20. SARPY 5G (645035) 13.8 kV to remove bus # b.21. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD24 | Single Phase Fault with Stuck Breaker on S1216 5 (646216) 161 kV Bus a. Apply Fault at the S1216 5 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.3. S1206T19 (648206) 13.8 kV to remove bus # b.4. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.7. S3456T49 (648256) 13.8 kV to remove bus # b.8. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S916 8 (647916) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.12. S1206T29 (648306) 13.8 kV to remove bus # b.13. SARPY 3G (645033) 13.8 kV to Generator #3 b.14. SARPY 3G (645033) 13.8 kV to remove bus # b.15. SCBSD G (645030) 4.2 kV to remove bus # b.16. SARPY 4G (645034) 13.8 kV to Generator #4 b.17. SARPY 4G (645034) 13.8 kV to remove bus # b.18. SARPY 5G (645035) 13.8 kV to Generator #5 b.19. SARPY 5G (645035) 13.8 kV to remove bus # b.20. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD25 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1286 5 (646286) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.3. S1220 5 (646220) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.5. S1201T19 (648201) 13.8 kV to remove bus # b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.7. S1206T19 (648206) 13.8 kV to remove bus # b.8. S1229 5 (646229) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.9. S1201 5 (646201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD26 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.4. S1259 5 (646259) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.6. S3455T39 (648355) 13.8 kV to remove bus # b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.8. S3455T19 (648255) 13.8 kV to remove bus # b.9. S1255 5 (646255) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD27 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.3. S940 8 (647940) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD28 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.5. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.7. S3451T49 (648351) 13.8 kV to remove bus # b.8. S1251 5 (646251) 161.0 kV to S3451 3 (645451) 345.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.9. S3451T39 (648251) 13.8 kV to remove bus # b.10. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.11. S1297 5 (646297) 161.0 kV to remove bus # b.12. FC1A 5 (645100) 161.0 kV to remove bus # b.13. FC1A3 9 (645103) 4.2 kV to remove bus # b.14. FC1A4 9 (645104) 4.2 kV to remove bus # b.15. S1251 5 (646251) 161.0 kV to remove bus # b.16. S1297 9 (649297) 13.8 kV to Generator #1 b.17. S1297 9 (649297) 13.8 kV to Load #O0 b.18. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD3 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G1_1 (541546), OUTLAW_G21_1 (541549), OUTLAW_G22_1 (541550). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD4 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD5 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to Load #O0 b.3. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1206 5 (646206) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD6 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD7 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD8 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to Load #O0 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD9 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G19-070-GEN1 (763991). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G19-070-GEN1 (763991). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. to AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Open # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: FRMR CTY W1 (635020). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | No | No | No | No | Unstable power response with failed voltage recovery was observed at the Grand Prairie units (645065, 645066, 645067, and 645068). | The issue is resolved by removal of reclosing action.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25S | Base | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: G287 NOB4G (600114) and G287 NOB2G (600112). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_065 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_066 | 3 Phase fault on DENISON5 161.00 (652561) 161 kV Bus a. Apply fault at the DENISON5 161.00 (652561) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_067 | 3 Phase fault on OSGOOD5 161.00 (656527) 161 kV Bus a. Apply fault at the OSGOOD5 161.00 (656527) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_068 | 3 Phase fault on SIOUXCY5 161.00 (652566) 161 kV Bus a. Apply fault at the SIOUXCY5 161.00 (652566) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_069 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_070 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_071 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_072 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_073 | 3 Phase fault on DENISON4 230.00 (652567) 230 kV Bus a. Apply fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON4 (652567) 230.0 kV to DENISON5 (652561) 161.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_074 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_075 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_076 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_077 | 3 Phase fault on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_078 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_079 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_080 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_081 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_082 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_083 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_084 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_085 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_086 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_087 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_088 | 3 Phase fault on NW5&BENTON7 115.00 (650212) 115 kV Bus a. Apply fault at the NW5&BENTON7 115.00 (650212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.2. W LINCOLN 7 (650208) 115.0 kV to NW5&BENTON7 (650212) 115.0 kV Transmission Circuit #1 b.3. NW5&BENTON7 (650212) 115.0 kV to NW5BENTN 9 (650312) 12.5 kV to 121TERTIARY (650512) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_089 | 3 Phase fault on 4&MORTON 7 115.00 (650205) 115 kV Bus a. Apply fault at the 4&MORTON 7 115.00 (650205) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4&MORTON 7 (650205) 115.0 kV to 19&ALVO 7 (650215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_090 | 3 Phase fault on W LINCOLN 7 115.00 (650208) 115 kV Bus a. Apply fault at the W LINCOLN 7 115.00 (650208) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W LINCOLN 7 (650208) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_091 | 3 Phase fault on NW12&ARBOR7 115.00 (650226) 115 kV Bus a. Apply fault at the NW12&ARBOR7 115.00 (650226) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to NW12&ARBOR7 (650226) 115.0 kV Transmission Circuit #1 b.3. NW12&ARBOR7 (650226) 115.0 kV to NW12&AR 9 (650326) 12.5 kV to 261TERTIARY (650526) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_092 | 3 Phase fault on 27FLETCHER7 115.00 (650228) 115 kV Bus a. Apply fault at the 27FLETCHER7 115.00 (650228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_093 | 3 Phase fault on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.2. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_094 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_095 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Fixed Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_096 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_097 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_098 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_099 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_100 | 3 Phase fault on 70&BLUFF 7 115.00 (650269) 115 kV Bus a. Apply fault at the 70&BLUFF 7 115.00 (650269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_101 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_102 | 3 Phase fault on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_103 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_104 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_105 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_106 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_107 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_108 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_109 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_110 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_111 | 3 Phase fault on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.4. 70&BLUFF 9 (650369) 13.8 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 5 (650169) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_112 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_113 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_114 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_115 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_116 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_117 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_118 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_119 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_120 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_121 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_122 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_123 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_124 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_125 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_126 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_127 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_128 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_129 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_130 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_131 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_132 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_133 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_134 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_135 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_136 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.4. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_137 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_138 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_139 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_140 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_141 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_142 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_143 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_144 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_145 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_146 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_147 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_148 | 3 Phase fault on HARMONY7 115.00 (640210) 115 kV Bus a. Apply fault at the HARMONY7 115.00 (640210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_149 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_150 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_151 | 3 Phase fault on GOTHNBG7 115.00 (640196) 115 kV Bus a. Apply fault at the GOTHNBG7 115.00 (640196) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. GOTHNBG7 (640196) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_152 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_153 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_154 | 3 Phase fault on ATKINSN7 115.00 (640058) 115 kV Bus a. Apply fault at the ATKINSN7 115.00 (640058) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLECREEK 7 (640465) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.2. ATKINSN7 (640058) 115.0 kV to EMMET 7 (640165) 115.0 kV Transmission Circuit #1 b.3. ATKINSN7 (640058) 115.0 kV to STUART 7 (640367) 115.0 kV Transmission Circuit #1 b.4. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_155 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_156 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_157 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_158 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_159 | 3 Phase fault on DAVEY 7 115.00 (640155) 115 kV Bus a. Apply fault at the DAVEY 7 115.00 (640155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVEY 7 (640155) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 b.2. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_160 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_161 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_162 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_163 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_164 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_165 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_166 | 3 Phase fault on SPENCER7 115.00 (640349) 115 kV Bus a. Apply fault at the SPENCER7 115.00 (640349) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEILL 7 (640305) 115.0 kV to SPENCER7 (640349) 115.0 kV Transmission Circuit #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_167 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_168 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_169 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_170 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_171 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_172 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_173 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_174 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_175 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_176 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_177 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_178 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_179 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_180 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_181 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_182 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_183 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_184 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_185 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_186 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_187 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_188 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_189 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_190 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_191 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_192 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_193 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_194 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_195 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_196 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_197 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_198 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_199 | 3 Phase fault on ORLEANS8 69.000 (640311) 69 kV Bus a. Apply fault at the ORLEANS8 69.000 (640311) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_200 | 3 Phase fault on VALENTN7 115.00 (640392) 115 kV Bus a. Apply fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALENTN7 (640392) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_201 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_202 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_203 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 7 (640580) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_204 | 3 Phase fault on BASSETT 869.000 (640581) 69 kV Bus a. Apply fault at the BASSETT 869.000 (640581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_205 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_206 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_207 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_208 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_209 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_210 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_211 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_212 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_213 | 3 Phase fault on BONESTL7 115.00 (652475) 115 kV Bus a. Apply fault at the BONESTL7 115.00 (652475) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_214 | 3 Phase fault on VETAL_TP-RM7115.00 (659153) 115 kV Bus a. Apply fault at the VETAL_TP-RM7115.00 (659153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_215 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_216 | 3 Phase fault on ARMOUR 7 115.00 (652501) 115 kV Bus a. Apply fault at the ARMOUR 7 115.00 (652501) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMOUR 7 (652501) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_217 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_218 | 3 Phase fault on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.2. TYNDALL7 (652525) 115.0 kV to TYNDALL8 (652286) 69.0 kV Two Winding #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_219 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_220 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_221 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_222 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_223 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_224 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_225 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_226 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_227 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_228 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_229 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_230 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_231 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_232 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_233 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_234 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to DENISONWEST8 (658030) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_235 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_236 | 3 Phase fault on WINNER 7 115.00 (652494) 115 kV Bus a. Apply fault at the WINNER 7 115.00 (652494) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREGORY7 (652478) 115.0 kV to WINNER 7 (652494) 115.0 kV Transmission Circuit #1 b.2. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.3. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_237 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_238 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_239 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_240 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_241 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_242 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_243 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_244 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_246 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_247 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_248 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_249 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_250 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_251 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_252 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_253 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_254 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_255 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1299 5 (646299) 161.0 kV Load #O0 b.4. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_256 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037-TAP (762712) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_257 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_258 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_259 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_260 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_261 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_262 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_263 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_264 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_265 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_266 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_267 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_268 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_269 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_270 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_271 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_272 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_273 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_274 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_275 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_276 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_277 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_278 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_279 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_280 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_281 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_282 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_283 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_284 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_285 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_286 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_287 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_288 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_289 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_290 | 3 Phase fault on S1361 5 161.00 (646361) 161 kV Bus a. Apply fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_291 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_292 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_293 | 3 Phase fault on 991TP 8 69.000 (647091) 69 kV Bus a. Apply fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_294 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_295 | 3 Phase fault on S6846 8 69.000 (647846) 69 kV Bus a. Apply fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_296 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_297 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_298 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_299 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_300 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_301 | 3 Phase fault on S902 8 69.000 (647902) 69 kV Bus a. Apply fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_302 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_303 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_304 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_305 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_306 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_307 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_308 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_309 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_310 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_311 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_312 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_313 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_314 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_315 | 3 Phase fault on S916 8 69.000 (647916) 69 kV Bus a. Apply fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_316 | 3 Phase fault on S917 8 69.000 (647917) 69 kV Bus a. Apply fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_317 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_318 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_319 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_320 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_321 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_322 | 3 Phase fault on S928 8 69.000 (647928) 69 kV Bus a. Apply fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_323 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_324 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_325 | 3 Phase fault on FREM F 8 69.000 (647426) 69 kV Bus a. Apply fault at the FREM F 8 69.000 (647426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM F 8 (647426) 69.0 kV to S992 8 (647992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_326 | 3 Phase fault on FREM D 8 69.000 (647424) 69 kV Bus a. Apply fault at the FREM D 8 69.000 (647424) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM D 8 (647424) 69.0 kV to FREM E 8 (647425) 69.0 kV Transmission Circuit #1 b.2. FREM D 8 (647424) 69.0 kV to S976 8 (647976) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_327 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_328 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_329 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_330 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_331 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_332 | 3 Phase fault on FREM C 8 69.000 (647423) 69 kV Bus a. Apply fault at the FREM C 8 69.000 (647423) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM C 8 (647423) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_333 | 3 Phase fault on FREM E 8 69.000 (647425) 69 kV Bus a. Apply fault at the FREM E 8 69.000 (647425) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM E 8 (647425) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_334 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_335 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_336 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_337 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_338 | 3 Phase fault on ASH GRV8 69.000 (647100) 69 kV Bus a. Apply fault at the ASH GRV8 69.000 (647100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_339 | 3 Phase fault on 979TP 8 69.000 (647079) 69 kV Bus a. Apply fault at the 979TP 8 69.000 (647079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_340 | 3 Phase fault on S914A 8 69.000 (647014) 69 kV Bus a. Apply fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_341 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_342 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_343 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_344 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_345 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_346 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_347 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_348 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_349 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_350 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_351 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_352 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_353 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_354 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_355 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_356 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_357 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_358 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_359 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_360 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_361 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_362 | 3 Phase fault on S900 8 69.000 (647900) 69 kV Bus a. Apply fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S900 8 (647900) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_363 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_364 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_365 | 3 Phase fault on S942 8 69.000 (647942) 69 kV Bus a. Apply fault at the S942 8 69.000 (647942) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S942 8 (647942) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_366 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT_REACT7 (541517) 345.0 kV remove bus # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_367 | 3 Phase fault on RENNER 7 115.00 (603274) 115 kV Bus a. Apply fault at the RENNER 7 115.00 (603274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYC7 (603008) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to RENNER 7 (603274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_370 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_371 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_372 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to PERRY___-NI8 (659895) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_373 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_374 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_375 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_376 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_377 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_378 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_379 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_380 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_381 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to MERRIL 8 (635393) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_382 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_383 | 3 Phase fault on HUDSON 8 69.000 (635385) 69 kV Bus a. Apply fault at the HUDSON 8 69.000 (635385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON 8 (635385) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_384 | 3 Phase fault on IRETONT8 69.000 (635391) 69 kV Bus a. Apply fault at the IRETONT8 69.000 (635391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IRETONT8 (635391) 69.0 kV to EAGLE___-NI8 (659901) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_385 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to LEMARSINDT 8 (635265) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_386 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_388 | 3 Phase fault on J1620 POI 115.00 (46207) 115 kV Bus a. Apply fault at the J1620 POI 115.00 (46207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1620 POI (46207) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_391 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENISON8 (652583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_392 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to DENSOUMAIN8 (658031) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_393 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K318MEC -NI8 (659855) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_394 | 3 Phase fault on NEWTAP 69.000 (99999) 69 kV Bus a. Apply fault at the NEWTAP 69.000 (99999) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWTAP (99999) 69.0 kV to K338WTCT-NI8 (659897) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_395 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_396 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_397 | 3 Phase fault on N HAYS3 115.00 (530581) 115 kV Bus a. Apply fault at the N HAYS3 115.00 (530581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_398 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_399 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_400 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_401 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_402 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_403 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_404 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_405 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_406 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_407 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_408 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_409 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_410 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_411 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_412 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_413 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_414 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_417 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_418 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_419 | 3 Phase fault on PLYMOTH8 69.000 (635224) 69 kV Bus a. Apply fault at the PLYMOTH8 69.000 (635224) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH8 (635224) 69.0 kV to SIOUXCY8 (652574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_420 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_421 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_422 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_423 | 3 Phase fault on AINSWND7 115.00 (640050) 115 kV Bus a. Apply fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_424 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_425 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_426 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_427 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_428 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_429 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_430 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_431 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_432 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_433 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_434 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_435 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_436 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_437 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_438 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_439 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_440 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_441 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_442 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_443 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_444 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_445 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_446 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_447 | 3 Phase fault on CODY 7 115.00 (640117) 115 kV Bus a. Apply fault at the CODY 7 115.00 (640117) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CODY 7 (640117) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_448 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_449 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_450 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_451 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_452 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_453 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_454 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_455 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_456 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_457 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_458 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_459 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_460 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_461 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_462 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_463 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_464 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_465 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_466 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_467 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_468 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_469 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_470 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_471 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_472 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_473 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_474 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_475 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_476 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_477 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_478 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_479 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_480 | 3 Phase fault on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_481 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_482 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_483 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_484 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_485 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_486 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_487 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_488 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_489 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_490 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_491 | 3 Phase fault on RIVERDL7 115.00 (640331) 115 kV Bus a. Apply fault at the RIVERDL7 115.00 (640331) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_492 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_493 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_494 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_495 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_496 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_497 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_498 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_499 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_500 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | No | No | No | No | Unstable power response with failed voltage recovery was observed at the Grand Prairie units (645065, 645066, 645067, and 645068). This issue was also present in the base case, with no CQ units contributing to it. | The issue is resolved by removal of reclosing action. This mitigation is also required in the base case.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_502 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_503 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 3 (640520) 345.0 kV to G18-065-TAP (763031) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_505 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_506 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_507 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_508 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_509 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_510 | 3 Phase fault on S1220 5 161.00 (646220) 161 kV Bus a. Apply fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1220 5 (646220) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_511 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_512 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_513 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_514 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_515 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_516 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_517 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1299 5 (646299) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_518 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_519 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_520 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM F 8 (647426) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_521 | 3 Phase fault on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_522 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_523 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to NORTHBEND4 (652516) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_524 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_525 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_526 | 3 Phase fault on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_527 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_528 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_529 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_530 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_531 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_532 | 3 Phase fault on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_533 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K216LIBE-NI8 (659946) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_534 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K412HTNM-NI8 (659953) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_535 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K301HINT-NI8 (659971) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_536 | 3 Phase fault on SIOUXCY8 69.000 (652574) 69 kV Bus a. Apply fault at the SIOUXCY8 69.000 (652574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY8 (652574) 69.0 kV to K135CONC-NI8 (659980) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_537 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to MANNINGTAP 8 (656267) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_538 | 3 Phase fault on DENISON8 69.000 (652583) 69 kV Bus a. Apply fault at the DENISON8 69.000 (652583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENISON8 (652583) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_539 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_540 | 3 Phase fault on PAHOJA__-BE4230.00 (659311) 230 kV Bus a. Apply fault at the PAHOJA__-BE4230.00 (659311) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_541 | 3 Phase fault on K335AMAI-NI869.000 (659854) 69 kV Bus a. Apply fault at the K335AMAI-NI869.000 (659854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K335AMAI-NI8 (659854) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_542 | 3 Phase fault on K307DENI-NI869.000 (659862) 69 kV Bus a. Apply fault at the K307DENI-NI869.000 (659862) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K307DENI-NI8 (659862) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_543 | 3 Phase fault on K306SCHL-NI869.000 (659885) 69 kV Bus a. Apply fault at the K306SCHL-NI869.000 (659885) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K306SCHL-NI8 (659885) 69.0 kV to J6BOYER_-NI8 (659912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_544 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J1CENTER-NI8 (659907) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_545 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to J15_____-NI8 (659921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_546 | 3 Phase fault on EAGLE___-NI869.000 (659901) 69 kV Bus a. Apply fault at the EAGLE___-NI869.000 (659901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE___-NI8 (659901) 69.0 kV to K217HWDN-NI8 (659942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_547 | 3 Phase fault on J6BOYER_-NI869.000 (659912) 69 kV Bus a. Apply fault at the J6BOYER_-NI869.000 (659912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J6BOYER_-NI8 (659912) 69.0 kV to J12_____-NI8 (659918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_548 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_549 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_550 | 3 Phase fault on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_552 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_553 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_554 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_555 | 3 Phase fault on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWRT8 (640052) 69.0 kV to AINSWRT7 (640051) 115.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_556 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_557 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_558 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_559 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG8 (640101) 69.0 kV to CAMBRIG7 (640100) 115.0 kV to CAMBRIDGET19 (643028) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_560 | 3 Phase fault on COZAD 7 115.00 (640144) 115 kV Bus a. Apply fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 8 (640145) 69.0 kV to COZAD 7 (640144) 115.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_561 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_562 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_563 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_564 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.LK8 (640245) 69.0 kV to JOHN.LK7 (640244) 115.0 kV to JOHNSONLKT19 (643089) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_565 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_566 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 8 (640262) 69.0 kV to LOWELL 7 (640261) 115.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_567 | 3 Phase fault on ORLEANS7 115.00 (640310) 115 kV Bus a. Apply fault at the ORLEANS7 115.00 (640310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORLEANS8 (640311) 69.0 kV to ORLEANS7 (640310) 115.0 kV to ORLEANS T1 9 (643120) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_568 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_569 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_570 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_571 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_572 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_573 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_574 | 3 Phase fault on BASSETT 7115.00 (640580) 115 kV Bus a. Apply fault at the BASSETT 7115.00 (640580) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASSETT 8 (640581) 69.0 kV to BASSETT 7 (640580) 115.0 kV to BASSETT T1 9 (643180) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_575 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_576 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_577 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_578 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_579 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_580 | 3 Phase fault on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_581 | 3 Phase fault on WHITE 3 345.00 (652537) 345 kV Bus a. Apply fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WHITE 3 (652537) 345.0 kV to WHITE 7 (652538) 115.0 kV to WHITE 9 (652293) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_582 | 3 Phase fault on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_583 | 3 Phase fault on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_584 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_585 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_586 | 3 Phase fault on MISSION7 115.00 (652482) 115 kV Bus a. Apply fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MISSION7 (652482) 115.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_LOCAL_FAULT_587 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_001 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_002 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_003 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_004 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_005 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_006 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_007 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_008 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_009 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_012 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_014 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_015 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_017 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_018 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_019 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_020 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_021 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_022 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_023 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_024 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_025 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_026 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_027 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_028 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_029 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_030 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_031 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_032 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_033 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_034 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_035 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_036 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_037 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_040 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_041 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_042 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_043 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_044 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_045 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_046 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_047 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_048 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_001 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_002 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to ANSON 7 (603200) 115.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 b.4. ANSON 7 (603200) 115.0 kV to ANS 72G (600020) 13.8 kV to ANS 73G (600021) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_003 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_004 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_005 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_006 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_007 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_008 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_009 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_010 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON5 (652561) 161.0 kV to EXIRA 5 (652603) 161.0 kV Transmission Circuit #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_011 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_013 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_014 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_016 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_017 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_018 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_019 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_020 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_021 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_022 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_023 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_024 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 b.5. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_025 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_026 | Single Phase Fault with Stuck Breaker on OGALALA4 230.00 (640302) 230 kV Bus a. Apply Fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.3. OGALALA4 (640302) 230.0 kV to OGALALANPPD7 (640304) 115.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_027 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_028 | Single Phase Fault with Stuck Breaker on AINSWRT7 115.00 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 115.00 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. AINSWRT7 (640051) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 b.4. AINSWRT9 (640053) 34.5 kV to AINSWRT7 (640051) 115.0 kV Two Winding #1 b.5. AINSWRT7 (640051) 115.0 kV to AINSWRT8 (640052) 69.0 kV to AINSWORTHT29 (643002) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_029 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_030 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.4. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_031 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_032 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to CANADY1G (640005) 13.8 kV Two Winding #1 b.2. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.3. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.4. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 b.5. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.6. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_033 | Single Phase Fault with Stuck Breaker on COZAD 7 115.00 (640144) 115 kV Bus a. Apply Fault at the COZAD 7 115.00 (640144) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COZAD 7 (640144) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.3. COZAD 7 (640144) 115.0 kV to COZAD 8 (640145) 69.0 kV to COZAD T2 9 (643174) 13.8 kV Three Winding #1 b.4. COZAD 7 (640144) 115.0 kV to COZAD 9 (640146) 34.5 kV to COZAD T1 9 (643043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_035 | Single Phase Fault with Stuck Breaker on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply Fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.2. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 b.3. LXNGTN 7 (640256) 115.0 kV to LEXNGTN8 (640257) 69.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 b.4. LXNGTN 7 (640256) 115.0 kV to LEXNGTN9 (640258) 34.5 kV to LEXINGTONT19 (643094) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_036 | Single Phase Fault with Stuck Breaker on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply Fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. LOWELL 7 (640261) 115.0 kV to PROSSER7 (640321) 115.0 kV Transmission Circuit #1 b.4. LOWELL 7 (640261) 115.0 kV to LOWELL 8 (640262) 69.0 kV to LOWELL T1 9 (643096) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_037 | Single Phase Fault with Stuck Breaker on MINDEN 7 115.00 (640275) 115 kV Bus a. Apply Fault at the MINDEN 7 115.00 (640275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.2. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 b.3. MINDEN 7 (640275) 115.0 kV to MINDEN 9 (640276) 34.5 kV to MINDEN T1 9 (643102) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_038 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_039 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_041 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_042 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_043 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_044 | Single Phase Fault with Stuck Breaker on TOWER 7 115.00 (640383) 115 kV Bus a. Apply Fault at the TOWER 7 115.00 (640383) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.2. RIVERDL7 (640331) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.3. TOWER 9 (640385) 12.5 kV to TOWER 7 (640383) 115.0 kV Two Winding #1 b.4. TOWER 7 (640383) 115.0 kV to TOWER A9 (640384) 34.5 kV to TOWER T2 9 (643154) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_045 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.2. HARMONY7 (640210) 115.0 kV to VALENTN7 (640392) 115.0 kV Transmission Circuit #1 b.3. VALENTN7 (640392) 115.0 kV to VALTN.W7 (640394) 115.0 kV Transmission Circuit #1 b.4. VALENTN7 (640392) 115.0 kV to VALENTN9 (640393) 34.5 kV to VALENTINET19 (643160) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_046 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_047 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_048 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_049 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_050 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_051 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_052 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_053 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_054 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.3. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_055 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET29 (643081) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_056 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.9. HOLDREG7 (640224) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_057 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_058 | Single Phase Fault with Stuck Breaker on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply Fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.3. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.4. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 b.5. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 b.6. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T1 9 (643091) 13.8 kV Three Winding #1 b.7. KEARNEY7 (640250) 115.0 kV to KEARNEY9 (640251) 34.5 kV to KEARNEY T2 9 (643092) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_059 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_060 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_061 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARMONY7 (640210) 115.0 kV to ST.FRANC (640351) 115.0 kV Transmission Circuit #1 b.2. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.4. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.5. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.8. WINNER 7 (652494) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_062 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_063 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_064 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_065 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_066 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_067 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_068 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_069 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_070 | Single Phase Fault with Stuck Breaker on VFODNES4 230.00 (652398) 230 kV Bus a. Apply Fault at the VFODNES4 230.00 (652398) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VFODNES4 (652398) 230.0 kV to G17-175TAP (762237) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_071 | Single Phase Fault with Stuck Breaker on WHITE 3 345.00 (652537) 345 kV Bus a. Apply Fault at the WHITE 3 345.00 (652537) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_072 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_073 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_074 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.3. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.4. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.5. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.6. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.7. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_075 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 b.2. DENISON5 (652561) 161.0 kV to DENISON4 (652567) 230.0 kV to DENISON 9 (652657) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_076 | Single Phase Fault with Stuck Breaker on SPENCER5 161.00 (652563) 161 kV Bus a. Apply Fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.2. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.3. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.4. SPENCER5 (652563) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.5. OSGOOD5 (656527) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 b.6. SPENCER5 (652563) 161.0 kV to SPENCER8 (652581) 69.0 kV to SPENCER 9 (652562) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_077 | Single Phase Fault with Stuck Breaker on MISSION7 115.00 (652482) 115 kV Bus a. Apply Fault at the MISSION7 115.00 (652482) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.FRANC (640351) 115.0 kV to MISSION7 (652482) 115.0 kV Transmission Circuit #1 b.2. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #1 b.3. MISSION9 (652264) 24.9 kV to MISSION7 (652482) 115.0 kV Two Winding #2 b.4. MARTIN 7 (652479) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.5. MISSION7 (652482) 115.0 kV to VETAL_TP-RM7 (659153) 115.0 kV Transmission Circuit #1 b.6. MISSION7 (652482) 115.0 kV to WITTEN__-RB7 (659166) 115.0 kV Transmission Circuit #1 b.7. MISSION7 (652482) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_078 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_079 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_080 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_081 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_082 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_083 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_084 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_085 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_086 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_087 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_088 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_089 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_090 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_091 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_092 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_093 | Single Phase Fault with Stuck Breaker on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply Fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY1G (645011) 18.0 kV to Generator #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_094 | Single Phase Fault with Stuck Breaker on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply Fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEBCTY2G (645012) 23.0 kV to Generator #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_095 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_096 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_097 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_098 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_099 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_100 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_101 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_102 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_103 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_104 | Single Phase Fault with Stuck Breaker on S1361 5 161.00 (646361) 161 kV Bus a. Apply Fault at the S1361 5 161.00 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_105 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_106 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_107 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_108 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_109 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_110 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_111 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_112 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_113 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_114 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_115 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_116 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_117 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_118 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_119 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_120 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_121 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator #4 b.3. SARPY 5G (645035) 13.8 kV to Generator #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_122 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_123 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_124 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_125 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_126 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_127 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 b.2. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_128 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_129 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_130 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_131 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_132 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_133 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_134 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to G18-037-TAP (762712) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_135 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_136 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_137 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_138 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_139 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_140 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_141 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_142 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_143 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_144 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_145 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_146 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_147 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_148 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_149 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_150 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_151 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_152 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_153 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_154 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_155 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_156 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_157 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_158 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_159 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_160 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_161 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_162 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_163 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_164 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_165 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_166 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_167 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_168 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_169 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_170 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_171 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1278 5 (646278) 161.0 kV to Load #O0 b.2. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_172 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_173 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_174 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.9. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_175 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.6. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.7. S1260 5 (646260) 161.0 kV to load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_176 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_177 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to Load #O0 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_178 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_179 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_180 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_181 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_182 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1298 5 (646298) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_183 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_184 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_185 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_186 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_187 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_188 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_189 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_190 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_191 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_192 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Frequency protection trips: WSEC 4G (635024). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_193 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_194 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_195 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_196 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_197 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_198 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_199 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_200 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_201 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_202 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_203 | Single Phase Fault with Stuck Breaker on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply Fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.3. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.4. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.5. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.6. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 b.7. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_204 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_205 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_206 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_207 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_208 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_209 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_210 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_211 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_212 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_213 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_214 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_215 | Single Phase Fault with Stuck Breaker on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply Fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_216 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_217 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_218 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_219 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_220 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 b.3. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_221 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_222 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to IDA GRV B1 9 (635207) 34.5 kV Two Winding #1 b.2. IDA CO 3 (635206) 345.0 kV to IDA GRV B2 9 (635208) 34.5 kV Two Winding #1 b.3. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_223 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_224 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_225 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_226 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_227 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to GLACIAL EDGE (637009) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_228 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_229 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_230 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B1 9 (635401) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_231 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to RICHLAND W (637024) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_232 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_233 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_234 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. HGHLND B2 9 (635402) 34.5 kV to HIGHLND 3 (635400) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_235 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_236 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_237 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to Load #M2 b.2. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_238 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_239 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_240 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_241 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_242 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_243 | Single Phase Fault with Stuck Breaker on BUCKEYE_230 230.00 (530702) 230 kV Bus a. Apply Fault at the BUCKEYE_230 230.00 (530702) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.4. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.5. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.6. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.7. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.8. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 b.9. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.10. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_244 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_245 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_246 | Single Phase Fault with Stuck Breaker on SHAYS_230 230.00 (530610) 230 kV Bus a. Apply Fault at the SHAYS_230 230.00 (530610) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.4. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 b.5. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_247 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.3. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_248 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_249 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_250 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_251 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_252 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_253 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_254 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_255 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_256 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_257 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_258 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_259 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_260 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_261 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_262 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.4. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_263 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_264 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_265 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_266 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_267 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_268 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_269 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_270 | Single Phase Fault with Stuck Breaker on 56&I80 7 115.00 (650261) 115 kV Bus a. Apply Fault at the 56&I80 7 115.00 (650261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVEY 7 (640155) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 56&I80 7 (650261) 115.0 kV Transmission Circuit #1 b.3. 56&I80 7 (650261) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 b.4. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.5. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 b.6. 56&I80 7 (650261) 115.0 kV to 56&I80 9 (650361) 12.5 kV to 611TERTIARY (650561) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_271 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_272 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_273 | Single Phase Fault with Stuck Breaker on TBGS_A 7 115.00 (650277) 115 kV Bus a. Apply Fault at the TBGS_A 7 115.00 (650277) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_274 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 115.00 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 115.00 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_275 | Single Phase Fault with Stuck Breaker on TBGS_B 7 115.00 (650278) 115 kV Bus a. Apply Fault at the TBGS_B 7 115.00 (650278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TBGS 4G (650004) 13.8 kV to TBGS LFG G (650010) 4.2 kV Two Winding #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.4. TBGS_A 7 (650277) 115.0 kV to TBGS 4G (650004) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.7. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_276 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_277 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.5. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.6. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_278 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_279 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_280 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_281 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_282 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_283 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_284 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_285 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_286 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_287 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to HALLAM3G (640021) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_288 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to SHELDN1G (640019) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_289 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_290 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SHELDN2G (640020) 13.8 kV Two Winding #1 b.2. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_291 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_292 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_293 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_294 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_295 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_296 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_297 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLM1G (640010) 23.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_298 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_299 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_300 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_301 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_302 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_303 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. N.PLATT4 (640286) 230.0 kV to N.PLATT7 (640287) 115.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_304 | Single Phase Fault with Stuck Breaker on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_305 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_306 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_307 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_308 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_309 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_310 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.3. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_311 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.3. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_312 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_313 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_314 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_315 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_316 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_317 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_318 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_319 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_320 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_321 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_322 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_323 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_324 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_325 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_326 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_327 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_328 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_329 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_330 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_331 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_332 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_333 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_334 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_335 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_336 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_337 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_338 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_339 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_340 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_341 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_342 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_343 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_344 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_346 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_347 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_348 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.5. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_349 | Single Phase Fault with Stuck Breaker on S900 8 69.000 (647900) 69 kV Bus a. Apply Fault at the S900 8 69.000 (647900) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 979TP 8 (647079) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.2. 979TP 8 (647079) 69.0 kV to S960 8 (647960) 69.0 kV Transmission Circuit #1 b.3. 979TP 8 (647079) 69.0 kV to S979 8 (647979) 69.0 kV Transmission Circuit #1 b.4. ASH GRV8 (647100) 69.0 kV to S900 8 (647900) 69.0 kV Transmission Circuit #1 b.5. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.6. S900 8 (647900) 69.0 kV to S972 8 (647972) 69.0 kV Transmission Circuit #1 b.7. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_350 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_351 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_352 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_353 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_354 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.6. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_355 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_356 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_357 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_358 | Single Phase Fault with Stuck Breaker on S914 8 69.000 (647914) 69 kV Bus a. Apply Fault at the S914 8 69.000 (647914) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_359 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_360 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_361 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_362 | Single Phase Fault with Stuck Breaker on S914A 8 69.000 (647014) 69 kV Bus a. Apply Fault at the S914A 8 69.000 (647014) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 b.2. S914A 8 (647014) 69.0 kV to S988 8 (647988) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_363 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_364 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_365 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_366 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_367 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_368 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_369 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_370 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_371 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_372 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_373 | Single Phase Fault with Stuck Breaker on 991TP 8 69.000 (647091) 69 kV Bus a. Apply Fault at the 991TP 8 69.000 (647091) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 991TP 8 (647091) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 b.2. 991TP 8 (647091) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.3. 991TP 8 (647091) 69.0 kV to S991 8 (647991) 69.0 kV Transmission Circuit #1 b.4. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_374 | Single Phase Fault with Stuck Breaker on FREM B 8 69.000 (647422) 69 kV Bus a. Apply Fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.3. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 b.4. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 b.5. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_375 | Single Phase Fault with Stuck Breaker on S937 8 69.000 (647937) 69 kV Bus a. Apply Fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S937 8 (647937) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 b.2. S937 8 (647937) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_376 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_377 | Single Phase Fault with Stuck Breaker on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply Fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SBRIDGE T8 (635227) 69.0 kV to NEAL N 8 (635204) 69.0 kV Transmission Circuit #1 b.2. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_378 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_379 | Single Phase Fault with Stuck Breaker on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply Fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_380 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_381 | Single Phase Fault with Stuck Breaker on GOSPER 7 115.00 (640194) 115 kV Bus a. Apply Fault at the GOSPER 7 115.00 (640194) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GOSPER 7 (640194) 115.0 kV to CAMBRIG7 (640100) 115.0 kV Transmission Circuit #1 b.2. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_382 | Single Phase Fault with Stuck Breaker on JEFFREY7 115.00 (640238) 115 kV Bus a. Apply Fault at the JEFFREY7 115.00 (640238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEFFREY7 (640238) 115.0 kV to GOTHNBG7 (640196) 115.0 kV Transmission Circuit #1 b.2. JEFFREY7 (640238) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_383 | Single Phase Fault with Stuck Breaker on JOHN.1 7 115.00 (640240) 115 kV Bus a. Apply Fault at the JOHN.1 7 115.00 (640240) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.1 7 (640240) 115.0 kV to JEFFREY7 (640238) 115.0 kV Transmission Circuit #1 b.2. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_384 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_385 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to G19-069-TAP (763982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_386 | Single Phase Fault with Stuck Breaker on STUART 7 115.00 (640367) 115 kV Bus a. Apply Fault at the STUART 7 115.00 (640367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STUART 7 (640367) 115.0 kV to ATKINSN7 (640058) 115.0 kV Transmission Circuit #1 b.2. STUART 7 (640367) 115.0 kV to BASSETT 7 (640580) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_387 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_388 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_389 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_390 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_391 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: OUTLAW_G21_1 (541549) and OUTLAW_G1_1 (541546). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_392 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_393 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_394 | Single Phase Fault with Stuck Breaker on S6846 8 69.000 (647846) 69 kV Bus a. Apply Fault at the S6846 8 69.000 (647846) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6846 8 (647846) 69.0 kV to S914A 8 (647014) 69.0 kV Transmission Circuit #1 b.2. S6846 8 (647846) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_395 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_396 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_397 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_398 | Single Phase Fault with Stuck Breaker on G18-065-TAP 345.00 (763031) 345 kV Bus a. Apply Fault at the G18-065-TAP 345.00 (763031) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-065-TAP (763031) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 b.2. G18-065-TAP (763031) 345.0 kV to G18-131-TAP (763443) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_399 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_400 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY4 (640102) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_401 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_402 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to (998025) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_403 | Single Phase Fault with Stuck Breaker on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply Fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.LK7 (640244) 115.0 kV to JOHN.1 7 (640240) 115.0 kV Transmission Circuit #1 b.2. JOHN.LK7 (640244) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_404 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_405 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_406 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_407 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 b.2. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_408 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1210 5 (646210) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_409 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_410 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_411 | Single Phase Fault with Stuck Breaker on 70&BLUFF 5 161.00 (650169) 161 kV Bus a. Apply Fault at the 70&BLUFF 5 161.00 (650169) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&BLUFF 5 (650169) 161.0 kV to S1214 5 (646214) 161.0 kV Transmission Circuit #1 b.2. 70&BLUFF 5 (650169) 161.0 kV to 70&BLUFF 7 (650269) 115.0 kV to 70&BLUFF 9 (650369) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_412 | Single Phase Fault with Stuck Breaker on CANADAY7 115.00 (640103) 115 kV Bus a. Apply Fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 b.2. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_413 | Single Phase Fault with Stuck Breaker on VALENTN7 115.00 (640392) 115 kV Bus a. Apply Fault at the VALENTN7 115.00 (640392) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALENTN7 (640392) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.2. VALENTN7 (640392) 115.0 kV to HARMONY7 (640210) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_414 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_415 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_416 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_417 | Single Phase Fault with Stuck Breaker on 84&BLUFF 7 (650275) 115 kV Bus a. Apply Fault at the 84&BLUFF 7 (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_418 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_419 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_420 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_421 | Single Phase Fault with Stuck Breaker on AXTELL 7 (640066) 115 kV Bus a. Apply Fault at the AXTELL 7 (640066) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_422 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_423 | Single Phase Fault with Stuck Breaker on JOHN.2 7 (640242) 115 kV Bus a. Apply Fault at the JOHN.2 7 (640242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOHN.2 7 (640242) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_424 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_425 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_426 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_427 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_428 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_429 | Single Phase Fault with Stuck Breaker on S1209 5 (646209) 161 kV Bus a. Apply Fault at the S1209 5 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_430 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_431 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_432 | Single Phase Fault with Stuck Breaker on S909 8 (647909) 69 kV Bus a. Apply Fault at the S909 8 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_433 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_434 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_435 | Single Phase Fault with Stuck Breaker on AINSWRT7 (640051) 115 kV Bus a. Apply Fault at the AINSWRT7 (640051) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWRT7 (640051) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_436 | Single Phase Fault with Stuck Breaker on S1347 5 (646347) 161 kV Bus a. Apply Fault at the S1347 5 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_438 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_439 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_440 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_441 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G15-088-GEN4 (585248). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES1 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES2 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES3 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_A 7 (650277) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.3. TBGS 1G (650001) 13.8 kV to Generator #1 b.4. TBGS 2G (650002) 13.8 kV to Generator #2 b.5. TBGS 3G (650003) 13.8 kV to Generator #3 b.6. TBGS 4G (650004) 13.8 kV to Generator #4 b.7. TBGS LFG G (650010) 4.2 kV to Generator #10 b.8. TBGS 1G (650001) 13.8 kV to Load #S1 b.9. TBGS 2G (650002) 13.8 kV to Load #S1 b.10. TBGS 3G (650003) 13.8 kV to Load #S1 b.11. TBGS 4G (650004) 13.8 kV to Load #S1 b.12. TBGS 1G (650001) 13.8 kV to remove bus # b.13. TBGS 2G (650002) 13.8 kV to remove bus # b.14. TBGS 3G (650003) 13.8 kV to remove bus # b.15. TBGS 4G (650004) 13.8 kV to remove bus # b.16. TBGS LFG G (650010) 4.2 kV to remove bus # b.17. TBGS_A 7 (650277) 115.0 kV to remove bus # b.18. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES4 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 70&BLUFF 7 (650269) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES5 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 1G (650001) 13.8 kV to Generator #1 b.3. TBGS 2G (650002) 13.8 kV to Generator #2 b.4. TBGS 3G (650003) 13.8 kV to Generator #3 b.5. TBGS 1G (650001) 13.8 kV to Load #S1 b.6. TBGS 2G (650002) 13.8 kV to Load #S1 b.7. TBGS 3G (650003) 13.8 kV to Load #S1 b.8. TBGS 1G (650001) 13.8 kV to remove bus # b.9. TBGS 2G (650002) 13.8 kV to remove bus # b.10. TBGS 3G (650003) 13.8 kV to remove bus # b.11. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES6 | Single Phase Fault with Stuck Breaker on NW 68th & Holdrege (650114) 345 kV Bus a. Apply Fault at the NW 68th & Holdrege (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES7 | Single Phase Fault with Stuck Breaker on Wagener (650185) 345 kV Bus a. Apply Fault at the Wagener (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_LES8 | Single Phase Fault with Stuck Breaker on 84th & Bluff (650275) 115 kV Bus a. Apply Fault at the 84th & Bluff (650275) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS 2G (650002) 13.8 kV to Generator #2 b.3. TBGS 3G (650003) 13.8 kV to Generator #3 b.4. TBGS 4G (650004) 13.8 kV to Generator #4 b.5. TBGS LFG G (650010) 4.2 kV to Generator #10 b.6. TBGS 1G (650001) 13.8 kV to Generator #1 b.7. TBGS 1G (650001) 13.8 kV to Load #S1 b.8. TBGS 2G (650002) 13.8 kV to Load #S1 b.9. TBGS 3G (650003) 13.8 kV to Load #S1 b.10. TBGS 1G (650001) 13.8 kV to remove bus # b.11. TBGS 2G (650002) 13.8 kV to remove bus # b.12. TBGS 3G (650003) 13.8 kV to remove bus # b.13. TBGS_B 7 (650278) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW1 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW10 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW11 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. KNOLL S 6 (530720) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW12 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 b.3. KNOLL S 6 (530720) 230.0 kV to remove bus # b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW13 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW14 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.5. KNOLL N 6 (530558) 230.0 kV to remove bus # b.6. KNOLL S 6 (530720) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW15 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW16 | Single Phase Fault with Stuck Breaker on S HAYS6 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_GEN (530614) 0.7 kV to remove bus # b.4. SHAYS_230 (530610) 230.0 kV to remove bus # b.5. SHAYS_13.8 (530611) 13.8 kV to remove bus # b.6. SHAYS_COLLR2 (530612) 34.5 kV to remove bus # b.7. SHAYS_COLLR1 (530613) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW17 | Single Phase Fault with Stuck Breaker on KNOLL S 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL S 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL S 6 (530720) 230.0 kV to SMOKYHL6 (530592) 230.0 kV Transmission Circuit #1 b.2. KNOLL S 6 (530720) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW2 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.3. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW3 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW4 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW5 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW6 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.4. BUCKE_WTG (530705) 0.7 kV to remove bus # b.5. BUCKW_WTG (530708) 0.7 kV to remove bus # b.6. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.7. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.8. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.9. BUCKW_TERT (530706) 13.8 kV to remove bus # b.10. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.11. BUCKE_TERT (530709) 13.8 kV to remove bus # b.12. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW7 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKE_WTG (530705) 0.7 kV to remove bus # b.4. BUCKW_WTG (530708) 0.7 kV to remove bus # b.5. BUCKEYE_230 (530702) 230.0 kV to remove bus # b.6. BUCKEYE_E1 (530703) 34.5 kV to remove bus # b.7. BUCKEYE_E2 (530704) 34.5 kV to remove bus # b.8. BUCKW_TERT (530706) 13.8 kV to remove bus # b.9. BUCKEYE_W2 (530707) 34.5 kV to remove bus # b.10. BUCKE_TERT (530709) 13.8 kV to remove bus # b.11. BUCKEYE_W1 (530710) 34.5 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW8 | Single Phase Fault with Stuck Breaker on POSTROCK6 (530584) 230 kV Bus a. Apply Fault at the POSTROCK6 (530584) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_MIDW9 | Single Phase Fault with Stuck Breaker on KNOLL N 6 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL N 6 (530558) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #Z1 b.4. KNOLL N 6 (530558) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD1 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD2 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.3. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD3 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.3. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.4. COOPER1G (640009) 22.0 kV to Generator #1 b.5. COOPER1G (640009) 22.0 kV to Load #S1 b.6. COOPER1G (640009) 22.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD4 | Single Phase Fault with Stuck Breaker on TWIN CH4 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 b.3. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.4. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD5 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD6 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 b.3. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_NPPD7 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD1 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD10 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD11 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD12 | Single Phase Fault with Stuck Breaker on S1260 5 (646260) 161 kV Bus a. Apply Fault at the S1260 5 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus # b.2. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.3. S1260 5 (646260) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD13 | Single Phase Fault with Stuck Breaker on S3455 3 (645455) 345 kV Bus a. Apply Fault at the S3455 3 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD14 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD15 | Single Phase Fault with Stuck Breaker on S1217 5 (646217) 161 kV Bus a. Apply Fault at the S1217 5 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to remove bus # b.2. S1217T19 (648217) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD16 | Single Phase Fault with Stuck Breaker on S1244 5 (646244) 161 kV Bus a. Apply Fault at the S1244 5 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1244 5 (646244) 161.0 kV to Load #O0 b.4. S1244 5 (646244) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD17 | Single Phase Fault with Stuck Breaker on S1305 5 (646305) 161 kV Bus a. Apply Fault at the S1305 5 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 b.4. S1305 5 (646305) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Oscillatory reactive power response was observed at GEN-2018-043 and GEN-2020-084. The issue was caused by both project units controlling the same POI branch, leading to VAR oscillations. | Updating the monitoring branches of individual units in the REPCA1 models to their respective collection systems resolves the issue.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD18 | Single Phase Fault with Stuck Breaker on S1210 5 (646210) 161 kV Bus a. Apply Fault at the S1210 5 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to Load #O0 b.5. S1210 5 (646210) 161.0 kV to Load #OW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD19 | Single Phase Fault with Stuck Breaker on S1251 5 (646251) 161 kV Bus a. Apply Fault at the S1251 5 (646251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.3. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.5. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.7. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.8. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.9. S1297 9 (649297) 13.8 kV to Load #O0 b.10. S1297 9 (649297) 13.8 kV to remove bus # b.11. S1297 9 (649297) 13.8 kV to Generator #1 b.12. S3451 3 (645451) 345.0 kV to remove bus # b.13. S3451T39 (648251) 13.8 kV to remove bus # b.14. S3451T49 (648351) 13.8 kV to remove bus # b.15. S1297 5 (646297) 161.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD2 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD20 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S1297 9 (649297) 13.8 kV to Generator #1 b.3. S1297 9 (649297) 13.8 kV to Load #O0 b.4. S1297 9 (649297) 13.8 kV to remove bus # b.5. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.6. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.7. S1237 5 (646237) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.8. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.9. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.10. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.11. S3451T49 (648351) 13.8 kV to remove bus # b.12. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.13. S1297 5 (646297) 161.0 kV to remove bus # b.14. S3451T39 (648251) 13.8 kV to remove bus # b.15. S3451 3 (645451) 345.0 kV to remove bus # b.16. S1305 5 (646305) 161.0 kV to remove bus # b.17. S1341 5 (646341) 161.0 kV to remove bus # b.18. S1298 5 (646298) 161.0 kV to remove bus # b.19. FC1A 5 (645100) 161.0 kV to remove bus # b.20. FC1A3 9 (645103) 4.2 kV to remove bus # b.21. FC1A4 9 (645104) 4.2 kV to remove bus # b.22. S1251 5 (646251) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD21 | Single Phase Fault with Stuck Breaker on S3459 3 (645459) 345 kV Bus a. Apply Fault at the S3459 3 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.4. S939 8 (647939) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.5. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.6. S3459T39 (648259) 13.8 kV to remove bus # b.7. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.8. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.9. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.10. S1231 5 (646231) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.11. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.12. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.13. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.14. S1250 5 (646250) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #2 b.15. S921 8 (647921) 69.0 kV to S909 8 (647909) 69.0 kV Transmission Circuit #1 b.16. S937 8 (647937) 69.0 kV to remove bus # b.17. S909 8 (647909) 69.0 kV to remove bus # b.18. S1209T19 (648209) 13.8 kV to remove bus # b.19. S3459 3 (645459) 345.0 kV to remove bus # b.20. S3459T69 (648359) 13.8 kV to remove bus # b.21. S1209 5 (646209) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD22 | Single Phase Fault with Stuck Breaker on S1220 5 (646220) 161 kV Bus a. Apply Fault at the S1220 5 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1220 5 (646220) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.3. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.4. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.5. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.6. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.7. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. S1211T19 (648211) 13.8 kV to remove bus # b.9. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.10. S950 8 (647950) 69.0 kV to remove bus # b.11. S1250T19 (648250) 13.8 kV to remove bus # b.12. N OMA 4G (645024) 15.0 kV to Generator #4 b.13. N OMA 4G (645024) 15.0 kV to remove bus # b.14. N OMA 5G (645025) 20.0 kV to Generator #5 b.15. N OMA 5G (645025) 20.0 kV to remove bus # b.16. S1299 5 (646299) 161.0 kV to remove bus # b.17. S1286 5 (646286) 161.0 kV to remove bus # b.18. S1211 5 (646211) 161.0 kV to remove bus # b.19. S1297 9 (649297) 13.8 kV to Generator #1 b.20. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.21. NO5 AUX9 (645125) 4.2 kV to Load #S1 b.22. S1211T39 (645127) 13.8 kV to Load #S1 b.23. S1211T39 (645127) 13.8 kV to Load #S2 b.24. S1211T39 (645127) 13.8 kV to Load #S3 b.25. S1211T39 (645127) 13.8 kV to Load #S4 b.26. S1211T39 (645127) 13.8 kV to Load #S5 b.27. S1211T49 (645128) 13.8 kV to Load #S1 b.28. S1211T49 (645128) 13.8 kV to Load #S2 b.29. S1211T49 (645128) 13.8 kV to Load #S3 b.30. S1211T49 (645128) 13.8 kV to Load #S4 b.31. S1211T49 (645128) 13.8 kV to Load #S5 b.32. S1250 5 (646250) 161.0 kV to Load #O0 b.33. S1297 9 (649297) 13.8 kV to Load #O0 b.34. NO4 AUX9 (645124) 2.4 kV to remove bus # b.35. NO5 AUX9 (645125) 4.2 kV to remove bus # b.36. S1211T39 (645127) 13.8 kV to remove bus # b.37. S1211T49 (645128) 13.8 kV to remove bus # b.38. S1297 5 (646297) 161.0 kV to remove bus # b.39. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD23 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.3. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.4. S1206T19 (648206) 13.8 kV to remove bus # b.5. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.7. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.8. S3456T49 (648256) 13.8 kV to remove bus # b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S938 8 (647938) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S924 8 (647924) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.12. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.13. S1206T29 (648306) 13.8 kV to remove bus # b.14. SARPY 3G (645033) 13.8 kV to Generator #3 b.15. SARPY 3G (645033) 13.8 kV to remove bus # b.16. SCBSD G (645030) 4.2 kV to remove bus # b.17. SARPY 4G (645034) 13.8 kV to Generator #4 b.18. SARPY 4G (645034) 13.8 kV to remove bus # b.19. SARPY 5G (645035) 13.8 kV to Generator #5 b.20. SARPY 5G (645035) 13.8 kV to remove bus # b.21. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD24 | Single Phase Fault with Stuck Breaker on S1216 5 (646216) 161 kV Bus a. Apply Fault at the S1216 5 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.3. S1206T19 (648206) 13.8 kV to remove bus # b.4. S1206 5 (646206) 161.0 kV to CBLUFFS5 (635001) 161.0 kV Transmission Circuit #1 b.5. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.6. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.7. S3456T49 (648256) 13.8 kV to remove bus # b.8. S1232 5 (646232) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.9. S1244 5 (646244) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.10. S916 8 (647916) 69.0 kV to S906 N 8 (647006) 69.0 kV Transmission Circuit #1 b.11. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.12. S1206T29 (648306) 13.8 kV to remove bus # b.13. SARPY 3G (645033) 13.8 kV to Generator #3 b.14. SARPY 3G (645033) 13.8 kV to remove bus # b.15. SCBSD G (645030) 4.2 kV to remove bus # b.16. SARPY 4G (645034) 13.8 kV to Generator #4 b.17. SARPY 4G (645034) 13.8 kV to remove bus # b.18. SARPY 5G (645035) 13.8 kV to Generator #5 b.19. SARPY 5G (645035) 13.8 kV to remove bus # b.20. S1206 5 (646206) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD25 | Single Phase Fault with Stuck Breaker on S1286 5 (646286) 161 kV Bus a. Apply Fault at the S1286 5 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1286 5 (646286) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.3. S1220 5 (646220) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 b.5. S1201T19 (648201) 13.8 kV to remove bus # b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.7. S1206T19 (648206) 13.8 kV to remove bus # b.8. S1229 5 (646229) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.9. S1201 5 (646201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD26 | Single Phase Fault with Stuck Breaker on S1361 5 (646361) 161 kV Bus a. Apply Fault at the S1361 5 (646361) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1361 5 (646361) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.3. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.4. S1259 5 (646259) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.5. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 b.6. S3455T39 (648355) 13.8 kV to remove bus # b.7. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.8. S3455T19 (648255) 13.8 kV to remove bus # b.9. S1255 5 (646255) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD27 | Single Phase Fault with Stuck Breaker on S1221 5 (646221) 161 kV Bus a. Apply Fault at the S1221 5 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.2. S1255 5 (646255) 161.0 kV to S1221 5 (646221) 161.0 kV Transmission Circuit #1 b.3. S940 8 (647940) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD28 | Single Phase Fault with Stuck Breaker on S1298 5 (646298) 161 kV Bus a. Apply Fault at the S1298 5 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.5. S1341 5 (646341) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 b.7. S3451T49 (648351) 13.8 kV to remove bus # b.8. S1251 5 (646251) 161.0 kV to S3451 3 (645451) 345.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 b.9. S3451T39 (648251) 13.8 kV to remove bus # b.10. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.11. S1297 5 (646297) 161.0 kV to remove bus # b.12. FC1A 5 (645100) 161.0 kV to remove bus # b.13. FC1A3 9 (645103) 4.2 kV to remove bus # b.14. FC1A4 9 (645104) 4.2 kV to remove bus # b.15. S1251 5 (646251) 161.0 kV to remove bus # b.16. S1297 9 (649297) 13.8 kV to Generator #1 b.17. S1297 9 (649297) 13.8 kV to Load #O0 b.18. S1297 9 (649297) 13.8 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD3 | Single Phase Fault with Stuck Breaker on S3458 3 (645458) 345 kV Bus a. Apply Fault at the S3458 3 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD4 | Single Phase Fault with Stuck Breaker on S3740 3 (645740) 345 kV Bus a. Apply Fault at the S3740 3 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD5 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to Load #O0 b.3. S1206 5 (646206) 161.0 kV to S1201 5 (646201) 161.0 kV Transmission Circuit #1 b.4. S1206 5 (646206) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD6 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD7 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD8 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to Load #O0 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_LOCAL_FAULT_OPPD9 | Single Phase Fault with Stuck Breaker on S1206 5 (646206) 161 kV Bus a. Apply Fault at the S1206 5 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_001 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_012 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_013 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_014 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_015 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_016 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_017 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_018 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_019 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_020 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_021 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_022 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_023 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_024 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_025 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_026 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_027 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_028 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_029 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_030 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_031 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_032 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_033 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_034 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_035 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_036 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_037 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_038 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_039 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_040 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_041 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_042 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_043 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_044 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_045 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_046 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_047 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_048 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_049 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_050 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_051 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_052 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_053 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FALLOW 3 (635590) 345.0 kV to ARBR HL 3 (635580) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_054 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. ARBR HL 3 (635580) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_055 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_056 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_057 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_058 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to J412 B1 9 (635254) 34.5 kV Two Winding #1 b.3. J412 POI 3 (635252) 345.0 kV to J412 B2 9 (635255) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_059 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_060 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_061 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_062 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_063 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_064 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_065 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_066 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to G18-125-TAP (763410) 345.0 kV Transmission Circuit #1 b.2. to AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Open # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_067 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_068 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_069 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_070 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Voltage protection trips: G16-074-GEN1 (587683). | Protection disabled with no impact to stability.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_071 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_072 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_073 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_074 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_075 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_076 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_077 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_078 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_079 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_080 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_081 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_083 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_084 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Transfer | GROUP2_P4_REGIONAL_FAULT_085 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. The issue is also observed in the base case and is not impacted by the CQ units. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_368 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_369 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_387 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_389 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_390 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_415 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_416 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_501 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | No | No | No | No | No | Unstable power response with failed voltage recovery was observed at the Grand Prairie units (645065, 645066, 645067, and 645068). | The issue is resolved by removal of reclosing action.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_LOCAL_FAULT_584 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_010 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_011 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_013 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_016 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_038 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_039 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P1_REGIONAL_FAULT_049 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P4_LOCAL_FAULT_437 | Single Phase Fault with Stuck Breaker on RAUN 3 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to remove bus # | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 | 25W | Base | GROUP2_P4_REGIONAL_FAULT_082 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | No | No | No | No | No | No | No | Simulation crashes after fault due to Non-Convergence of multiple dynamic controller models at J524 (637031), J412 (635259), IDA GRV (635215), J455 (631248 and 631249) and J542 (637031) units. Disabling the controllers allows the simulation to complete with no stability issue observed. | No mitigation required.
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_001 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_002 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_003 | 3 Phase fault on LEMARST5 161.00 (635260) 161 kV Bus a. Apply fault at the LEMARST5 161.00 (635260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEMARST5 (635260) 161.0 kV Transmission Circuit #1 b.2. LEMARST5 (635260) 161.0 kV to LEMARS S 5 (635261) 161.0 kV Transmission Circuit #1 b.3. LEMARST5 (635260) 161.0 kV to LTL SIOUX 5 (635360) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_004 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_005 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_006 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Fixed Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_007 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_008 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_009 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_010 | 3 Phase fault on BRKNGCO3 345.00 (601031) 345 kV Bus a. Apply fault at the BRKNGCO3 345.00 (601031) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BRKNGCO3 (601031) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_011 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_012 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to WSX FLS7 (603017) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_013 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_014 | 3 Phase fault on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_015 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_016 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_017 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES9 8 (605664) 34.5 kV Three Winding #9 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_018 | 3 Phase fault on NOBLES 3 345.00 (601034) 345 kV Bus a. Apply fault at the NOBLES 3 345.00 (601034) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLES 3 (601034) 345.0 kV to NOBLES 7 (603194) 115.0 kV to NOBLES10 8 (605665) 34.5 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_019 | 3 Phase fault on LAWRENC7 115.00 (603012) 115 kV Bus a. Apply fault at the LAWRENC7 115.00 (603012) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWRENC7 (603012) 115.0 kV to SPLT RK7 (603016) 115.0 kV Transmission Circuit #1 b.2. LAWRENC8 (605191) 69.0 kV to LAWRENC7 (603012) 115.0 kV Two Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_020 | 3 Phase fault on SPLT RK4 230.00 (602004) 230 kV Bus a. Apply fault at the SPLT RK4 230.00 (602004) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. SPLT RK4 (602004) 230.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK161 9 (605725) 13.8 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_021 | 3 Phase fault on SPLT RK5 161.00 (602005) 161 kV Bus a. Apply fault at the SPLT RK5 161.00 (602005) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPLT RK5 (602005) 161.0 kV to ROCK CO5 (602039) 161.0 kV Transmission Circuit #1 b.2. SPLT RK5 (602005) 161.0 kV to SPLT RK7 (603016) 115.0 kV to SPLT RK230 9 (605726) 36.2 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_022 | 3 Phase fault on CAYLER5 161.00 (631183) 161 kV Bus a. Apply fault at the CAYLER5 161.00 (631183) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAYLER5 (631183) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_023 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_024 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_025 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_026 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_027 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_028 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_029 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_030 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_031 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_032 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_033 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_034 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_035 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_036 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_037 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_038 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_039 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_040 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_041 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_042 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_043 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_044 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_045 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_046 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_047 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_048 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_049 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_050 | 3 Phase fault on BVISTA 5 161.00 (635280) 161 kV Bus a. Apply fault at the BVISTA 5 161.00 (635280) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BVISTA 5 (635280) 161.0 kV to WISDOM5 (656570) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_051 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_052 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_053 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_054 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_055 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_056 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_057 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_058 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_059 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_060 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_061 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to PLYMOTH8 (635224) 69.0 kV to PLYMXT9 (635228) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_062 | 3 Phase fault on SPENCER5 161.00 (652563) 161 kV Bus a. Apply fault at the SPENCER5 161.00 (652563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_063 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2020-001 CF | 25S | Transfer | GROUP2_P1_LOCAL_FAULT_064 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes