## Executive Summary
Executive Summary: DISIS-2020-001 Phase 1 of Power Flow
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on April 30, 2020. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 1.8 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2020-001 Phase 1 - Restudy includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
DISIS Manual Version 1.8
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
15,720.88 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $1,533,069,969.50 Steady State Network Upgrade $801,604,665.50 Interconnection Costs: $731,465,304
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
By: SPP Generator Interconnection Department
Published: March 17, 2023
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4498600% | SPP | Phase 1 Draft Posting
4500200% | SPP | Phase 1 Final Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4500200% | Interconnection Costs | 1 | Executive Summary | Updated Total Network Upgrade and Interconnection Costs to reflect the removal of UID 156928
4500200% | Interconnection Costs | 1 | Executive Summary | Updated Total Network Upgrade and Interconnection Costs to reflect the removal of UID 156879 and 156880
4500200% | Interconnection Costs | 1 | Executive Summary | Updated Total Network Upgrade and Interconnection Costs to reflect the correction of UID 156981
4500200% | Interconnection Costs | 1 | Executive Summary | Updated Total Network Upgrade and Interconnection Costs to reflect the removal of UID 156953 and 156954
4500200% | Generator Area | 4 | Requests | Updated area for project GEN-2020-057 and GEN-2020-089 to KCPL
4500200% | Generator Area | 4 | Requests | Updated area for project GEN-2020-070 to MIDW
4500200% | Generator POI | 4 | Requests | Updated POI for project GEN-2020-057 to Craig-West Gardner 345 kV
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the removal of UID 156928
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection cost allocatiom to reflect the correction of UID 156929
4500200% | Network Upgrade | 6 | Assigned Upgrade Costs | Updated network upgrade cost allocation to correspond to the corrected generation areas
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the removal of UID's 156879 and 156880
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the correction of UID's 156897 and 156898
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the correction of UID 156981
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection Costs to reflect the removal of UID's 156953 and 156954
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection cost allocation for UID 156955
4500200% | Interconnection Costs | 6 | Assigned Upgrade Costs | Updated Interconnection cost allocation for UID 156393 to reflect the maximum summer MWs
4500200% | Network Upgrade | 6 | Assigned Upgrade Costs | Updated network upgrade cost allocation for S1362 to S1363 161 kV Build Second Line
4500200% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the removal of UID 156928
4500200% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the removal of UID's 156879 and 156880
4500200% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the correction of UID's 156897 and 156898
4500200% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the correction of UID 156981
4500200% | Interconnection Costs | 7 | Upgrade Summary | Updated Interconnection Costs to reflect the removal of UID's 156953 and 156954
4500200% | TDF Values | 8 | All Thermal | Updated thermal overloads and associated TDF values to correspond to the corrected generation areas

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
GEN-2020-006 | 01 - North | 22 | DIS-20-1 | Solar | 250 | 0 | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 (ftlo) P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | ER/NR | BEPC | Bowman 230kV substation | DISIS STAGE
GEN-2020-014 | 01 - North | 22 | DIS-20-1 | Thermal | 45 | 45 | None | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 - North | 22 | DIS-20-1 | Wind | 235 | 235 | None | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 - North | 22 | DIS-20-1 | Solar | 99 | 66 | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 (ftlo) 659183 CHARL_CK-BE3 345 659390 PATENTGT-BE3 345 1 | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 - North | 22 | DIS-20-1 | Solar | 150 | 150 | None | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-093 | 01 - North | 22 | DIS-20-1 | Solar | 150 | 150 | None | ER/NR | BEPC | Whitlock Substation 230 kV | DISIS STAGE
GEN-2020-001 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 200 | 200 | None | ER/NR | BEPC | Sidney 345 kV Substation | DISIS STAGE
GEN-2020-002 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 81 | 74 | 646362 S1362 5 161 646363 S1363 5 161 2 (ftlo) 646362 S1362 5 161 646363 S1363 5 161 1 | ER/NR | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 320 | 320 | None | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 215 | 215 | None | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 | 255 | None | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-027 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 | 45 | 646362 S1362 5 161 646363 S1363 5 161 2 (ftlo) 646362 S1362 5 161 646363 S1363 5 161 1 | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-028 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 255 | 255 | None | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-030 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 | 45 | 646362 S1362 5 161 646363 S1363 5 161 2 (ftlo) 646362 S1362 5 161 646363 S1363 5 161 1 | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-031 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 | 303 | None | ER/NR | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-033 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 50 | 45 | 646362 S1362 5 161 646363 S1363 5 161 2 (ftlo) 646362 S1362 5 161 646363 S1363 5 161 1 | ER/NR | OPPD | S1281 - S1362 161kV (S1363) | DISIS STAGE
GEN-2020-036 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 303 | 303 | None | ER/NR | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-038 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 303 | 303 | None | ER/NR | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 - Nebraska | 22 | DIS-20-1 | Thermal | 56.52 | 56.52 | None | ER/NR | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-069 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 52.85 | 52.85 | None | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-070 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 255 | 255 | None | ER/NR | MIDW | Postrock to Axtell 345 KV line | DISIS STAGE
GEN-2020-077 | 02 - Nebraska | 22 | DIS-20-1 | Wind | 151.2 | 89 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 (ftlo) P12:115:WERE:KNOB-NPPD-115:::HV: | ER | NPPD | North Hebron to Fairbury 115 kV | DISIS STAGE
GEN-2020-078 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 100 | 100 | None | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 350 | 350 | None | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 - Nebraska | 22 | DIS-20-1 | Solar | 250 | 250 | None | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 - Central | 22 | DIS-20-1 | Solar | 45 | 0 | Voltage Violation | ER | KCPL | South Waverly 69 kV | DISIS STAGE
ASGI-2020-002 | 03 - Central | 22 | DIS-20-1 | Solar | 45 | 0 | Voltage Violation | ER | KCPL | Post Oak 69 kV | DISIS STAGE
ASGI-2020-003 | 03 - Central | 22 | DIS-20-1 | Solar | 45 | 0 | Voltage Violation | ER | KCPL | Carollton 161 kV | DISIS STAGE
GEN-2020-003 | 03 - Central | 22 | DIS-20-1 | Thermal | 58 | 58 | None | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 - Central | 22 | DIS-20-1 | Solar | 650 | 0 | Voltage Violation | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 - Central | 22 | DIS-20-1 | Solar | 250 | 0 | Voltage Violation | ER/NR | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-022 | 03 - Central | 22 | DIS-20-1 | Solar | 125 | 125 | None | ER/NR | SUNC | Holcomb Substation 115KV | DISIS STAGE
GEN-2020-052 | 03 - Central | 22 | DIS-20-1 | Wind | 250.999 | 250.999 | None | ER/NR | WERE | Neosho-Delaware 345 kV | DISIS STAGE
GEN-2020-056 | 03 - Central | 22 | DIS-20-1 | Solar | 20 | 20 | None | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 - Central | 22 | DIS-20-1 | Storage | 424.5 | 0 | Voltage Violation | ER/NR | KCPL | Craig-West Gardner 345 kV | DISIS STAGE
GEN-2020-058 | 03 - Central | 22 | DIS-20-1 | Solar | 424.5 | 0 | Voltage Violation | ER/NR | KCPL | Craig-West Gardner 345 kV | DISIS STAGE
GEN-2020-061 | 03 - Central | 22 | DIS-20-1 | Thermal | 29 | 29 | None | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 - Central | 22 | DIS-20-1 | Thermal | 64 | 64 | None | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-071 | 03 - Central | 22 | DIS-20-1 | Wind | 252 | 252 | None | ER/NR | WERE | Swissvale to Morris 230 KV line | DISIS STAGE
GEN-2020-072 | 03 - Central | 22 | DIS-20-1 | Solar | 150 | 0 | Voltage Violation | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 - Central | 22 | DIS-20-1 | Solar | 190 | 0 | Voltage Violation | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-076 | 03 - Central | 22 | DIS-20-1 | Storage | 200 | 0 | Voltage Violation | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-079 | 03 - Central | 22 | DIS-20-1 | Solar | 225 | 0 | Voltage Violation | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-082 | 03 - Central | 22 | DIS-20-1 | Solar | 20 | 0 | Voltage Violation | ER/NR | SUNC | North Liberal 115 kV Substation | DISIS STAGE
GEN-2020-086 | 03 - Central | 22 | DIS-20-1 | Solar | 500 | 0 | Voltage Violation | ER/NR | WERE | Benton to Wolf Creek 345 kV Line | DISIS STAGE
GEN-2020-088 | 03 - Central | 22 | DIS-20-1 | Solar | 150 | 142 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 (ftlo) 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-089 | 03 - Central | 22 | DIS-20-1 | Solar | 104 | 0 | Voltage Violation | ER/NR | KCPL | Dakota 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 - Central | 22 | DIS-20-1 | Storage | 204.3 | 0 | Voltage Violation | ER/NR | WERE | Wolf Creek- Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 - Southeast | 22 | DIS-20-1 | Solar | 140 | 140 | None | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 - Southeast | 22 | DIS-20-1 | Solar | 113 | 103 | 511409 TREASILD7 345 515800 GRACMNT7 345 1 ftlo 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 | ER/NR | AEPW | Snyder-Altus Jct. 138kV | DISIS STAGE
GEN-2020-015 | 04 - Southeast | 22 | DIS-20-1 | Solar | 104 | 69 | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 ftlo P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | ER/NR | OGE | Johnston County 345 kV Substation | DISIS STAGE
GEN-2020-016 | 04 - Southeast | 22 | DIS-20-1 | Wind | 202 | 165 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 ftlo P12:138:WFEC:ANADRKO_CHRYRD:::: | ER/NR | WFEC | Snyder SW-Cache 138 kV line | DISIS STAGE
GEN-2020-020 | 04 - Southeast | 22 | DIS-20-1 | Solar | 201.6 | 201.6 | None | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-023 | 04 - Southeast | 22 | DIS-20-1 | Storage | 202 | 202 | None | ER/NR | OGE | Woodring 345 KV Station | DISIS STAGE
GEN-2020-054 | 04 - Southeast | 22 | DIS-20-1 | Solar | 298 | 298 | None | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-055 | 04 - Southeast | 22 | DIS-20-1 | Storage | 71 | 71 | None | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-074 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 | 134 | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 ftlo P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-075 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 | 165 | 511467 L.E.S.-4 138 997967 LES 5 138 2 ftlo P12:345:OKGE-AEPW:BKRBKR365:::: | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-081 | 04 - Southeast | 22 | DIS-20-1 | Storage | 200 | 200 | None | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-085 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 | 335 | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 ftlo P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 - Southeast | 22 | DIS-20-1 | Solar | 500 | 412 | 511467 L.E.S.-4 138 997967 LES 5 138 2 ftlo P12:345:OKGE-AEPW:BKRBKR365:::: | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 - Southeast | 22 | DIS-20-1 | Solar | 100 | 100 | None | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-005 | 05 - Southwest | 22 | DIS-20-1 | Wind | 150 | 126 | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 ftlo 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | ER/NR | SPS | Conway 115 kV Line (524079) | DISIS STAGE
GEN-2020-009 | 05 - Southwest | 22 | DIS-20-1 | Solar | 300 | 300 | None | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | DISIS STAGE
GEN-2020-017 | 05 - Southwest | 22 | DIS-20-1 | Solar | 74.88 | 74.88 | None | ER/NR | SPS | 230kV Lamb County Interchange | DISIS STAGE
GEN-2020-059 | 05 - Southwest | 22 | DIS-20-1 | Solar | 500 | 435 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER/NR | SPS | Tuco-Yoakum-Hobbs 345 kV | DISIS STAGE
GEN-2020-060 | 05 - Southwest | 22 | DIS-20-1 | Storage | 200 | 174 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-062 | 05 - Southwest | 22 | DIS-20-1 | Solar | 256 | 223 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER | SPS | OASIS 230kV Substation | DISIS STAGE
GEN-2020-063 | 05 - Southwest | 22 | DIS-20-1 | Solar | 184 | 160 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER | SPS | San Juan Mesa 230 kV Line | DISIS STAGE
GEN-2020-065 | 05 - Southwest | 22 | DIS-20-1 | Thermal | 1002.99 | 0 | Non-Converged | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 - Southwest | 22 | DIS-20-1 | Wind | 352.5 | 307 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER/NR | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 - Southwest | 22 | DIS-20-1 | Solar | 400 | 348 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER/NR | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-080 | 05 - Southwest | 22 | DIS-20-1 | Storage | 200 | 174 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 ftlo P42:345:OKGE:SB_BAER7388:::: | ER/NR | SPS | Tuco Interchange 345 kV Substation | DISIS STAGE
GEN-2018-067 | 01 - North | 21 | DIS-18-2 | Wind | 255 |  |  | ER | BEPC | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 - North | 21 | DIS-18-2 | Wind | 125 |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV
GEN-2018-070 | 01 - North | 21 | DIS-18-2 | Wind | 18.31 |  |  | ER/NR | WAPA | Utica Junction 230 kV substation
GEN-2018-074 | 01 - North | 21 | DIS-18-2 | Wind | 78 |  |  | ER | WAPA | Denison 230kV Substation
GEN-2019-019 | 01 - North | 21 | DIS-19-1 | Thermal | 15.15 |  |  | ER/NR | BEPC | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 - North | 21 | DIS-19-1 | Wind | 110 |  |  | ER/NR | WAPA | WAPA-UGP Mingusville 230kV
GEN-2019-037 | 01 - North | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | BEPC | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-065 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 19.8 |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 303 |  |  | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 250 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-090 | 02 - Nebraska | 21 | DIS-18-2 | Storage | 125 |  |  | ER/NR | OPPD | Raun-Fort Calhoun 345kV Line | DISIS STAGE
GEN-2018-125 | 02 - Nebraska | 21 | DIS-18-2 | Wind | 231 |  |  | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 221.4 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-132 | 02 - Nebraska | 21 | DIS-18-2 | Solar | 201.6 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2019-009 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-029 | 02 - Nebraska | 21 | DIS-19-1 | Wind | 404 |  |  | ER/NR | NPPD | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-033 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 182 |  |  | ER/NR | BEPC | Sidney Keystone 345 kV line | DISIS STAGE
GEN-2019-039 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 174.5 |  |  | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 78 |  |  | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 50 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 - Nebraska | 21 | DIS-19-1 | Solar | 100 |  |  | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-063 | 03 - Central | 21 | DIS-18-2 | Solar | 57 |  |  | ER | EMDE | Sedalia Marshfield Springfield Nichols Street 69kV circuit | DISIS STAGE
GEN-2018-093 | 03 - Central | 21 | DIS-18-2 | Storage | 60 |  |  | ER | WERE | Gordan Evans 137kV Substation | DISIS STAGE
GEN-2018-108 | 03 - Central | 21 | DIS-18-2 | Storage | 95 |  |  | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-116 | 03 - Central | 21 | DIS-18-2 | Solar | 150 |  |  | ER/NR | SUNC | Frey Street 115kV bus
GEN-2018-121 | 03 - Central | 21 | DIS-18-2 | Storage | 50 |  |  | ER | KCPL | KC South-N. Raymore 161kV Line | DISIS STAGE
GEN-2018-128 | 03 - Central | 21 | DIS-18-2 | Wind | 200.22 |  |  | ER/NR | OGE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 - Central | 21 | DIS-19-1 | Wind | 25 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-014 | 03 - Central | 21 | DIS-19-1 | Solar | 125 |  |  | ER/NR | SUNC | Holcomb 115kV substation
GEN-2019-016 | 03 - Central | 21 | DIS-19-1 | Solar | 200 |  |  | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 - Central | 21 | DIS-19-1 | Thermal | 15.56 |  |  | ER/NR | MIDW | Saxman 115kV substation
GEN-2019-030 | 03 - Central | 21 | DIS-19-1 | Wind | 252 |  |  | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-035 | 03 - Central | 21 | DIS-19-1 | Solar | 80 |  |  | ER/NR | EMDE | Reeds Spring-Aurora 161kV Line | DISIS STAGE
GEN-2019-044 | 03 - Central | 21 | DIS-19-1 | Solar | 100 |  |  | ER | SUNC | North Fort Dodge 115kV Substation
GEN-2019-048 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER | AEPW | Duncan 69kV substation | DISIS STAGE
GEN-2019-051 | 03 - Central | 21 | DIS-19-1 | Storage | 40 |  |  | ER/NR | SUNC | Frey St 115kV bus
GEN-2019-053 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-054 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Great Bend- Circle 230kV line
GEN-2019-055 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Great Bend-Spearville 230kV line
GEN-2019-058 | 03 - Central | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-062 | 03 - Central | 21 | DIS-19-1 | Storage | 90 |  |  | ER | WERE | Pony Meadows - El Paso 161kV Line Break | DISIS STAGE
GEN-2019-063 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 - Central | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | SUNC | Great Bend - Circle 230kV line
GEN-2018-064 | 04 - Southeast | 21 | DIS-18-2 | Solar | 80 |  |  | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  | ER/NR | OGE | Ranch Road 345 kV
GEN-2018-072 | 04 - Southeast | 21 | DIS-18-2 | Storage | 151 |  |  | ER/NR | OGE | Ranch Road 345 kV
GEN-2018-079 | 04 - Southeast | 21 | DIS-18-2 | Solar | 148 |  |  | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 - Southeast | 21 | DIS-18-2 | Wind | 215 |  |  | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-087 | 04 - Southeast | 21 | DIS-18-2 | Storage | 75 |  |  | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-088 | 04 - Southeast | 21 | DIS-18-2 | Solar | 130 |  |  | ER | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2018-106 | 04 - Southeast | 21 | DIS-18-2 | Solar | 165 |  |  | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 - Southeast | 21 | DIS-18-2 | Solar | 250 |  |  | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2018-117 | 04 - Southeast | 21 | DIS-18-2 | Solar | 150 |  |  | ER/NR | AEPW | Sweetwater 230kV | DISIS STAGE
GEN-2019-002 | 04 - Southeast | 21 | DIS-19-1 | Storage | 100 |  |  | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 - Southeast | 21 | DIS-19-1 | Storage | 200 |  |  | ER/NR | OGE | Woodward 345kV substation
GEN-2019-013 | 04 - Southeast | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | AEPW | Dempsey 230kV sub/Sweetwater 230kV | DISIS STAGE
GEN-2019-045 | 04 - Southeast | 21 | DIS-19-1 | Solar | 155 |  |  | ER | OGE | DeGrasse 138kV Substation
GEN-2019-052 | 04 - Southeast | 21 | DIS-19-1 | Solar | 135 |  |  | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2019-065 | 04 - Southeast | 21 | DIS-19-1 | Storage | 180 |  |  | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2019-066 | 04 - Southeast | 21 | DIS-19-1 | Storage | 50 |  |  | ER/NR | AEPW | Sweetwater 230kV substation | DISIS STAGE
GEN-2019-067 | 04 - Southeast | 21 | DIS-19-1 | Storage | 30 |  |  | ER/NR | OKGE | Cimarron 345 kV Substation
GEN-2018-073 | 05 - Southwest | 21 | DIS-18-2 | Solar | 250 |  |  | ER | SPS | 345kV Crawfish Substation | DISIS STAGE
GEN-2018-081 | 05 - Southwest | 21 | DIS-18-2 | Solar | 175 |  |  | ER | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2018-089 | 05 - Southwest | 21 | DIS-18-2 | Wind | 196 |  |  | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-092 | 05 - Southwest | 21 | DIS-18-2 | Solar | 400 |  |  | ER | SPS | Oklaunion-Tuco 345kV Line Break | DISIS STAGE
GEN-2018-097 | 05 - Southwest | 21 | DIS-18-2 | Solar | 100 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 - Southwest | 21 | DIS-18-2 | Wind | 300 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2018-111 | 05 - Southwest | 21 | DIS-18-2 | Storage | 75 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-112 | 05 - Southwest | 21 | DIS-18-2 | Solar | 185 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2018-124 | 05 - Southwest | 21 | DIS-18-2 | Solar | 200 |  |  | ER | SPS | Tolk 230kV substation | DISIS STAGE
GEN-2019-003 | 05 - Southwest | 21 | DIS-19-1 | Solar | 150 |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-004 | 05 - Southwest | 21 | DIS-19-1 | Thermal | 71.732 |  |  | ER | SPS | Hobbs 230kV / 115kV Switchyard | DISIS STAGE
GEN-2019-011 | 05 - Southwest | 21 | DIS-19-1 | Storage | 230 |  |  | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 - Southwest | 21 | DIS-19-1 | Solar | 50 |  |  | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-056 | 05 - Southwest | 21 | DIS-19-1 | Storage | 100 |  |  | ER | SPS | Randall 115kV substation | DISIS STAGE
GEN-2019-074 | 05 - Southwest | 21 | DIS-19-1 | Storage | 100 |  |  | ER | SPS | Plant X 230kV Substation | DISIS STAGE
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 |  |  | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-007 | 01 - North | 20 | DIS-18-1 | Solar | 150 |  |  | ER/NR | WAPA | Summit 115kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 |  |  | ER/NR | WAPA | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Storage | 74.1 |  |  | ER/NR | WAPA | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 |  |  | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 |  |  | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
GEN-2018-044 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 |  |  | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 |  |  | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 |  |  | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-014 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER | KCPL | Holt County 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 |  |  | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Storage | 200 |  |  | ER | SPS | Lamar-Finney 345kV Substation
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Storage | 50 |  |  | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 |  |  | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-053 | 03 - Central | 20 | DIS-18-1 | Wind | 100 |  |  | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 |  |  | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-058 | 03 - Central | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-059 | 03 - Central | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-061 | 03 - Central | 20 | DIS-18-1 | Wind | 50 |  |  | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 |  |  | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 |  |  | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Storage | 74.1 |  |  | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 |  |  | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | AEPW | Tulsa Power Station 38kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Storage | 200 |  |  | ER | AEPW | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 |  |  | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 |  |  | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 |  |  | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 |  |  | ER | SPS | T14 Circuit 115kV line
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | SPS | Tuco-Oklaunion 345kV Line
GEN-2018-051 | 05 - Southwest | 20 | DIS-18-1 | Storage | 35 |  |  | ER | OKGE | Pecan Creek 345kV | DISIS STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Storage | 70 |  |  | ER | SPS | Roadrunner 115kV Substation
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1494 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | Chisago 115kV | NOT STARTED
J1495 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | North Rochester 161kV | NOT STARTED
J1498 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | XEL | Chanarambie 115 kV Substation | NOT STARTED
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | NOT STARTED
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV | NOT STARTED
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Rutland Substation 161kV | NOT STARTED
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | NOT STARTED
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | NOT STARTED
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Nobles County 345 kV Substation | NOT STARTED
J1582 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 160 |  |  | ER/NR | XEL | Pine Lake to Three Lakes 115 kV | NOT STARTED
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Bison 345kV | NOT STARTED
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Sherburne 345kV | NOT STARTED
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  | ER/NR | XEL | Langola 115kV Tap | NOT STARTED
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | XEL | Pipestone to Split Rock 115kV | NOT STARTED
J1622 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | OTP | Harvey-Underwood 230kV | NOT STARTED
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | XEL | Pine Lake to Apple River 161 kV | NOT STARTED
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | NOT STARTED
J1754 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER/NR | GRE | McHenry ND | NOT STARTED
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | NOT STARTED
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  | ER | DPC | Barron 161 kV | NOT STARTED
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  | ER | XEL | Cannon Falls Transmission 69 kV | NOT STARTED
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
MPC3600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | DISIS STAGE
MPC3700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | DISIS STAGE
MPC3800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line | DISIS STAGE
MPC3900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC4000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Square Butte 230 kV Substation
IR39 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 151.88 |  |  | ER/NR | ALTW | Dundee 161 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | NOT STARTED
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | NOT STARTED
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | NOT STARTED
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | NOT STARTED
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | NOT STARTED
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 97.5 |  |  | ER | AECI | Stroud 138kV
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 68 |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | NOT STARTED
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Driver 230kV | NOT STARTED
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | NOT STARTED
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | NOT STARTED
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | NOT STARTED
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | NOT STARTED
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325 |  |  | ER | EES | Solac - Chalkley 230kV | NOT STARTED
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | NOT STARTED
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | NOT STARTED
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | NOT STARTED
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | NOT STARTED
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | NOT STARTED
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | NOT STARTED
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | NOT STARTED
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 |  |  | ER | EES | 138 kV Grimes | NOT STARTED
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | NOT STARTED
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 |  |  | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | NOT STARTED
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EMI | J830 POI | NOT STARTED
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | NOT STARTED
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  | ER/NR | EES | Timberland 230kV | NOT STARTED
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | NOT STARTED
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | NOT STARTED
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  | ER/NR | EES | Bastrop tap point | NOT STARTED
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 126 |  |  | ER/NR | EES | Sabine 138/230 kV Substation | NOT STARTED
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | NOT STARTED
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-199 | 01 - North | 19 | DIS-17-2 | Storage | 202 |  |  | ER/NR | WAPA | Groton 345kV Substation | DISIS STAGE
GEN-2017-200 | 01 - North | 19 | DIS-17-2 | Wind | 302 |  |  | ER/NR | WAPA | Groton 345kV Substation | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-235 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-236 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | Logan 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | NPPD | Tekamah - Raun 161 kV Line
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 20 |  |  | ER | OPPD | Jones St. No 1201 69kV substation
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | Hoskins 345kV Substation
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 310 |  |  | ER | NPPD | McCool 345kV Substation
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding to North Loup 115kV
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-194 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | WERE | Tecumseh 230kV Substation | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | GRDA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar | 300 |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-225 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  | ER/NR | KCPL | Craig 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar | 210 |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-213 | 04 - Southeast | 19 | DIS-17-2 | Solar | 300 |  |  | ER | AEPW | Clarksville 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith-Plant X 230kV
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | Flatland 115 kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 57 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation | IA PENDING
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 447.3 |  |  | ER/NR | AECI | Morgan 345 kV
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | DISIS STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Philip Tap 230 kV | DISIS STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Neset 230 kV Substation | DISIS STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | DISIS STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | DISIS STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | DISIS STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | DISIS STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-060 | 03 - Central | 18 | DIS-17-1 | Wind | 149.4 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | DISIS STAGE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | DISIS STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  | ER | AEPW | Snyder - Cache 138 kV | DISIS STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | DISIS STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | WAPA | NELSON 7
J718 | 01 - North | 17.5 | DIS-17-1-PQ | Solar | 49.98 |  |  | ER/NR | XEL | Cherry Grove 69kV Substation
J748 | 02 - Nebraska | 17.5 | DIS-17-1-PQ | Wind | 200 |  |  | ER/NR | MEC | Highland - Raun 345kV Line Tap
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA PENDING
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA PENDING
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA PENDING
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA PENDING
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA PENDING
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3 | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-123 | 05 - Southwest | 17 | DIS-16-2 | Wind | 238.6 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV
GEN-2016-124 | 05 - Southwest | 17 | DIS-16-2 | Wind | 150 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 - Southwest | 17 | DIS-16-2 | Wind | 134.2 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 - North | 16.5 | DIS-16-2-PQ | Wind | 100 |  |  | ER/NR | XEL | NSP Rock County Substation
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
J476 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 246 |  |  | ER/NR | AMMO | Atchison County to Booneville 345 kV Line Tap
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 01 - North | 16 | DIS-16-1 | Wind | 250.24 |  |  | ER | BEPC | Fort Thompson-Leland Olds 345kV
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 300 |  |  | ER | NPPD | Hoskins 345kV
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 03 - Central | 16 | DIS-16-1 | CT | 10 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-022 | 04 - Southeast | 16 | DIS-16-1 | Wind | 151.8 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-041 | 05 - Southwest | 16 | DIS-16-1 | CT | 5 |  |  | ER | SPS | TUCO 345kV
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-069 | 03 - Central | 15 | DIS-15-2 | Wind | 5.23 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 - Central | 15 | DIS-15-2 | Wind | 11.74 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 - Southeast | 15 | DIS-15-2 | Wind | 2.17 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.505 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 - Southeast | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | WAPA | Hilken 230kV [Ecklund 230kV]
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | WAPA | Groton 115kV
GEN-2009-020AIS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | WAPA | Dickenson-Heskett 230kV
GEN-2010-001IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER/NR | WAPA | Bismarck-Glenham 230kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2014-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Gas | 11.72 |  |  | ER/NR | BEPC | Williston 115kV
MPC100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99 |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC1200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 49.5 |  |  | ER | OTP | Maple River 230 kV
MPC1300 | 01 - North | 14.5 | DIS-15-2-PQ | Coal | 493 |  |  | ER/NR | OTP | Square Butte 230 kV
MPC200 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 60 |  |  | ER | OTP | Langdon 115 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
MPC2100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 99.25 |  |  | ER | OTP | Center - Mandan 230 kV
MPC300 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  | ER | OTP | Langdon 115 kV
MPC500 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 327.9 |  |  | ER/NR | OTP | Maple River 230 kV
MPC500GRE | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 51 |  |  | ER/NR | GRE | Maple River 230 kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 16.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 - Central | 14 | DIS-15-1 | Wind | 200 |  |  | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 - Central | 14 | DIS-15-1 | Wind | 22.1 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 - Central | 14 | DIS-15-1 | Wind | 23.8 |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 - Southeast | 13 | DIS-14-2 | Wind | 1.06 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 - Southeast | 13 | DIS-14-2 | Wind | 1 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | DISIS STAGE
GEN-2014-013 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 0.11 |  |  | ER/NR | NPPD | Meadow Grove 230kV
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-016 | 05 - Southwest | 10 | DIS-13-1 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 - Central | 9 | DIS-12-2 | Wind | 1.8 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 - Southeast | 9 | DIS-12-2 | Wind | 0.72 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-037 | 05 - Southwest | 9 | DIS-12-2 | CT | 203 |  |  | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 - Nebraska | 8 | PQ | Wind | 15 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV
NPPDBUFFALOCOUNTYSOLAR | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBURTCOUNTYWIND | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 21.25 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-030 | 03 - Central | 8 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 - Central | 8 | PQ | CT | 50 |  |  | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 - Central | 8 | PQ | Wind | 3 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 - Central | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 - Southeast | 8 | PQ | Wind | 1.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 - Southwest | 8 | PQ | Wind | 120 |  |  | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 - Southwest | 8 | PQ | Wind | 78 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 - Southwest | 8 | PQ | Gas | 15.689 |  |  | ER | SPS | Hobbs 230kV & Hobbs 115kV
GEN-2006-044 | 05 - Southwest | 8 | PQ | Wind | 370 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 - Southeast | 7 | DIS-11-2 | Wind | 2 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-040 | 04 - Southeast | 5 | DIS-10-2 | Wind | 1.8 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-001 | 05 - Southwest | 5 | DIS-10-2 | Wind | 0.3 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 - Central | 4 | DIS-10-1 | Wind | 3.6 |  |  | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 - Central | 4 | DIS-10-1 | Wind | 199.5 |  |  | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 - Southwest | 4 | DIS-10-1 | Wind | 60.475 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 - Southwest | 4 | DIS-10-1 | Wind | 13.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-086N02 | 02 - Nebraska | 3 | DIS-09-1 | Wind | 0.4 |  |  | ER | NPPD | Meadow Grove 230kV
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 280 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 - Central | 3 | DIS-09-1 | CT | 682.2 |  |  | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 - Southwest | 3 | DIS-09-1 | Wind | 1 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 - Southeast | 2 | ICS1 | Wind | 0.3 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 - Southeast | 2 | ICS1 | Wind | 199 |  |  | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | ERIS | Non-Converge | Non-Converge | 24SP, 27SP, 27WP | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1 | [7 empty] | Hobbs to GEN-2020-065 230 kV Build Second Line
00ALL | ERIS | Thermal | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1 | 24SP, 27SP | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 2 |  | 606 | 16.62 | 120.18 |  |  |  | Hobbs to GEN-2020-065 230 kV Rebuild
00ALL | ERIS | Thermal | 646249 S1249 5 161 646254 S1254 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 298 | 42.26 | 114.97 |  |  |  | S1362 to S1363 161 kV Build Second Line
00ALL | ERIS | Thermal | 646254 S1254 5 161 646281 S1281 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 298 | 28.44 | 226.63 |  |  |  | S1362 to S1363 161 kV Build Second Line
00ALL | ERIS | Thermal | 646281 S1281 5 161 646363 S1363 5 161 1 | 24SP, 27SP, 27WP | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 298 | 0.07 | 164.72 |  |  |  | S1362 to S1363 161 kV Build Second Line
00ALL | ERIS | Thermal | 646362 S1362 5 161 646363 S1363 5 161 1 | 24SP, 27SP, 27WP | P12:161:OPPD:S1281-S1362:::HV: |  | 558 | 0.16 | 164.74 |  |  |  | S1362 to S1363 161 kV Build Second Line
00ALL | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
01ALL | ERIS | Thermal | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 | 24SP | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV: |  | 119 | 42.11 | 100.13 |  |  |  | East Fork 115 kV Terminal Equipment
01ALL | ERIS | Thermal | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 | 24SP | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV: |  | 119 | 42.11 | 100.13 |  |  |  | East Fork 345/115 kV Substation
01ALL | ERIS | Thermal | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 | 24SP | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV: |  | 119 | 42.11 | 100.13 |  |  |  | East Fork 345/115 kV Transformer
01ALL | ERIS | Thermal | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1 | 24SP, 27SP | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 264 | 48.17 | 104.54 |  |  |  | Whitlock to Oahe 230 kV New Line Build
01ALL | ERIS | Thermal | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 | 24SP, 27SP | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 264 | 52.22 | 108.48 |  |  |  | Whitlock to Oahe 230 kV New Line Build
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 | 24SP, 27SP, 27WP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 313 | 106.71 | 120.88 |  |  |  | Ft. Thompson 345/230 kV Install Third Transformer
01ALL | ERIS | Thermal | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 | 24SP, 27SP, 27WP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 313 | 109.02 | 123.5 |  |  |  | Ft. Thompson 345/230 kV Install Third Transformer
01ALL | ERIS | Thermal | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 24SP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 239 | 71.25 | 128.31 |  |  |  | Oahe 230 kV Terminal Upgrades (WAPA)
01ALL | ERIS | Thermal | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 24SP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 239 | 78.16 | 135.57 |  |  |  | Sully Buttes - Whitlock 230 kV Line Clearance Increase
01ALL | ERIS | Thermal | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 24SP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 239 | 78.16 | 135.57 |  |  |  | Whitlock 230 kV Terminal Upgrades
01ALL | ERIS | Thermal | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 24SP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: |  | 239 | 78.16 | 135.57 |  |  |  | Sully Buttes 230 kV Terminal Upgrades
01ALL | ERIS | Thermal | None | 27L | None | [7 empty] | None
01ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
02ALL | ERIS | Thermal | 530582 S HAYS6 230 539679 GRTBEND6 230 1 | 24SP, 27SP, 27WP | P23:345:ITCGP:SV_BRK382:::EHV: |  | 319 | 82.72 | 130.63 |  |  |  | Hays to Great Bend 230 kV Rebuild
02ALL | ERIS | Thermal | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 | 27WP | P23:345:ITCGP:SV_BRK382:::EHV: |  | 600 | 63.44 | 110.22 |  |  |  | Post Rock 345/230 kV Install Second Transformer
02ALL | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 27L, 27WP | P12:115:WERE:KNOB-NPPD-115:::HV: |  | 99 | 66.64 | 127.47 |  |  |  | Beatrice to Harbine 115 kV Rebuild
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 24SP, 27L, 27SP, 27WP | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 17.44 | 137.3 |  |  |  | Fairbury to Harbine 115 kV Rebuild
02ALL | ERIS | Thermal | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 24SP, 27L, 27SP, 27WP | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.76 | 149.96 |  |  |  | Fairbury to G20-077-TAP 115 kV Rebuild
02ALL | ERIS | Thermal | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 | 24SP, 27L, 27SP, 27WP | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.82 | 149.77 |  |  |  | N. Hebron to G20-077-TAP 115 kV Rebuild
02ALL | ERIS | Thermal | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 24SP, 27SP, 27WP | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.05 | 175.69 |  |  |  | Holdrege to G20-013-TAP 115 kV Rebuild
02ALL | ERIS | Thermal | 659210 SIDNEY__-MB4 230 996552 SDQ KV2A 230 1 | 24SP, 27SP, 27WP | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1 |  | 496 | 98.11 | 119.63 |  |  |  | Sidney 345/230 kV Transformer Replacement
02ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
03ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
03ALL | ERIS | Thermal | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 | 27WP | 547479 LAR382 5 161 547480 MON383 5 161 1 |  | 167 | 68.62 | 108.76 |  |  |  | Springfield to LA Russell 161 kV Build Second Line
03ALL | ERIS | Thermal | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: |  | 956 | 62.43 | 162.47 |  |  |  | Benton to G20-076-TAP 345 kV Rebuild
03ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1016 | 71.33 | 130.95 |  |  |  | Blackberry - Wolf Creek 345 kV
03ALL | ERIS | Thermal | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1016 | 71.33 | 130.95 |  |  |  | Wolf Creek 345kV Terminal Equipment
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 | 24SP, 27SP, 27WP | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1 |  | 189 | 77.09 | 113.41 |  |  |  | Marmaton 161 kV Bus-Tie Upgrade
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 24SP, 27SP | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1 |  | 281 | 72.41 | 110.69 |  |  |  | Marmaton to Dakota 161 kV Build Second Line
03ALL | ERIS | Thermal | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 24SP, 27SP | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1 |  | 281 | 72.41 | 110.69 |  |  |  | Marmaton 161 kV Terminal Equipment Upgrade
03ALL | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: |  | 717 | 80.84 | 113.18 |  |  |  | Pleasant Hill 345 kV Terminal Equiment Upgrade
03ALL | ERIS | Thermal | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1 | 24SP, 27SP | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1 |  | 74 | 49.05 | 108.57 |  |  |  | Warrensburg to Post Oak 69 kV Rebuild
03ALL | ERIS | Thermal | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1 | 24SP, 27SP | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1 |  | 74 | 48.82 | 108.59 |  |  |  | Post Oak to Clinton PLT2 69 kV Rebuild
03ALL | ERIS | Thermal | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 24SP, 27SP | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 334 | 82.41 | 122.93 |  |  |  | Craig to G20-057-TAP 345 kV Build Second Line
03ALL | ERIS | Thermal | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 | 24SP, 27SP | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: |  | 1195 | 61.02 | 109.04 |  |  |  | Craig to G20-057-TAP 345 kV Build Second Line
03ALL | ERIS | Thermal | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | 42.22 | 113.74 |  |  |  | Blackberry - Wolf Creek 345 kV
03ALL | ERIS | Thermal | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 1195 | 42.22 | 113.74 |  |  |  | Wolf Creek 345kV Terminal Equipment
03ALL | ERIS | Thermal | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 | 24SP, 27SP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 255 | 69.58 | 108.97 |  |  |  | Marmaton to Dakota 161 kV Build Second Line
03ALL | ERIS | Thermal | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 | 24SP, 27SP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 281 | 71.28 | 107.19 |  |  |  | Marmaton to Dakota 161 kV Build Second Line
03ALL | ERIS | Thermal | 543066 S.OTTWA5 161 543069 PAOLA 5 161 1 | 27SP | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 |  | 167 | 40.5 | 100.97 |  |  |  | Pleasant Valley to West Gardner 161 kV Build Second Line
03ALL | ERIS | Thermal | 543067 CENTENL5 161 543069 PAOLA 5 161 1 | 24SP, 27SP, 27WP | P12:161:WERE:MARM-KCPL-161:::HV: |  | 167 | 100.18 | 175.03 |  |  |  | Marmaton to Dakota 161 kV Build Second Line
03ALL | ERIS | Thermal | 543067 CENTENL5 161 543069 PAOLA 5 161 1 | 27SP | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1 |  | 167 | 35.64 | 122.39 |  |  |  | Pleasant Valley to West Gardner 161 kV Build Second Line
03ALL | ERIS | Thermal | 547479 LAR382 5 161 547480 MON383 5 161 1 | 27WP | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 223 | 67.4 | 103.46 |  |  |  | Springfield to LA Russell 161 kV Build Second Line
03ALL | ERIS | Voltage | None | 27L, 27SP, 27WP | None | [7 empty] | None
03ALL | ERIS | Voltage | WOLFCRK7 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  |  |  |  | 0.9476 | 0.985 | 1.03 | Blackberry - Wolf Creek 345 kV
03ALL | ERIS | Voltage | WOLFCRK7 | 24SP | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  |  |  |  | 0.9476 | 0.985 | 1.03 | Wolf Creek 345kV Terminal Equipment
04ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP, 27SP, 27WP | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT:::: |  | 970 | 91.16 | 111.93 |  |  |  | Welsh to Wilkes 345 kV Rebuild
04ALL | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 27WP | 510419 PRY-JCT4 138 764160 G20-092-TAP 138 1 |  | 188 | 87.41 | 119.38 |  |  |  | Catoosa to Catsag 138 kV Equipment Upgrade
04ALL | ERIS | Thermal | 511409 TREASILD7 345 515800 GRACMNT7 345 1 | 24SP, 27SP | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1541 | 39 | 110.95 |  |  |  | Treasild7 to Gracemont 345 kV Build Second Line
04ALL | ERIS | Thermal | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 | 27SP | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 1176 | 34.42 | 101.88 |  |  |  | Treasild7 to G20-075-Tap 345 kV Rebuild
04ALL | ERIS | Thermal | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 | 24SP, 27SP | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1176 | 10.05 | 102.84 |  |  |  | Treasild7 to Gracemont 345 kV Build Second Line
04ALL | ERIS | Thermal | 511467 L.E.S.-4 138 997967 LES 5 138 2 | 24SP, 27SP | P12:345:OKGE-AEPW:BKRBKR365:::: |  | 515 | 66.69 | 116.31 |  |  |  | Treasild7 to Gracemont 345 kV Build Second Line
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 | 24SP, 27SP, 27WP | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1301 | 76.54 | 132.57 |  |  |  | Sunnyside to G20-085-Tap 345 kV Build Second Line
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 | 24SP, 27SP | P12:345:OKGE-AEPW:BKRBKR365:::: |  | 1176 | 42.15 | 101.93 |  |  |  | Treasild7 to Gracemont 345 kV Build Second Line
04ALL | ERIS | Thermal | 511468 L.E.S.-7 345 997967 LES 5 138 2 | 24SP, 27SP | P12:345:OKGE-AEPW:BKRBKR365:::: |  | 515 | 66.18 | 116.15 |  |  |  | Treasild7 to Gracemont 345 kV Build Second Line
04ALL | ERIS | Thermal | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 | 24SP, 27SP | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1301 | 57.64 | 113.42 |  |  |  | Sunnyside to G20-085-Tap 345 kV Build Second Line
04ALL | ERIS | Thermal | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 | 24SP, 27SP, 27WP | P23:345:AEPW:PITTSBURG CB 3429A NBTB:::: |  | 478 | 88.36 | 124.48 |  |  |  | Build Johnston County 345 kV Second Transformer
04ALL | ERIS | Thermal | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 24SP, 27SP | SYSTEM INTACT | 194 |  | 75.81 | 111.44 |  |  |  | Sunnyside to Uniroyal 138 kV Rebuild
04ALL | ERIS | Thermal | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 | 24SP, 27SP, 27WP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1195 | 84.44 | 145.48 |  |  |  | Sunnyside to G20-085-Tap 345 kV Build Second Line
04ALL | ERIS | Thermal | 520814 ANADARK4 138 521129 CHERRYRD 4 138 1 | 27L | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 19.73 | 101.25 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 520926 GRANFLD2 69.0 997733 GRNDFLD 69.0 1 | 27L, 27SP, 27WP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 39.26 | 135.81 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 520926 GRANFLD2 69.0 997735 GRNDFLD 69.0 1 | 24SP, 27L, 27SP, 27WP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 36.89 | 115.45 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 | 24SP, 27L, 27SP | P12:138:WFEC:ANADRKO_CHRYRD:::: |  | 169 | 24.51 | 117.62 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 521106 GRNDFLD4 138 997733 GRNDFLD 69.0 1 | 27L, 27SP, 27WP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 39 | 132.99 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 521106 GRNDFLD4 138 997735 GRNDFLD 69.0 1 | 24SP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 56 | 28.59 | 103.84 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 | 24SP, 27L, 27SP | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 0.24 | 117.52 |  |  |  | Snyder to G20-016-Tap 138 kV Build Second Line
04ALL | ERIS | Thermal | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 | 24SP, 27SP, 27WP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1195 | 84.46 | 102.84 |  |  |  | Lawton Eastside to G17-171-Tap 345 kV Build Second Line
04ALL | ERIS | Thermal | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 | 24SP, 27SP, 27WP | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1195 | 84.45 | 102.84 |  |  |  | Lawton Eastside to G17-171-Tap 345 kV Build Second Line
04ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | ERIS | Non-Converge | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
05ALL | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 24SP, 27L, 27SP, 27WP | P42:345:OKGE:SB_BAER7314:::: |  | 439 | 119.76 | 130.3 |  |  |  | Sweetwater to Chisholm 230 kV Rebuild
05ALL | ERIS | Thermal | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 | 24SP, 27SP, 27WP | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 |  | 159 | 54 | 116.22 |  |  |  | Kirby to Conway 115 kV Rebuild
05ALL | ERIS | Thermal | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 | 24SP, 27SP | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1 |  | 319 | 51.92 | 104.3 |  |  |  | San Juan to Oasis 230 kV Rebuild
05ALL | ERIS | Thermal | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 24SP, 27SP | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 |  | 456 | 49.85 | 106.99 |  |  |  | Newhart to Plant X 230 kV Rebuild
05ALL | ERIS | Thermal | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | 27WP | P12:345:OKGE-SPS:BKRBKR430:::: |  | 997.3 | 23.31 | 105.51 |  |  |  | Tuco to GEN-2017-151 345 kV Rebuild
05ALL | ERIS | Thermal | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | 24SP, 27SP, 27WP | P12:345:OKGE-SPS:BKRBKR430:::: |  | 997.3 | 36.2 | 120.57 |  |  |  | GEN-2017-151 to GEN-2018-015 345 kV Rebuild
05ALL | ERIS | Thermal | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 | 24SP, 27SP, 27WP | P12:345:OKGE-SPS:BKRBKR430:::: |  | 997.3 | 38.03 | 122.94 |  |  |  | GEN-2018-015 to GEN-2018-092 345 kV Rebuild
05ALL | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
00NR | NRIS | Non-Converge | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | NRIS | Thermal | 505602 S BROWN4 138 521044 RUSSETT4 138 1 | 24SP | 515120 RUSSET-4 138 515147 GLASSES4 138 1 |  | 136 | 80.72 | 109.51 |  |  |  | Russett - South Brown 138 kV Ckt 1 Rebuild
00NR | NRIS | Thermal | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | 24SP, 27SP | P13:69-138:AEPW:DUNCAN-2:::: |  | 45 | 66.85 | 111.14 |  |  |  | Walters2 to Walters-2 69 kV Rebuild
00NR | NRIS | Thermal | 511435 SNYDER-4 138 997966 SNYDER 69.0 1 | 24SP, 27SP | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1 |  | 75 | 51.95 | 117.92 |  |  |  | Replace Snyder 138-69 kV Transformer
00NR | NRIS | Thermal | 515120 RUSSET-4 138 515147 GLASSES4 138 1 | 27SP | P12:138:OKGE:BKRBKR345:::: |  | 153 | 90.44 | 104.69 |  |  |  | Russett to Glasses 138 kV Rebuild
00NR | NRIS | Thermal | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 | 24SP, 27SP | P12:138:OKGE:BKRBKR257:::: |  | 222 | 63.02 | 108 |  |  |  | Uniroyal to Ardmore West 138 kV Rebuild
00NR | NRIS | Thermal | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 | 24SP | P12:138:OKGE:BKRBKR257:::: |  | 191 | 75.28 | 103.67 |  |  |  | Carter Tap to Chickasaw 138 kV Rebuild
00NR | NRIS | Thermal | 515138 CARTER 4 138 515372 ARDWEST4 138 1 | 24SP | P12:138:OKGE:BKRBKR257:::: |  | 222 | 57.88 | 102.96 |  |  |  | Carter Tap to Ardmore West 138 kV Rebuild
00NR | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7381:::: |  | 234 | 39.66 | 151.43 |  |  |  | Anadarko - Gracemont 138 kV Ckt 2 Rebuild
00NR | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7381:::: |  | 234 | 39.66 | 151.43 |  |  |  | Anadarko - Gracemont 138 kV Ckt 1 Rebuild
00NR | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7381:::: |  | 234 | 39.66 | 151.43 |  |  |  | Gracemont 138 kV Ckt 2 Terminal Equipment
00NR | NRIS | Thermal | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 | 24SP, 27SP | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 |  | 559 | 67.15 | 119.15 |  |  |  | Replace Tuco 345-230 kV Transformer #1
00NR | NRIS | Thermal | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 24SP, 27SP, 27WP | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 |  | 559 | 99.64 | 172.13 |  |  |  | Install Third Tuco 345-230 kV Transformer
00NR | NRIS | Thermal | 526161 CARLISLE 6 230 997613 SIEM 0136201 115 1 | 24SP, 27SP | 526161 CARLISLE 6 230 526525 WOLFFORTH 6 230 1 |  | 168 | 115.95 | 126.51 |  |  |  | Replace Carlisle 230-115 kV Transformer
00NR | NRIS | Thermal | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 | 24SP, 27SP | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1 |  | 547 | 74.35 | 114.15 |  |  |  | Yoakum to Ink Basin 230 kV Rebuild
00NR | NRIS | Thermal | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 | 24SP, 27SP | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1 |  | 641 | 44.54 | 102.98 |  |  |  | Install Third Yoakum 345-230 kV Transformer
00NR | NRIS | Thermal | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 | 24SP, 27SP, 27WP | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1 |  | 641 | 82.73 | 191.59 |  |  |  | Install Second Yoakum 345-230 kV Transformer
00NR | NRIS | Thermal | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 | 24SP | P42:345:SPS:KIOWA:J20####_SLG::EHV: |  | 607 | 59.45 | 116.32 |  |  |  | Crossroads-Hobbs-Roadrunner RFP
00NR | NRIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 251 | 54.96 | 100.88 |  |  |  | Litchfield to Asbury Plant 161 kV Rebuild (EDE)
00NR | NRIS | Thermal | 532932 LITCH 5 161 547476 ASB349 5 161 1 | 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 251 | 54.96 | 100.88 |  |  |  | Litchfield to Asbury Plant 161 kV Rebuild (KCPL)
00NR | NRIS | Thermal | 541340 BELTONS5 161 541342 PECULR 5 161 1 | 24SP, 27SP | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 281 | 93.11 | 101.98 |  |  |  | Belton to Peculiar 161 kV Rebuild
00NR | NRIS | Thermal | 542969 STILWEL5 161 542994 HICKMAN5 161 1 | 24SP, 27SP | 542969 STILWEL5 161 543053 REDEL 5 161 1 |  | 223 | 90.59 | 106.3 |  |  |  | Stilwell to Hickman 161 kV Terminal Equiment Upgrade
00NR | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 24SP, 27SP, 27WP | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 |  | 374 | 102.9 | 126.12 |  |  |  | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002)
00NR | NRIS | Thermal | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 | 24SP, 27SP, 27WP | 542978 CRAIG 5 161 543038 LENEXA 5 161 1 |  | 374 | 102.9 | 126.12 |  |  |  | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002)
00NR | NRIS | Thermal | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 | 24SP, 27SP, 27WP | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1 |  | 334 | 87.56 | 119.37 |  |  |  | Shawnee to Lenexa 161 kV Rebuild
00NR | NRIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 27WP | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 |  | 557 | 50.77 | 102.15 |  |  |  | Riverton to G20-079-TAP 161kV Rebuild
00NR | NRIS | Thermal | 661008 BEULAH 7 115 661011 BEULAH27 115 Z | 24SP, 27SP, 27WP | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1 |  | 149 | 150.85 | 161.14 |  |  |  | Beulah 115 kV Bus-Tie Upgrade
00NR | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
01NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | NRIS | Voltage | None | 27L | None | [7 empty] | None
02NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
02NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
02NR | NRIS | Voltage | None | 27L | None | [7 empty] | None
03NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
03NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
03NR | NRIS | Voltage | None | 27L | None | [7 empty] | None
04NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
04NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
04NR | NRIS | Voltage | None | 27L | None | [7 empty] | None
05NR | NRIS | Non-Converge | None | 27L | None | [7 empty] | None
05NR | NRIS | Thermal | None | 27L | None | [7 empty] | None
05NR | NRIS | Voltage | None | 27L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
GEN-2020-010 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 21.53% | 5750000 | 0.07787
GEN-2020-015 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 0.2588% | 5750000 | 0.00126
GEN-2020-016 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 6.276% | 5750000 | 0.01573
GEN-2020-074 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 3.883% | 5750000 | 0.00983
GEN-2020-075 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 12.87% | 5750000 | 0.03259
GEN-2020-085 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 9.362% | 5750000 | 0.00948
GEN-2020-087 | 04 - Southeast | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 32.18% | 5750000 | 0.03259
GEN-2020-009 | 05 - Southwest | 122577 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | Contingent | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | 0 | 13.63% | 5750000 | 0.02301
GEN-2020-010 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 21.53% | 1750000 | 0.07787
GEN-2020-015 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 0.2588% | 1750000 | 0.00126
GEN-2020-016 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 6.276% | 1750000 | 0.01573
GEN-2020-074 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 3.883% | 1750000 | 0.00983
GEN-2020-075 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 12.87% | 1750000 | 0.03259
GEN-2020-085 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 9.362% | 1750000 | 0.00948
GEN-2020-087 | 04 - Southeast | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 32.18% | 1750000 | 0.03259
GEN-2020-009 | 05 - Southwest | 122753 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | Contingent | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | 0 | 13.63% | 1750000 | 0.02301
ASGI-2020-001 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.02114% | 87298154 | 0.00125
ASGI-2020-002 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.06561% | 87298154 | 0.00388
ASGI-2020-003 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.05039% | 87298154 | 0.00298
GEN-2020-007 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 45.78% | 87298154 | 0.18743
GEN-2020-008 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 1.53% | 87298154 | 0.01629
GEN-2020-052 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 6.515% | 87298154 | 0.06908
GEN-2020-057 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 5.408% | 87298154 | 0.0339
GEN-2020-058 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 5.408% | 87298154 | 0.0339
GEN-2020-072 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.4165% | 87298154 | 0.00739
GEN-2020-073 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 1.776% | 87298154 | 0.02488
GEN-2020-076 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 7.275% | 87298154 | 0.0968
GEN-2020-079 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 4.808% | 87298154 | 0.05687
GEN-2020-082 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.1506% | 87298154 | 0.02004
GEN-2020-086 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 18.19% | 87298154 | 0.0968
GEN-2020-089 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 0.9074% | 87298154 | 0.02322
GEN-2020-090 | 03 - Central | 122598 | ERIS | Blackberry - Wolf Creek 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | 0 | 1.701% | 87298154 | 0.02216
GEN-2020-007 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | 0 | 23.21% | 2915107.52 | 0.02558
GEN-2020-057 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | 0 | 31.53% | 2915107.52 | 0.0532
GEN-2020-058 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | 0 | 31.53% | 2915107.52 | 0.0532
GEN-2020-073 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | 0 | 10.5% | 2915107.52 | 0.0396
GEN-2020-089 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | 0 | 3.236% | 2915107.52 | 0.02229
GEN-2020-007 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | 0 | 23.21% | 2915107.52 | 0.02707
GEN-2020-057 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | 0 | 31.53% | 2915107.52 | 0.05629
GEN-2020-058 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | 0 | 31.53% | 2915107.52 | 0.05629
GEN-2020-073 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | 0 | 10.5% | 2915107.52 | 0.0419
GEN-2020-089 | 03 - Central | 156461 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | Contingent | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | 0 | 3.236% | 2915107.52 | 0.02359
GEN-2020-008 | 03 - Central | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 2.884% | 395000000 | 0.00746
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 0.6124% | 395000000 | 0.00264
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 24.77% | 395000000 | 0.03204
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 35.31% | 395000000 | 0.06478
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 32.54% | 395000000 | 0.0526
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Crossroads-Hobbs-Roadrunner RFP | Contingent | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | 0 | 3.884% | 395000000 | 0.01256
GEN-2020-006 | 01 - North | 210663 | ERIS | East Fork 115 kV Terminal Equipment | Contingent | Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | 0 | 20.58% | 2511246 | 0.01546
GEN-2020-083 | 01 - North | 210663 | ERIS | East Fork 115 kV Terminal Equipment | Contingent | Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | 0 | 79.42% | 2511246 | 0.15064
GEN-2020-006 | 01 - North | 210675 | ERIS | East Fork 345/115 kV Substation | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 0 | 20.58% | 17766380 | 0.01546
GEN-2020-083 | 01 - North | 210675 | ERIS | East Fork 345/115 kV Substation | Contingent | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 0 | 79.42% | 17766380 | 0.15064
GEN-2020-006 | 01 - North | 210675 | ERIS | East Fork 345/115 kV Transformer | Contingent | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 0 | 20.58% | 5904650 | 0.01546
GEN-2020-083 | 01 - North | 210675 | ERIS | East Fork 345/115 kV Transformer | Contingent | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 0 | 79.42% | 5904650 | 0.15064
GEN-2020-010 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 21.53% | 1124593 | 0.07787
GEN-2020-015 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 0.2588% | 1124593 | 0.00126
GEN-2020-016 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 6.276% | 1124593 | 0.01573
GEN-2020-074 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 3.883% | 1124593 | 0.00983
GEN-2020-075 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 12.87% | 1124593 | 0.03259
GEN-2020-085 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 9.362% | 1124593 | 0.00948
GEN-2020-087 | 04 - Southeast | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 32.18% | 1124593 | 0.03259
GEN-2020-009 | 05 - Southwest | 122755 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | Contingent | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | 0 | 13.63% | 1124593 | 0.02301
GEN-2020-006 | 01 - North | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 0 | 6.053% | 561800 | 0.014
GEN-2020-021 | 01 - North | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 0 | 0.5812% | 561800 | 0.00143
GEN-2020-083 | 01 - North | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 0 | 4.03% | 561800 | 0.02354
GEN-2020-091 | 01 - North | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 0 | 6.231% | 561800 | 0.02402
GEN-2020-093 | 01 - North | 122734 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | Contingent | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | 0 | 83.1% | 561800 | 0.32036
GEN-2020-015 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 14.85% | 10267390.81 | 0.03086
GEN-2020-074 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 24.1% | 10267390.81 | 0.02604
GEN-2020-085 | 04 - Southeast | 112443 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | Contingent | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 0 | 61.04% | 10267390.81 | 0.02638
GEN-2020-006 | 01 - North | 143613 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 0 | 6.053% | 1744800 | 0.014
GEN-2020-021 | 01 - North | 143613 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 0 | 0.5812% | 1744800 | 0.00143
GEN-2020-083 | 01 - North | 143613 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 0 | 4.03% | 1744800 | 0.02354
GEN-2020-091 | 01 - North | 143613 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 0 | 6.231% | 1744800 | 0.02402
GEN-2020-093 | 01 - North | 143613 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 0 | 83.1% | 1744800 | 0.32036
GEN-2020-006 | 01 - North | 122735 | ERIS | Sully Buttes 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 0 | 6.053% | 587000 | 0.014
GEN-2020-021 | 01 - North | 122735 | ERIS | Sully Buttes 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 0 | 0.5812% | 587000 | 0.00143
GEN-2020-083 | 01 - North | 122735 | ERIS | Sully Buttes 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 0 | 4.03% | 587000 | 0.02354
GEN-2020-091 | 01 - North | 122735 | ERIS | Sully Buttes 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 0 | 6.231% | 587000 | 0.02402
GEN-2020-093 | 01 - North | 122735 | ERIS | Sully Buttes 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | 0 | 83.1% | 587000 | 0.32036
GEN-2020-005 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 20.1% | 33000000 | 0.26005
GEN-2020-017 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 3.497% | 33000000 | 0.09063
GEN-2020-059 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 19.64% | 33000000 | 0.07624
GEN-2020-060 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 7.345% | 33000000 | 0.07127
GEN-2020-062 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 12.14% | 33000000 | 0.09201
GEN-2020-063 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 8.479% | 33000000 | 0.08943
GEN-2020-067 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 10.2% | 33000000 | 0.05613
GEN-2020-068 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 13.35% | 33000000 | 0.06477
GEN-2020-080 | 05 - Southwest | TBD | ERIS | Sweetwater to Chisholm 230 kV Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | 0 | 5.256% | 33000000 | 0.051
GEN-2020-006 | 01 - North | 122733 | ERIS | Whitlock 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | 0 | 6.053% | 614000 | 0.014
GEN-2020-021 | 01 - North | 122733 | ERIS | Whitlock 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | 0 | 0.5812% | 614000 | 0.00143
GEN-2020-083 | 01 - North | 122733 | ERIS | Whitlock 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | 0 | 4.03% | 614000 | 0.02354
GEN-2020-091 | 01 - North | 122733 | ERIS | Whitlock 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | 0 | 6.231% | 614000 | 0.02402
GEN-2020-093 | 01 - North | 122733 | ERIS | Whitlock 230 kV Terminal Upgrades | Contingent | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | 0 | 83.1% | 614000 | 0.32036
ASGI-2020-001 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.02114% | 17884513 | 0.00125
ASGI-2020-002 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.06561% | 17884513 | 0.00388
ASGI-2020-003 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.05039% | 17884513 | 0.00298
GEN-2020-007 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 45.78% | 17884513 | 0.18743
GEN-2020-008 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 1.53% | 17884513 | 0.01629
GEN-2020-052 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 6.515% | 17884513 | 0.06908
GEN-2020-057 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 5.408% | 17884513 | 0.0339
GEN-2020-058 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 5.408% | 17884513 | 0.0339
GEN-2020-072 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.4165% | 17884513 | 0.00739
GEN-2020-073 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 1.776% | 17884513 | 0.02488
GEN-2020-076 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 7.275% | 17884513 | 0.0968
GEN-2020-079 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 4.808% | 17884513 | 0.05687
GEN-2020-082 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.1506% | 17884513 | 0.02004
GEN-2020-086 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 18.19% | 17884513 | 0.0968
GEN-2020-089 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 0.9074% | 17884513 | 0.02322
GEN-2020-090 | 03 - Central | 112509 | ERIS | Wolf Creek 345kV Terminal Equipment | Contingent | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | 0 | 1.701% | 17884513 | 0.02216
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Beatrice to Harbine 115 kV Rebuild | Current Study | Rebuild the Beatrice to Harbine 115 kV 14.08 mile line to a minimum rating of 139 MVA | 10008627.2 | 100% | 10008627.2 | 0.36753
GEN-2020-007 | 03 - Central | TBD | NRIS | Belton to Peculiar 161 kV Rebuild | Current Study | Rebuild the Belton to Peculiar 161 kV 4.15 mile line to a minumum of 291 MVA | 3247536.64 | 80% | 4059629.6 | 0.02333
GEN-2020-073 | 03 - Central | TBD | NRIS | Belton to Peculiar 161 kV Rebuild | Current Study | Rebuild the Belton to Peculiar 161 kV 4.15 mile line to a minumum of 291 MVA | 417878.4823 | 10.29% | 4059629.6 | 0.01027
GEN-2020-089 | 03 - Central | TBD | NRIS | Belton to Peculiar 161 kV Rebuild | Current Study | Rebuild the Belton to Peculiar 161 kV 4.15 mile line to a minumum of 291 MVA | 394214.4777 | 9.711% | 4059629.6 | 0.0177
ASGI-2020-001 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 55703.7036 | 0.2212% | 25177768 | 0.03648
ASGI-2020-002 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 60910.6562 | 0.2419% | 25177768 | 0.03989
ASGI-2020-003 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 52283.3008 | 0.2077% | 25177768 | 0.03424
GEN-2020-007 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 4216477.8668 | 16.75% | 25177768 | 0.19117
GEN-2020-052 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 385140.5776 | 1.53% | 25177768 | 0.04522
GEN-2020-057 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 638401.9053 | 2.536% | 25177768 | 0.04432
GEN-2020-058 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 638401.9053 | 2.536% | 25177768 | 0.04432
GEN-2020-072 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 196469.5688 | 0.7803% | 25177768 | 0.0386
GEN-2020-073 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 290381.344 | 1.153% | 25177768 | 0.04504
GEN-2020-076 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 5068507.6832 | 20.13% | 25177768 | 0.74685
GEN-2020-079 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 232938.5962 | 0.9252% | 25177768 | 0.03051
GEN-2020-086 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 12671269.208 | 50.33% | 25177768 | 0.74685
GEN-2020-088 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 163385.315 | 0.6489% | 25177768 | 0.0321
GEN-2020-089 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 142712.2372 | 0.5668% | 25177768 | 0.04044
GEN-2020-090 | 03 - Central | TBD | ERIS | Benton to G20-076-TAP 345 kV Rebuild | Current Study | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | 364784.1321 | 1.449% | 25177768 | 0.05262
GEN-2020-006 | 01 - North | TBD | NRIS | Beulah 115 kV Bus-Tie Upgrade | Current Study | Upgrade bus-tie equipment at Beulah 115 kV to a minimum rating of 241 MVA | 566485 | 100% | 566485 | 0.01537
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 2118896.2353 | 25.52% | 8302968 | 0.09573
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 444506.9691 | 5.354% | 8302968 | 0.01036
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 537824.2837 | 6.477% | 8302968 | 0.00848
GEN-2020-055 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 128139.3428 | 1.543% | 8302968 | 0.00848
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 1354010.2621 | 16.31% | 8302968 | 0.03181
GEN-2020-081 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 272845.199 | 3.286% | 8302968 | 0.00641
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Build Johnston County 345 kV Second Transformer | Current Study | Install a second 345/138 kV transformer at Johnston County | 3446745.7081 | 41.51% | 8302968 | 0.03239
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Carter Tap to Ardmore West 138 kV Rebuild | Current Study | Rebuild the Carter Tap to Ardmore West 138 kV 4.06 mile line to a minumum of 232 MVA | 1105528.4706 | 28.24% | 3914485.54 | 0.05511
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Carter Tap to Ardmore West 138 kV Rebuild | Current Study | Rebuild the Carter Tap to Ardmore West 138 kV 4.06 mile line to a minumum of 232 MVA | 2808957.0694 | 71.76% | 3914485.54 | 0.05601
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Carter Tap to Chickasaw 138 kV Rebuild | Current Study | Rebuild the Carter Tap to Chickasaw 138 kV mile 2.73 line to a minumum of 202 MVA | 743858.6379 | 28.26% | 2632154.07 | 0.02207
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Carter Tap to Chickasaw 138 kV Rebuild | Current Study | Rebuild the Carter Tap to Chickasaw 138 kV mile 2.73 line to a minumum of 202 MVA | 1888295.4321 | 71.74% | 2632154.07 | 0.02241
GEN-2020-092 | 04 - Southeast | TBD | ERIS | Catoosa to Catsag 138 kV Equipment Upgrade | Current Study | Upgrade terminal equipment at Catoosa for Catoosa to Catsag 138 kV line | 500000 | 100% | 500000 | 0.00671
GEN-2020-007 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 2043042.3242 | 12.63% | 16180630.05 | 0.05139
GEN-2020-052 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 434300.4987 | 2.684% | 16180630.05 | 0.02829
GEN-2020-057 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 5388203.2561 | 33.3% | 16180630.05 | 0.20753
GEN-2020-058 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 5388203.2561 | 33.3% | 16180630.05 | 0.20753
GEN-2020-071 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 290688.3445 | 1.797% | 16180630.05 | 0.01886
GEN-2020-073 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 310858.5212 | 1.921% | 16180630.05 | 0.02675
GEN-2020-076 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 352907.7555 | 2.181% | 16180630.05 | 0.02885
GEN-2020-079 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 318442.674 | 1.968% | 16180630.05 | 0.02314
GEN-2020-086 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 882269.3887 | 5.453% | 16180630.05 | 0.02885
GEN-2020-089 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 150562.5587 | 0.9305% | 16180630.05 | 0.02367
GEN-2020-090 | 03 - Central | TBD | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | Current Study | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | 621151.4725 | 3.839% | 16180630.05 | 0.04971
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Fairbury to G20-077-TAP 115 kV Rebuild | Current Study | Rebuild the Fairbury to G20-077-TAP 115 kV 10.83 mile line to a minimum rating of 157 MVA | 7698397.2 | 100% | 7698397.2 | 0.50486
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Fairbury to Harbine 115 kV Rebuild | Current Study | Rebuild the Fairbury to Harbine 115 kV 9.82 mile line to a minimum rating of 136 MVA | 6980448.8 | 100% | 6980448.8 | 0.50486
GEN-2020-006 | 01 - North | TBD | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | Current Study | Install a third 345/230 kV transformer at Ft. Thompson | 1870711.116 | 15.59% | 12000000 | 0.02969
GEN-2020-021 | 01 - North | TBD | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | Current Study | Install a third 345/230 kV transformer at Ft. Thompson | 5155173.2503 | 42.96% | 12000000 | 0.08704
GEN-2020-083 | 01 - North | TBD | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | Current Study | Install a third 345/230 kV transformer at Ft. Thompson | 386494.3353 | 3.221% | 12000000 | 0.01549
GEN-2020-091 | 01 - North | TBD | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | Current Study | Install a third 345/230 kV transformer at Ft. Thompson | 522463.3403 | 4.354% | 12000000 | 0.01382
GEN-2020-093 | 01 - North | TBD | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | Current Study | Install a third 345/230 kV transformer at Ft. Thompson | 4065157.9582 | 33.88% | 12000000 | 0.10753
GEN-2020-005 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 2142166.7766 | 2.431% | 88122188 | 0.11037
GEN-2020-017 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 2694788.2768 | 3.058% | 88122188 | 0.27813
GEN-2020-059 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 19597225.644 | 22.24% | 88122188 | 0.30291
GEN-2020-060 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 8073091.6931 | 9.161% | 88122188 | 0.31196
GEN-2020-062 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 9132789.7862 | 10.36% | 88122188 | 0.27571
GEN-2020-063 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 6670139.695 | 7.569% | 88122188 | 0.28016
GEN-2020-067 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 14149460.8768 | 16.06% | 88122188 | 0.31022
GEN-2020-068 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 16699985.6757 | 18.95% | 88122188 | 0.32266
GEN-2020-080 | 05 - Southwest | TBD | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | Current Study | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | 8962539.5758 | 10.17% | 88122188 | 0.34633
GEN-2020-005 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 645432.0678 | 2.431% | 26551100.8 | 0.11037
GEN-2020-017 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 811936.2081 | 3.058% | 26551100.8 | 0.27813
GEN-2020-059 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 5904618.6356 | 22.24% | 26551100.8 | 0.30291
GEN-2020-060 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 2432412.0426 | 9.161% | 26551100.8 | 0.31196
GEN-2020-062 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 2751697.7018 | 10.36% | 26551100.8 | 0.27571
GEN-2020-063 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 2009704.4276 | 7.569% | 26551100.8 | 0.28016
GEN-2020-067 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 4263214.1863 | 16.06% | 26551100.8 | 0.31022
GEN-2020-068 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 5031683.9958 | 18.95% | 26551100.8 | 0.32266
GEN-2020-080 | 05 - Southwest | TBD | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | Current Study | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | 2700401.5345 | 10.17% | 26551100.8 | 0.34633
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Hays to Great Bend 230 kV Rebuild | Current Study | Rebuild the Hays to Great Bemd 230 kV 39.2 mile line to a minimum rating of 489 MVA | 3481750.456 | 10.05% | 34633552.8 | 0.04015
GEN-2020-011 | 02 - Nebraska | TBD | ERIS | Hays to Great Bend 230 kV Rebuild | Current Study | Rebuild the Hays to Great Bemd 230 kV 39.2 mile line to a minimum rating of 489 MVA | 8995143.4943 | 25.97% | 34633552.8 | 0.06483
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Hays to Great Bend 230 kV Rebuild | Current Study | Rebuild the Hays to Great Bemd 230 kV 39.2 mile line to a minimum rating of 489 MVA | 5002317.1651 | 14.44% | 34633552.8 | 0.05366
GEN-2020-070 | 02 - Nebraska | TBD | ERIS | Hays to Great Bend 230 kV Rebuild | Current Study | Rebuild the Hays to Great Bemd 230 kV 39.2 mile line to a minimum rating of 489 MVA | 17154341.6846 | 49.53% | 34633552.8 | 0.15515
GEN-2020-065 | 05 - Southwest | TBD | ERIS | Hobbs to GEN-2020-065 230 kV Build Second Line | Current Study | Build a second 230 kV line from Hobbs to GEN-2020-065 (17.6 miles) | 20375273.6 | 100% | 20375273.6 | 0.45363
GEN-2020-065 | 05 - Southwest | TBD | ERIS | Hobbs to GEN-2020-065 230 kV Rebuild | Current Study | Rebuild the Hobbs to GEN-2020-065 230 kV 17.6 mile line to minimum rating of 760 MVA | 15549758.4 | 100% | 15549758.4 | 0.45363
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Holdrege to G20-013-TAP 115 kV Rebuild | Current Study | Rebuild the Holdrege to G20-013-TAP 115 kV 0.39 mile line to a minimum rating of 211 MVA | 277227.6 | 100% | 277227.6 | 0.9999
GEN-2020-008 | 03 - Central | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 298358.5244 | 3.162% | 9435938 | 0.01826
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 65488.5524 | 0.694% | 9435938 | 0.00668
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 3636836.8221 | 38.54% | 9435938 | 0.11129
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 2257556.0817 | 23.93% | 9435938 | 0.09799
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 2751042.0615 | 29.15% | 9435938 | 0.10523
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Install Second Yoakum 345-230 kV Transformer | Current Study | Install a second 345-230 kV transformer at Yoakum | 426655.9578 | 4.522% | 9435938 | 0.03264
GEN-2020-008 | 03 - Central | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 1096788.4213 | 11.62% | 9435938 | 0.08361
GEN-2020-075 | 04 - Southeast | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 118480.9595 | 1.256% | 9435938 | 0.01129
GEN-2020-087 | 04 - Southeast | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 296202.3987 | 3.139% | 9435938 | 0.01129
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 334113.1574 | 3.541% | 9435938 | 0.04245
GEN-2020-009 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 295782.6256 | 3.135% | 9435938 | 0.01879
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 984630.2942 | 10.43% | 9435938 | 0.03753
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 1925829.8134 | 20.41% | 9435938 | 0.10412
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 2266984.6646 | 24.03% | 9435938 | 0.10801
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Install Third Tuco 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Tuco | 2117125.6654 | 22.44% | 9435938 | 0.20174
GEN-2020-008 | 03 - Central | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 298358.5244 | 3.162% | 9435938 | 0.01826
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 65488.5524 | 0.694% | 9435938 | 0.00668
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 3636836.8221 | 38.54% | 9435938 | 0.11129
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 2257556.0817 | 23.93% | 9435938 | 0.09799
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 2751042.0615 | 29.15% | 9435938 | 0.10523
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Install Third Yoakum 345-230 kV Transformer | Current Study | Install a third 345-230 kV transformer at Yoakum | 426655.9578 | 4.522% | 9435938 | 0.03264
GEN-2020-005 | 05 - Southwest | TBD | ERIS | Kirby to Conway 115 kV Rebuild | Current Study | Rebuild the Kirby to Conway 115 kV 25.18 mile line to a minimum rating of 195 MVA | 17898951.2 | 100% | 17898951.2 | 0.39125
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Lawton Eastside to G17-171-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Lawton Eastside to G17-171-Tap (14.4 miles) | 21594168 | 100% | 21594168 | 0.21501
GEN-2020-073 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (EDE) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 5.24 mile line to a minumum of 254 MVA (EDE) | 769714.956 | 15.03% | 5121980.864 | 0.02912
GEN-2020-079 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (EDE) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 5.24 mile line to a minumum of 254 MVA (EDE) | 1030137.8724 | 20.11% | 5121980.864 | 0.03291
GEN-2020-088 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (EDE) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 5.24 mile line to a minumum of 254 MVA (EDE) | 157760.4034 | 3.08% | 5121980.864 | 0.00756
GEN-2020-089 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (EDE) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 5.24 mile line to a minumum of 254 MVA (EDE) | 3164367.6321 | 61.78% | 5121980.864 | 0.21871
GEN-2020-073 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (KCPL) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 1.56 mile line to a minumum of 254 MVA (KCPL) | 229914.857 | 15.03% | 1529942.336 | 0.02912
GEN-2020-079 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (KCPL) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 1.56 mile line to a minumum of 254 MVA (KCPL) | 307703.5203 | 20.11% | 1529942.336 | 0.03291
GEN-2020-088 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (KCPL) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 1.56 mile line to a minumum of 254 MVA (KCPL) | 47123.2374 | 3.08% | 1529942.336 | 0.00756
GEN-2020-089 | 03 - Central | TBD | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (KCPL) | Current Study | Rebuild the Litchfield to Asbury Plant 161 kV 1.56 mile line to a minumum of 254 MVA (KCPL) | 945200.7213 | 61.78% | 1529942.336 | 0.21871
GEN-2020-073 | 03 - Central | TBD | ERIS | Marmaton 161 kV Bus-Tie Upgrade | Current Study | Updated the Marmaton 161 kV Bus-Tie to a minimum rating of 228 MVA | 130897.4529 | 23.11% | 566485 | 0.07023
GEN-2020-089 | 03 - Central | TBD | ERIS | Marmaton 161 kV Bus-Tie Upgrade | Current Study | Updated the Marmaton 161 kV Bus-Tie to a minimum rating of 228 MVA | 435587.5471 | 76.89% | 566485 | 0.42696
GEN-2020-057 | 03 - Central | TBD | ERIS | Marmaton 161 kV Terminal Equipment Upgrade | Current Study | Install terminal equipment upgrade at Marmaton 161 kV to connect the second Marmaton to Dakota 161 kV line | 64170.5546 | 11.33% | 566485 | 0.01929
GEN-2020-058 | 03 - Central | TBD | ERIS | Marmaton 161 kV Terminal Equipment Upgrade | Current Study | Install terminal equipment upgrade at Marmaton 161 kV to connect the second Marmaton to Dakota 161 kV line | 64170.5546 | 11.33% | 566485 | 0.01929
GEN-2020-073 | 03 - Central | TBD | ERIS | Marmaton 161 kV Terminal Equipment Upgrade | Current Study | Install terminal equipment upgrade at Marmaton 161 kV to connect the second Marmaton to Dakota 161 kV line | 103854.1088 | 18.33% | 566485 | 0.06975
GEN-2020-089 | 03 - Central | TBD | ERIS | Marmaton 161 kV Terminal Equipment Upgrade | Current Study | Install terminal equipment upgrade at Marmaton 161 kV to connect the second Marmaton to Dakota 161 kV line | 334289.7821 | 59.01% | 566485 | 0.41017
GEN-2020-057 | 03 - Central | TBD | ERIS | Marmaton to Dakota 161 kV Build Second Line | Current Study | Build a second 161 kV 10.5 mile line from Marmaton to Dakota with a minimum rating of 281 MVA | 1308002.3178 | 11.33% | 11546786.5 | 0.01929
GEN-2020-058 | 03 - Central | TBD | ERIS | Marmaton to Dakota 161 kV Build Second Line | Current Study | Build a second 161 kV 10.5 mile line from Marmaton to Dakota with a minimum rating of 281 MVA | 1308002.3178 | 11.33% | 11546786.5 | 0.01929
GEN-2020-073 | 03 - Central | TBD | ERIS | Marmaton to Dakota 161 kV Build Second Line | Current Study | Build a second 161 kV 10.5 mile line from Marmaton to Dakota with a minimum rating of 281 MVA | 2116880.8016 | 18.33% | 11546786.5 | 0.06975
GEN-2020-089 | 03 - Central | TBD | ERIS | Marmaton to Dakota 161 kV Build Second Line | Current Study | Build a second 161 kV 10.5 mile line from Marmaton to Dakota with a minimum rating of 281 MVA | 6813901.0628 | 59.01% | 11546786.5 | 0.41017
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | N. Hebron to G20-077-TAP 115 kV Rebuild | Current Study | Rebuild the N. Hebron to G20-077-TAP 115 kV 11.27 mile line to a minimum rating of 149 MVA | 8011166.8 | 100% | 8011166.8 | 0.49514
GEN-2020-017 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 1816370.108 | 5.193% | 34978121.31 | 0.19412
GEN-2020-059 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 9305711.4435 | 26.6% | 34978121.31 | 0.14894
GEN-2020-060 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 1981353.0368 | 5.665% | 34978121.31 | 0.07928
GEN-2020-062 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 6077695.4746 | 17.38% | 34978121.31 | 0.18999
GEN-2020-063 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 4243954.2387 | 12.13% | 34978121.31 | 0.18458
GEN-2020-067 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 4791994.6643 | 13.7% | 34978121.31 | 0.10879
GEN-2020-068 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 5329759.695 | 15.24% | 34978121.31 | 0.10663
GEN-2020-080 | 05 - Southwest | TBD | ERIS | Newhart to Plant X 230 kV Rebuild | Current Study | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | 1431282.649 | 4.092% | 34978121.31 | 0.05727
GEN-2020-007 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 293159.6989 | 24.43% | 1200000 | 0.07855
GEN-2020-052 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 56652.5882 | 4.721% | 1200000 | 0.03931
GEN-2020-057 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 197476.1512 | 16.46% | 1200000 | 0.08102
GEN-2020-058 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 197476.1512 | 16.46% | 1200000 | 0.08102
GEN-2020-071 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 63867.1579 | 5.322% | 1200000 | 0.04414
GEN-2020-073 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 85758.2911 | 7.147% | 1200000 | 0.07861
GEN-2020-076 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 53340.9118 | 4.445% | 1200000 | 0.04645
GEN-2020-086 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 133352.2794 | 11.11% | 1200000 | 0.04645
GEN-2020-089 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 32299.4436 | 2.692% | 1200000 | 0.05409
GEN-2020-090 | 03 - Central | TBD | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | Current Study | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | 86617.3266 | 7.218% | 1200000 | 0.07384
GEN-2020-073 | 03 - Central | TBD | ERIS | Pleasant Valley to West Gardner 161 kV Build Second Line | Current Study | Build a second 161 kV 12.05 line from Pleasant Valley to West Gardner with a minimum of 351 MVA | 11566754.4551 | 91.79% | 12601203.15 | 0.39385
GEN-2020-089 | 03 - Central | TBD | ERIS | Pleasant Valley to West Gardner 161 kV Build Second Line | Current Study | Build a second 161 kV 12.05 line from Pleasant Valley to West Gardner with a minimum of 351 MVA | 1034448.6949 | 8.209% | 12601203.15 | 0.06435
ASGI-2020-002 | 03 - Central | TBD | ERIS | Post Oak to Clinton PLT2 69 kV Rebuild | Current Study | Rebuild the Post Oak to Clinton PLT2 69 kV 13.6 mile line to a minimum rating of 81 MVA | 12361706.4 | 100% | 12361706.4 | 0.52324
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 641238.4422 | 6.796% | 9435938 | 0.03493
GEN-2020-002 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 130780.1489 | 1.386% | 9435938 | 0.01759
GEN-2020-011 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 1787610.4937 | 18.94% | 9435938 | 0.06086
GEN-2020-013 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 976470.4832 | 10.35% | 9435938 | 0.04948
GEN-2020-027 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 78250.1821 | 0.8293% | 9435938 | 0.01705
GEN-2020-030 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 78250.1821 | 0.8293% | 9435938 | 0.01705
GEN-2020-033 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 78250.1821 | 0.8293% | 9435938 | 0.01705
GEN-2020-036 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 457786.9713 | 4.852% | 9435938 | 0.01646
GEN-2020-069 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 129765.6502 | 1.375% | 9435938 | 0.02675
GEN-2020-070 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 3639666.0934 | 38.57% | 9435938 | 0.1555
GEN-2020-077 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 311433.7053 | 3.301% | 9435938 | 0.02244
GEN-2020-078 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 156683.9423 | 1.661% | 9435938 | 0.01707
GEN-2020-084 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 558995.4356 | 5.924% | 9435938 | 0.0174
GEN-2020-094 | 02 - Nebraska | TBD | ERIS | Post Rock 345/230 kV Install Second Transformer | Current Study | Install a second 345/230 kV transformer at Post Rock | 410756.0877 | 4.353% | 9435938 | 0.0179
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Replace Carlisle 230-115 kV Transformer | Current Study | Replace the Carlisle 230-115 kV Transformer to a minimum of 211 MVA | 6621188 | 100% | 6621188 | 0.0106
GEN-2020-012 | 04 - Southeast | TBD | NRIS | Replace Snyder 138-69 kV Transformer | Current Study | Replace Snyder 138-69 kV Transformer to a minimum of 90 MVA | 117726.8668 | 3.763% | 3128743 | 0.00465
GEN-2020-016 | 04 - Southeast | TBD | NRIS | Replace Snyder 138-69 kV Transformer | Current Study | Replace Snyder 138-69 kV Transformer to a minimum of 90 MVA | 3011016.1332 | 96.24% | 3128743 | 0.06653
GEN-2020-008 | 03 - Central | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 1043679.8316 | 12.57% | 8302968 | 0.08361
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 317934.7603 | 3.829% | 8302968 | 0.04245
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 936952.6152 | 11.28% | 8302968 | 0.03753
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 1832577.4564 | 22.07% | 8302968 | 0.10412
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 2157212.9384 | 25.98% | 8302968 | 0.10801
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Replace Tuco 345-230 kV Transformer #1 | Current Study | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | 2014610.398 | 24.26% | 8302968 | 0.20174
GEN-2020-052 | 03 - Central | TBD | NRIS | Riverton to G20-079-TAP 161kV Rebuild | Current Study | Rebuild the Riverton to G20-079-TAP 161kV mile 5.47 line to a minumum of 570 MVA | 214304.2865 | 4.005% | 5350885.28 | 0.03621
GEN-2020-079 | 03 - Central | TBD | NRIS | Riverton to G20-079-TAP 161kV Rebuild | Current Study | Rebuild the Riverton to G20-079-TAP 161kV mile 5.47 line to a minumum of 570 MVA | 4497332.9742 | 84% | 5350885.28 | 0.8477
GEN-2020-088 | 03 - Central | TBD | NRIS | Riverton to G20-079-TAP 161kV Rebuild | Current Study | Rebuild the Riverton to G20-079-TAP 161kV mile 5.47 line to a minumum of 570 MVA | 462696.0007 | 8.673% | 5350885.28 | 0.13082
GEN-2020-090 | 03 - Central | TBD | NRIS | Riverton to G20-079-TAP 161kV Rebuild | Current Study | Rebuild the Riverton to G20-079-TAP 161kV mile 5.47 line to a minumum of 570 MVA | 176552.0186 | 3.299% | 5350885.28 | 0.03665
GEN-2020-015 | 04 - Southeast | TBD | NRIS | Russett to Glasses 138 kV Rebuild | Current Study | Rebuild the Russett to Glasses 138 kV mile 8.33 line to a minumum of 176 MVA | 8031444.47 | 100% | 8031444.47 | 0.01271
GEN-2020-025 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 1522639.9216 | 26.77% | 5688841.92 | 0.3652
GEN-2020-027 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 323965.9408 | 5.695% | 5688841.92 | 0.3652
GEN-2020-028 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 1522639.9216 | 26.77% | 5688841.92 | 0.3652
GEN-2020-030 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 323965.9408 | 5.695% | 5688841.92 | 0.3652
GEN-2020-031 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 1671664.2544 | 29.38% | 5688841.92 | 0.3652
GEN-2020-033 | 02 - Nebraska | TBD | ERIS | S1362 to S1363 161 kV Build Second Line | Current Study | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | 323965.9408 | 5.695% | 5688841.92 | 0.3652
GEN-2020-063 | 05 - Southwest | TBD | ERIS | San Juan to Oasis 230 kV Rebuild | Current Study | Rebuild the San Juan to Oasis 230 kV 46.2 mile line to a minimum rating of 335 MVA | 40818115.8 | 100% | 40818115.8 | 0.9999
GEN-2020-007 | 03 - Central | TBD | NRIS | Shawnee to Lenexa 161 kV Rebuild | Current Study | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | 907382.9891 | 23.72% | 3824855.84 | 0.04109
GEN-2020-057 | 03 - Central | TBD | NRIS | Shawnee to Lenexa 161 kV Rebuild | Current Study | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | 1190517.8393 | 31.13% | 3824855.84 | 0.08255
GEN-2020-058 | 03 - Central | TBD | NRIS | Shawnee to Lenexa 161 kV Rebuild | Current Study | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | 1190517.8393 | 31.13% | 3824855.84 | 0.08255
GEN-2020-089 | 03 - Central | TBD | NRIS | Shawnee to Lenexa 161 kV Rebuild | Current Study | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | 132355.5776 | 3.46% | 3824855.84 | 0.03746
GEN-2020-073 | 03 - Central | TBD | NRIS | Shawnee to Lenexa 161 kV Rebuild | Current Study | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | 404081.5947 | 10.56% | 3824855.84 | 0.0626
GEN-2020-001 | 02 - Nebraska | TBD | ERIS | Sidney 345/230 kV Transformer Replacement | Current Study | Replace the existing 345/230 kV transformer at Sidney to a minimum of 604 MVA | 8174940.7223 | 98.46% | 8302968 | 0.26744
GEN-2020-069 | 02 - Nebraska | TBD | ERIS | Sidney 345/230 kV Transformer Replacement | Current Study | Replace the existing 345/230 kV transformer at Sidney to a minimum of 604 MVA | 128027.2777 | 1.542% | 8302968 | 0.01585
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Snyder to G20-016-Tap 138 kV Build Second Line | Current Study | Build a second 138 kV line from Snyder to G20-016-Tap (14.61 miles) | 12176952.87 | 100% | 12176952.87 | 0.3087
GEN-2020-079 | 03 - Central | TBD | ERIS | Springfield to LA Russell 161 kV Build Second Line | Current Study | Build a second 161 kV 43.1 line from Springfield to LA Russell with a minimum rating of 189 MVA | 12444665.0802 | 27.61% | 45071523.3 | 0.05893
GEN-2020-088 | 03 - Central | TBD | ERIS | Springfield to LA Russell 161 kV Build Second Line | Current Study | Build a second 161 kV 43.1 line from Springfield to LA Russell with a minimum rating of 189 MVA | 32626858.2198 | 72.39% | 45071523.3 | 0.23175
GEN-2020-007 | 03 - Central | TBD | NRIS | Stilwell to Hickman 161 kV Terminal Equiment Upgrade | Current Study | Upgrade existing terminal equipment at Stilwell to Hickman 161 kV to 334 MVA | 180052.4778 | 60.02% | 300000 | 0.02445
GEN-2020-089 | 03 - Central | TBD | NRIS | Stilwell to Hickman 161 kV Terminal Equiment Upgrade | Current Study | Upgrade existing terminal equipment at Stilwell to Hickman 161 kV to 334 MVA | 44090.3965 | 14.7% | 300000 | 0.03742
GEN-2020-073 | 03 - Central | TBD | NRIS | Stilwell to Hickman 161 kV Terminal Equiment Upgrade | Current Study | Upgrade existing terminal equipment at Stilwell to Hickman 161 kV to 334 MVA | 75857.1257 | 25.29% | 300000 | 0.03524
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 490450.9755 | 2.774% | 17680225.05 | 0.07605
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 767215.5032 | 4.339% | 17680225.05 | 0.06655
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 3424051.0992 | 19.37% | 17680225.05 | 0.29998
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 1232398.1505 | 6.97% | 17680225.05 | 0.10797
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 8685113.9454 | 49.12% | 17680225.05 | 0.30436
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | Current Study | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | 3080995.3762 | 17.43% | 17680225.05 | 0.10797
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Sunnyside to Uniroyal 138 kV Rebuild | Current Study | Rebuild the Sunnyside to Uniroyal 138 kV mile 5.58 line to a minumum of 268 MVA | 1519724.962 | 28.25% | 5380007.22 | 0.05546
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Sunnyside to Uniroyal 138 kV Rebuild | Current Study | Rebuild the Sunnyside to Uniroyal 138 kV mile 5.58 line to a minumum of 268 MVA | 3860282.258 | 71.75% | 5380007.22 | 0.05635
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 317668.4559 | 2.279% | 13939327.92 | 0.14283
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 328414.4103 | 2.356% | 13939327.92 | 0.16044
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 564766.3595 | 4.052% | 13939327.92 | 0.14205
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 339180.7949 | 2.433% | 13939327.92 | 0.08548
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 414092.3216 | 2.971% | 13939327.92 | 0.0706
GEN-2020-055 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 98659.58 | 0.7078% | 13939327.92 | 0.0706
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 1028952.1449 | 7.382% | 13939327.92 | 0.26139
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 2323654.928 | 16.67% | 13939327.92 | 0.59029
GEN-2020-081 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 199893.6069 | 1.434% | 13939327.92 | 0.05078
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 2514907.998 | 18.04% | 13939327.92 | 0.25555
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | Current Study | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 5809137.32 | 41.67% | 13939327.92 | 0.59029
GEN-2020-012 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 503694.973 | 2.279% | 22104030.3 | 0.0733
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 520750.146 | 2.356% | 22104030.3 | 0.08234
GEN-2020-016 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 895496.9194 | 4.051% | 22104030.3 | 0.0729
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 537827.9408 | 2.433% | 22104030.3 | 0.04387
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 656734.2277 | 2.971% | 22104030.3 | 0.03624
GEN-2020-055 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 156470.2355 | 0.7079% | 22104030.3 | 0.03624
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 1631692.2232 | 7.382% | 22104030.3 | 0.13416
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 3684686.0164 | 16.67% | 22104030.3 | 0.30296
GEN-2020-081 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 316949.1602 | 1.434% | 22104030.3 | 0.02606
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 3988013.4168 | 18.04% | 22104030.3 | 0.13116
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | Current Study | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | 9211715.0409 | 41.67% | 22104030.3 | 0.30296
GEN-2020-005 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 723329.0414 | 2.431% | 29755544 | 0.11037
GEN-2020-067 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 4777740.0363 | 16.06% | 29755544 | 0.31022
GEN-2020-017 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 909928.509 | 3.058% | 29755544 | 0.27813
GEN-2020-059 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 6617245.0226 | 22.24% | 29755544 | 0.30291
GEN-2020-060 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 2725979.0133 | 9.161% | 29755544 | 0.31196
GEN-2020-062 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 3083799.1486 | 10.36% | 29755544 | 0.27571
GEN-2020-063 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 2252254.9619 | 7.569% | 29755544 | 0.28016
GEN-2020-068 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 5638956.2022 | 18.95% | 29755544 | 0.32266
GEN-2020-080 | 05 - Southwest | TBD | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | Current Study | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | 3026312.0646 | 10.17% | 29755544 | 0.34633
GEN-2020-074 | 04 - Southeast | TBD | NRIS | Uniroyal to Ardmore West 138 kV Rebuild | Current Study | Rebuild the Uniroyal to Ardmore West 138 kV mile 0.57 line to a minumum of 244 MVA | 155209.6621 | 28.24% | 549570.63 | 0.05511
GEN-2020-085 | 04 - Southeast | TBD | NRIS | Uniroyal to Ardmore West 138 kV Rebuild | Current Study | Rebuild the Uniroyal to Ardmore West 138 kV mile 0.57 line to a minumum of 244 MVA | 394360.9679 | 71.76% | 549570.63 | 0.05601
GEN-2020-012 | 04 - Southeast | TBD | NRIS | Walters2 to Walters-2 69 kV Rebuild | Current Study | Rebuild the Walters2 to Walters-2 69 kV mile 5.13 line to a minumum of 56 MVA | 1502993.7523 | 32.23% | 4662908.37 | 0.03038
GEN-2020-016 | 04 - Southeast | TBD | NRIS | Walters2 to Walters-2 69 kV Rebuild | Current Study | Rebuild the Walters2 to Walters-2 69 kV mile 5.13 line to a minumum of 56 MVA | 3159914.6177 | 67.77% | 4662908.37 | 0.03573
ASGI-2020-002 | 03 - Central | TBD | ERIS | Warrensburg to Post Oak 69 kV Rebuild | Current Study | Rebuild the Warrensburg to Post Oak 69 kV 13.7 mile line to a minimum rating of 81 MVA | 12452601.3 | 100% | 12452601.3 | 0.47676
GEN-2020-015 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 1277740.3572 | 3.645% | 35054319.72 | 0.0441
GEN-2020-020 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 5280016.307 | 15.06% | 35054319.72 | 0.09401
GEN-2020-054 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 11729179.5278 | 33.46% | 35054319.72 | 0.14128
GEN-2020-055 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 2794536.062 | 7.972% | 35054319.72 | 0.14128
GEN-2020-074 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 2408717.7588 | 6.871% | 35054319.72 | 0.04323
GEN-2020-075 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 1569594.7089 | 4.478% | 35054319.72 | 0.02817
GEN-2020-085 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 6070548.2262 | 17.32% | 35054319.72 | 0.04358
GEN-2020-087 | 04 - Southeast | TBD | ERIS | Welsh to Wilkes 345 kV Rebuild | Current Study | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | 3923986.7722 | 11.19% | 35054319.72 | 0.02817
GEN-2020-093 | 01 - North | TBD | ERIS | Whitlock to Oahe 230 kV New Line Build | Current Study | Build a new 40.38 mile 230 kV line from Whitlock to Oahe with a minimum rating of 264 MVA | 47880330.68 | 100% | 47880330.68 | 0.49189
GEN-2020-008 | 03 - Central | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 1653131.1276 | 10.82% | 15275870.61 | 0.03257
GEN-2020-005 | 05 - Southwest | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 965688.4505 | 6.322% | 15275870.61 | 0.03171
GEN-2020-059 | 05 - Southwest | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 1334889.4276 | 8.739% | 15275870.61 | 0.01315
GEN-2020-067 | 05 - Southwest | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 4575234.5384 | 29.95% | 15275870.61 | 0.06393
GEN-2020-068 | 05 - Southwest | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 5023650.7979 | 32.89% | 15275870.61 | 0.06186
GEN-2020-080 | 05 - Southwest | TBD | NRIS | Yoakum to Ink Basin 230 kV Rebuild | Current Study | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | 1723276.2679 | 11.28% | 15275870.61 | 0.04244
GEN-2020-017 | 05 - Southwest | 156875 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | 10594150 | 100% | 10594150 | 1
GEN-2020-017 | 05 - Southwest | 156876 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | 1017923 | 100% | 1017923 | 1
GEN-2020-064 | 03 - Central | 156877 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-064 | 03 - Central | 156878 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | 0 | 100% | 0 | 1
GEN-2020-002 | 02 - Nebraska | 143683 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 0 | 100% | 0 | 1
GEN-2020-002 | 02 - Nebraska | 143682 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | 2345838 | 100% | 2345838 | 1
GEN-2020-011 | 02 - Nebraska | 156881 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | 9300000 | 100% | 9300000 | 1
GEN-2020-011 | 02 - Nebraska | 156882 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | 700000 | 100% | 700000 | 1
GEN-2020-076 | 03 - Central | 156883 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-076 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-076 (200/Battery/Storage), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 1705963 | 100% | 1705963 | 1
GEN-2020-086 | 03 - Central | 156884 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-086 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-086 (500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 1705963 | 100% | 1705963 | 1
GEN-2020-076 | 03 - Central | 156885 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 11419939 | 50% | 22839878 | 1
GEN-2020-086 | 03 - Central | 156885 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | 11419939 | 50% | 22839878 | 1
GEN-2020-043 | 02 - Nebraska | 156390 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-043 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-044 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-045 | 02 - Nebraska | 156394 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 9139550 | 33.33% | 27418650 | 1
GEN-2020-044 | 02 - Nebraska | 156391 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-045 | 02 - Nebraska | 156392 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | 2292537 | 100% | 2292537 | 1
GEN-2020-006 | 01 - North | 156886 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | 2400062 | 100% | 2400062 | 1
GEN-2020-006 | 01 - North | 156887 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | 1140031 | 100% | 1140031 | 1
GEN-2020-075 | 04 - Southeast | 156888 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-075 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-075 (200/Battery/Storage), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 3000000 | 100% | 3000000 | 1
GEN-2020-087 | 04 - Southeast | 156889 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 3000000 | 100% | 3000000 | 1
GEN-2020-075 | 04 - Southeast | 156890 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 6000000 | 28.57% | 21000000 | 1
GEN-2020-087 | 04 - Southeast | 156890 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | 15000000 | 71.43% | 21000000 | 1
GEN-2020-069 | 02 - Nebraska | 156891 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | 11800000 | 100% | 11800000 | 1
GEN-2020-069 | 02 - Nebraska | 156892 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | 700000 | 100% | 700000 | 1
GEN-2020-005 | 05 - Southwest | 156893 | ERIS | Conway 115 kV Line (524079) GEN-2020-005 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-005 (150/Wind), into the Point of Interconnection (POI) at Conway 115 kV Line (524079) | 14515481 | 100% | 14515481 | 1
GEN-2020-005 | 05 - Southwest | 156894 | ERIS | Conway 115 kV Line (524079) GEN-2020-005 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-005 (150/Wind), into the Point of Interconnection (POI) at Conway 115 kV Line (524079) | 624130 | 100% | 624130 | 1
GEN-2020-008 | 03 - Central | 156895 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 1636674 | 100% | 1636674 | 1
GEN-2020-008 | 03 - Central | 156896 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | 2424709 | 100% | 2424709 | 1
GEN-2020-057 | 03 - Central | 156897 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 11428449 | 50% | 22856898 | 1
GEN-2020-058 | 03 - Central | 156897 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 11428449 | 50% | 22856898 | 1
GEN-2020-057 | 03 - Central | 156898 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 852982 | 50% | 1705964 | 1
GEN-2020-058 | 03 - Central | 156898 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | 852982 | 50% | 1705964 | 1
GEN-2020-089 | 03 - Central | 156899 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | 591562 | 100% | 591562 | 1
GEN-2020-089 | 03 - Central | 156900 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | 648515 | 100% | 648515 | 1
GEN-2020-003 | 03 - Central | 156901 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 1250000 | 100% | 1250000 | 1
GEN-2020-003 | 03 - Central | 156902 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | 30000 | 100% | 30000 | 1
GEN-2020-007 | 03 - Central | 156903 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 21420834 | 100% | 21420834 | 1
GEN-2020-007 | 03 - Central | 156904 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | 1705964 | 100% | 1705964 | 1
GEN-2020-083 | 01 - North | 156905 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 0 | 100% | 0 | 1
GEN-2020-083 | 01 - North | 156906 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | 0 | 100% | 0 | 1
GEN-2020-065 | 05 - Southwest | 156909 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 30437222 | 100% | 30437222 | 1
GEN-2020-065 | 05 - Southwest | 156910 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | 1532799 | 100% | 1532799 | 1
GEN-2020-022 | 03 - Central | 156911 | ERIS | Holcomb Substation 115KV GEN-2020-022 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-022 (125/Solar), into the Point of Interconnection (POI) at Holcomb Substation 115KV | 4500000 | 100% | 4500000 | 1
GEN-2020-022 | 03 - Central | 156912 | ERIS | Holcomb Substation 115KV GEN-2020-022 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-022 (125/Solar), into the Point of Interconnection (POI) at Holcomb Substation 115KV | 1500000 | 100% | 1500000 | 1
GEN-2020-015 | 04 - Southeast | 156913 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | 2000000 | 100% | 2000000 | 1
GEN-2020-015 | 04 - Southeast | 156914 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2020-088 | 03 - Central | 156915 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 2500000 | 100% | 2500000 | 1
GEN-2020-088 | 03 - Central | 156916 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | 2500000 | 100% | 2500000 | 1
GEN-2020-009 | 05 - Southwest | 156917 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | 17000000 | 100% | 17000000 | 1
GEN-2020-009 | 05 - Southwest | 156918 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | 3000000 | 100% | 3000000 | 1
GEN-2020-085 | 04 - Southeast | 156919 | ERIS | Lawton to Sunnyside 345 kV Line GEN-2020-085 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-085 (500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Line | 3000000 | 100% | 3000000 | 1
GEN-2020-074 | 04 - Southeast | 156920 | ERIS | Lawton to Sunnyside 345 kV Substation GEN-2020-074 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-074 (200/Battery/Storage), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | 3000000 | 100% | 3000000 | 1
GEN-2020-074 | 04 - Southeast | 156921 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | 10500000 | 50% | 21000000 | 1
GEN-2020-085 | 04 - Southeast | 156921 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | 10500000 | 50% | 21000000 | 1
GEN-2020-021 | 01 - North | 156922 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 21698256 | 100% | 21698256 | 1
GEN-2020-021 | 01 - North | 156923 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | 3279091 | 100% | 3279091 | 1
GEN-2020-082 | 03 - Central | 156924 | ERIS | Liberal 115 kV Substation GEN-2020-082 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-082 (20/Solar), into the Point of Interconnection (POI) at Liberal 115 kV Substation | 9000000 | 100% | 9000000 | 1
GEN-2020-082 | 03 - Central | 156925 | ERIS | Liberal 115 kV Substation GEN-2020-082 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-082 (20/Solar), into the Point of Interconnection (POI) at Liberal 115 kV Substation | 500000 | 100% | 500000 | 1
GEN-2020-014 | 01 - North | 144259 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-014 | 01 - North | 144258 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | 0 | 100% | 0 | 1
GEN-2020-060 | 05 - Southwest | 156926 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 9772056 | 100% | 9772056 | 1
GEN-2020-060 | 05 - Southwest | 156927 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | 1947926 | 100% | 1947926 | 1
GEN-2020-054 | 04 - Southeast | 156929 | ERIS | Lydia 345 kV Station GEN-2020-054, GEN-2020-055 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar) and GEN-2020-055 (71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | 750000 | 50% | 1500000 | 1
GEN-2020-055 | 04 - Southeast | 156929 | ERIS | Lydia 345 kV Station GEN-2020-054, GEN-2020-055 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar) and GEN-2020-055 (71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | 750000 | 50% | 1500000 | 1
GEN-2020-054 | 04 - Southeast | 156930 | ERIS | Lydia 345kV Station GEN-2020-054, GEN-2020-055 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, GEN-2020-055 (298/Solar and 71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | 1500000 | 50% | 3000000 | 1
GEN-2020-055 | 04 - Southeast | 156930 | ERIS | Lydia 345kV Station GEN-2020-054, GEN-2020-055 Interconnection (DISIS-2020-001) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, GEN-2020-055 (298/Solar and 71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | 1500000 | 50% | 3000000 | 1
GEN-2020-094 | 02 - Nebraska | 156931 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 7810696 | 100% | 7810696 | 1
GEN-2020-094 | 02 - Nebraska | 156932 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | 3905348 | 100% | 3905348 | 1
GEN-2020-052 | 03 - Central | 156933 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | 22839882 | 100% | 22839882 | 1
GEN-2020-052 | 03 - Central | 156934 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | 1705965 | 100% | 1705965 | 1
GEN-2020-077 | 02 - Nebraska | 156935 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | 11800000 | 100% | 11800000 | 1
GEN-2020-077 | 02 - Nebraska | 156936 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | 700000 | 100% | 700000 | 1
GEN-2020-062 | 05 - Southwest | 156937 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | 9895590 | 100% | 9895590 | 1
GEN-2020-062 | 05 - Southwest | 156938 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | 1852814 | 100% | 1852814 | 1
GEN-2020-013 | 02 - Nebraska | 156939 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | 11800000 | 100% | 11800000 | 1
GEN-2020-013 | 02 - Nebraska | 156940 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | 700000 | 100% | 700000 | 1
GEN-2020-091 | 01 - North | 156941 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 1733148 | 100% | 1733148 | 1
GEN-2020-091 | 01 - North | 156942 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | 2162065 | 100% | 2162065 | 1
GEN-2020-061 | 03 - Central | 156943 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 0 | 100% | 0 | 1
GEN-2020-061 | 03 - Central | 156944 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | 0 | 100% | 0 | 1
GEN-2020-070 | 02 - Nebraska | 156945 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (Non-shared NU) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | 15500000 | 100% | 15500000 | 1
GEN-2020-070 | 02 - Nebraska | 156946 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (TOIF) (ITCGP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | 950000 | 100% | 950000 | 1
GEN-2020-092 | 04 - Southeast | 156947 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 10000000 | 100% | 10000000 | 1
GEN-2020-092 | 04 - Southeast | 156948 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | 1500000 | 100% | 1500000 | 1
GEN-2020-084 | 02 - Nebraska | 156949 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | 0 | 100% | 0 | 1
GEN-2020-084 | 02 - Nebraska | 156950 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | 3905348 | 100% | 3905348 | 1
GEN-2020-079 | 03 - Central | 156951 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 8850000 | 100% | 8850000 | 1
GEN-2020-079 | 03 - Central | 156952 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | 8850000 | 100% | 8850000 | 1
GEN-2020-056 | 03 - Central | 144325 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 219182 | 100% | 219182 | 1
GEN-2020-056 | 03 - Central | 144324 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | 2352460 | 100% | 2352460 | 1
GEN-2020-063 | 05 - Southwest | 156956 | ERIS | San Juan Mesa 230 kV Line GEN-2020-063 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-063 (184/Solar), into the Point of Interconnection (POI) at San Juan Mesa 230 kV Line | 3488419 | 100% | 3488419 | 1
GEN-2020-063 | 05 - Southwest | 156957 | ERIS | San Juan Mesa 230 kV Line GEN-2020-063 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-063 (184/Solar), into the Point of Interconnection (POI) at San Juan Mesa 230 kV Line | 1211256 | 100% | 1211256 | 1
GEN-2020-073 | 03 - Central | 156958 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (Non-shared NU) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | 10619884 | 100% | 10619884 | 1
GEN-2020-073 | 03 - Central | 156959 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (TOIF) (KCPL) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | 842712 | 100% | 842712 | 1
GEN-2020-010 | 04 - Southeast | 156960 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 4900000 | 100% | 4900000 | 1
GEN-2020-010 | 04 - Southeast | 156961 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | 400000 | 100% | 400000 | 1
GEN-2020-001 | 02 - Nebraska | 156962 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | 4316195 | 100% | 4316195 | 1
GEN-2020-001 | 02 - Nebraska | 156963 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | 1643596 | 100% | 1643596 | 1
GEN-2020-016 | 04 - Southeast | 156964 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (Non-shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | 4900000 | 100% | 4900000 | 1
GEN-2020-016 | 04 - Southeast | 156965 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | 400000 | 100% | 400000 | 1
GEN-2020-012 | 04 - Southeast | 156966 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 10000000 | 100% | 10000000 | 1
GEN-2020-012 | 04 - Southeast | 156967 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | 1500000 | 100% | 1500000 | 1
GEN-2020-078 | 02 - Nebraska | 143685 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 9079099 | 100% | 9079099 | 1
GEN-2020-078 | 02 - Nebraska | 143684 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | 5539550 | 100% | 5539550 | 1
GEN-2020-025 | 02 - Nebraska | 156388 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-027 | 02 - Nebraska | 156955 | ERIS | Substation 1363; 161kV Substation GEN-2020-027, GEN-2020-030, and GEN-2020-033 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-027 (50/Hybrid), GEN-2020-030 (50/Hybrid), and GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 764179 | 33.33% | 2292537 | 1
GEN-2020-028 | 02 - Nebraska | 156389 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-030 | 02 - Nebraska | 156955 | ERIS | Substation 1363; 161kV Substation GEN-2020-027, GEN-2020-030, and GEN-2020-033 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-027 (50/Hybrid), GEN-2020-030 (50/Hybrid), and GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 764179 | 33.33% | 2292537 | 1
GEN-2020-031 | 02 - Nebraska | 156968 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (303/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | 2292537 | 100% | 2292537 | 1
GEN-2020-033 | 02 - Nebraska | 156955 | ERIS | Substation 1363; 161kV Substation GEN-2020-027, GEN-2020-030, and GEN-2020-033 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-027 (50/Hybrid), GEN-2020-030 (50/Hybrid), and GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 764179 | 33.33% | 2292537 | 1
GEN-2020-036 | 02 - Nebraska | 156969 | ERIS | Substation 3740; 345kV GEN-2020-036 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Hybrid), into the Point of Interconnection (POI) at Substation 3740; 345kV | 2949006 | 100% | 2949006 | 1
GEN-2020-036 | 02 - Nebraska | 156970 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 941366 | 50% | 1882732 | 1
GEN-2020-038 | 02 - Nebraska | 156970 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 941366 | 50% | 1882732 | 1
GEN-2020-038 | 02 - Nebraska | 156971 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | 2949006 | 100% | 2949006 | 1
GEN-2020-025 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 10990710.7175 | 26.77% | 41063166 | 1
GEN-2020-027 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2338449.0888 | 5.695% | 41063166 | 1
GEN-2020-028 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 10990710.7175 | 26.77% | 41063166 | 1
GEN-2020-030 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2338449.0888 | 5.695% | 41063166 | 1
GEN-2020-031 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 12066397.2984 | 29.38% | 41063166 | 1
GEN-2020-033 | 02 - Nebraska | 156393 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | 2338449.0888 | 5.695% | 41063166 | 1
GEN-2020-071 | 03 - Central | 156972 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | 22839880 | 100% | 22839880 | 1
GEN-2020-071 | 03 - Central | 156973 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | 1705965 | 100% | 1705965 | 1
GEN-2020-020 | 04 - Southeast | 156993 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 17000000 | 100% | 17000000 | 1
GEN-2020-020 | 04 - Southeast | 156974 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | 3000000 | 100% | 3000000 | 1
GEN-2020-081 | 04 - Southeast | 156975 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 4000000 | 100% | 4000000 | 1
GEN-2020-081 | 04 - Southeast | 156976 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | 3000000 | 100% | 3000000 | 1
GEN-2020-080 | 05 - Southwest | 156977 | ERIS | Tuco Interchange 345 kV Substation GEN-2020-080 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-080 (200/Battery/Storage), into the Point of Interconnection (POI) at Tuco Interchange 345 kV Substation | 8073719 | 100% | 8073719 | 1
GEN-2020-080 | 05 - Southwest | 156978 | ERIS | Tuco Interchange 345 kV Substation GEN-2020-080 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-080 (200/Battery/Storage), into the Point of Interconnection (POI) at Tuco Interchange 345 kV Substation | 8252153 | 100% | 8252153 | 1
GEN-2020-067 | 05 - Southwest | 156979 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 690867 | 100% | 690867 | 1
GEN-2020-067 | 05 - Southwest | 156980 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 1381735 | 50% | 2763470 | 1
GEN-2020-068 | 05 - Southwest | 156980 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 1381735 | 50% | 2763470 | 1
GEN-2020-068 | 05 - Southwest | 156981 | ERIS | Tuco to Yoakum 345kV line GEN-2020-068 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-068 (400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | 690867 | 100% | 690867 | 1
GEN-2020-059 | 05 - Southwest | 156982 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (Non-shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (500/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | 15573312 | 100% | 15573312 | 1
GEN-2020-059 | 05 - Southwest | 156983 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (500/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | 1381735 | 100% | 1381735 | 1
GEN-2020-093 | 01 - North | 156984 | ERIS | Whitlock Substation 230 kV GEN-2020-093 Interconnection (Non-shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-093 (150/Solar), into the Point of Interconnection (POI) at Whitlock Substation 230 kV | 14581959 | 100% | 14581959 | 1
GEN-2020-093 | 01 - North | 156985 | ERIS | Whitlock Substation 230 kV GEN-2020-093 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-093 (150/Solar), into the Point of Interconnection (POI) at Whitlock Substation 230 kV | 1364529 | 100% | 1364529 | 1
GEN-2020-072 | 03 - Central | 156986 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 10565920 | 100% | 10565920 | 1
GEN-2020-072 | 03 - Central | 156987 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | 842710 | 100% | 842710 | 1
GEN-2020-090 | 03 - Central | 156988 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 21420836 | 100% | 21420836 | 1
GEN-2020-090 | 03 - Central | 156989 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (WERE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | 1705965 | 100% | 1705965 | 1
GEN-2020-023 | 04 - Southeast | 156990 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (Non-shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | 4500000 | 100% | 4500000 | 1
GEN-2020-023 | 04 - Southeast | 156991 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | 1000000 | 100% | 1000000 | 1
1533069969.5

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Beatrice to Harbine 115 kV Rebuild | TBD | Rebuild the Beatrice to Harbine 115 kV 14.08 mile line to a minimum rating of 139 MVA | NPPD | 36 | 10008627.2
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (Non-shared NU) (BEPC) | 156886 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | BEPC | 24 | 2400062
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Bowman 230kV substation GEN-2020-006 Interconnection (TOIF) (BEPC) | 156887 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-006 (250/Solar), into the Point of Interconnection (POI) at Bowman 230kV substation | BEPC | 24 | 1140031
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | East Fork 115 kV Terminal Equipment | 144199 | Install 115 kV terminal equipment at MWEC’s East Fork 115 kV substation to accommodate a 115 kV tie line from the East Fork 345/115 kV substation. Construct a 115 kV tie line from the East Fork 115 kV substation to the proposed BEPC East Fork 345/115 kV substation. | MWE | 36 | 2511246
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | East Fork 345/115 kV Substation | 144171 | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | BEPC | 36 | 17766380
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | East Fork 345/115 kV Transformer | 144198 | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | BEPC | 36 | 5904650
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (Non-shared NU) (WAPA) | 156905 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Fairview 115kV Substation GEN-2020-083 Interconnection (TOIF) (WAPA) | 156906 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-083 (74.5/Solar), into the Point of Interconnection (POI) at Fairview 115kV Substation | WAPA | 0 | 0
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Belton to Peculiar 161 kV Rebuild | TBD | Rebuild the Belton to Peculiar 161 kV 4.15 mile line to a minumum of 291 MVA | KCPL | 36 | 4059629.6
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (Non-shared NU) (BEPC) | 156922 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 36 | 21698256
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | LeLand Olds-Chapelle Creek 345kV line GEN-2020-021 Interconnection (TOIF) (BEPC) | 156923 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-021 (235/Wind), into the Point of Interconnection (POI) at LeLand Olds-Chapelle Creek 345kV line | BEPC | 36 | 3279091
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (Non-shared NU) (BEPC) | 144259 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Lonesome Creek 115kV GEN-2020-014 Interconnection (TOIF) (BEPC) | 144258 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-014 (60.5/Thermal), into the Point of Interconnection (POI) at Lonesome Creek 115kV | BEPC | 0 | 0
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | Oahe 230 kV Terminal Upgrades (WAPA) | 122734 | Upgrade terminal equipment at Oahe 230 kV for the Oahe to Sully Buttes 230 kV line. Re-conductor three spans of line between Oahe 230 kV substation and Sully Buttes 230 kV substation.. | WAPA | 36 | 561800
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (Non-shared NU) (BEPC) | 156941 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 24 | 1733148
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Patent Gate Substation 345 kV GEN-2020-091 Interconnection (TOIF) (BEPC) | 156942 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-091 (150/Solar), into the Point of Interconnection (POI) at Patent Gate Substation 345 kV | BEPC | 24 | 2162065
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | Sully Buttes - Whitlock 230 kV Line Clearance Increase | 143613 | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | WAPA | 36 | 1744800
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | Sully Buttes 230 kV Terminal Upgrades | 122735 | Upgrade terminal equipment at Sully Buttes for Oahe - Sully Buttes - Whitlock 230 kV line | EREC | 36 | 587000
Contingent | Steady State | 01 - North | DISIS-2020-001 | ERIS | Whitlock 230 kV Terminal Upgrades | 122733 | Upgrade terminal equipment at Whitlock 230 kV for Oahe to Sully Buttes to Whitlock to Glenham 230 kV line. | BEPC | 36 | 614000
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Whitlock Substation 230 kV GEN-2020-093 Interconnection (Non-shared NU) (BEPC) | 156984 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-093 (150/Solar), into the Point of Interconnection (POI) at Whitlock Substation 230 kV | BEPC | 36 | 14581959
Interconnection | Steady State | 01 - North | DISIS-2020-001 | ERIS | Whitlock Substation 230 kV GEN-2020-093 Interconnection (TOIF) (BEPC) | 156985 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-093 (150/Solar), into the Point of Interconnection (POI) at Whitlock Substation 230 kV | BEPC | 36 | 1364529
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to G20-076-TAP 345 kV Rebuild | TBD | Rebuild Benton to G20-076-TAP 345 kV 22 mile line to a minimum rating of 1559 MVA | WERE | 36 | 25177768
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (Non-shared NU) (OPPD) | 143683 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | 6846 Substation 69 kV GEN-2020-002 Interconnection (TOIF) (OPPD) | 143682 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-002 (81/Solar), into the Point of Interconnection (POI) at 6846 Substation 69 kV | OPPD | 18 | 2345838
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (Non-shared NU) (NPPD) | 156881 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | NPPD | 36 | 9300000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Axtell-Sweetwater Substation 345kV GEN-2020-011 Interconnection (TOIF) (NPPD) | 156882 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-011 (320/Hybrid), into the Point of Interconnection (POI) at Axtell-Sweetwater Substation 345kV | NPPD | 36 | 700000
Current Study | Steady State | 01 - North | DISIS-2020-001 | NRIS | Beulah 115 kV Bus-Tie Upgrade | TBD | Upgrade bus-tie equipment at Beulah 115 kV to a minimum rating of 241 MVA | WAPA | 36 | 566485
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043 Interconnection (TOIF) (OPPD) | 156390 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-043 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-043, GEN-2020-044, GEN-2020-045 Interconnection (DISIS-2020-001) (OPPD) | 156394 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-043, GEN-2020-044, GEN-2020-045 (Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 36 | 27418650
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-044 Interconnection (TOIF) (OPPD) | 156391 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-044 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Between Substation 1209 and 1252; 161kV GEN-2020-045 Interconnection (TOIF) (OPPD) | 156392 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-045 (56.52/Thermal), into the Point of Interconnection (POI) at Between Substation 1209 and 1252; 161kV | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (Non-shared NU) (NPPD) | 156891 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | NPPD | 36 | 11800000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Cody to Valentine 115kV line GEN-2020-069 Interconnection (TOIF) (NPPD) | 156892 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-069 (52.85/Wind), into the Point of Interconnection (POI) at Cody to Valentine 115kV line | NPPD | 36 | 700000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Build Johnston County 345 kV Second Transformer | TBD | Install a second 345/138 kV transformer at Johnston County | SPS | 36 | 8302968
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Carter Tap to Ardmore West 138 kV Rebuild | TBD | Rebuild the Carter Tap to Ardmore West 138 kV 4.06 mile line to a minumum of 232 MVA | OGE | 36 | 3914485.54
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Carter Tap to Chickasaw 138 kV Rebuild | TBD | Rebuild the Carter Tap to Chickasaw 138 kV mile 2.73 line to a minumum of 202 MVA | OGE | 36 | 2632154.07
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Catoosa to Catsag 138 kV Equipment Upgrade | TBD | Upgrade terminal equipment at Catoosa for Catoosa to Catsag 138 kV line | SPS | 36 | 500000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Craig to G20-057-TAP 345 kV Build Second Line | TBD | Build a second 345 kV10.79 mile line from Craig to G20-057-TA with a minimum rating of 1195 MVA | KCPL | 36 | 16180630.05
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (Non-shared NU) (OPPD) | 156931 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 36 | 7810696
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Neb. City - 103rd & Rokeby 345 kV GEN-2020-094 Interconnection (TOIF) (OPPD) | 156932 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-094 (250/Solar), into the Point of Interconnection (POI) at Neb. City - 103rd & Rokeby 345 kV | OPPD | 36 | 3905348
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (Non-shared NU) (NPPD) | 156935 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | NPPD | 36 | 11800000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | North Hebron to Fairbury 115 kV GEN-2020-077 Interconnection (TOIF) (NPPD) | 156936 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-077 (151.2/Wind), into the Point of Interconnection (POI) at North Hebron to Fairbury 115 kV | NPPD | 36 | 700000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (Non-shared NU) (NPPD) | 156939 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | NPPD | 36 | 11800000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Orleans-Holdrege Substation 115kV GEN-2020-013 Interconnection (TOIF) (NPPD) | 156940 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-013 (215/Hybrid), into the Point of Interconnection (POI) at Orleans-Holdrege Substation 115kV | NPPD | 36 | 700000
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Fairbury to G20-077-TAP 115 kV Rebuild | TBD | Rebuild the Fairbury to G20-077-TAP 115 kV 10.83 mile line to a minimum rating of 157 MVA | NPPD | 36 | 7698397.2
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (Non-shared NU) (ITCGP) | 156945 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | ITCGP | 36 | 15500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Postrock to Axtell 345 KV line GEN-2020-070 Interconnection (TOIF) (ITCGP) | 156946 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-070 (255/Wind), into the Point of Interconnection (POI) at Postrock to Axtell 345 KV line | ITCGP | 36 | 950000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (Non-shared NU) (OPPD) | 156949 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Raun - Fort Calhoun 345 kV GEN-2020-084 Interconnection (TOIF) (OPPD) | 156950 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-084 (350/Solar), into the Point of Interconnection (POI) at Raun - Fort Calhoun 345 kV | OPPD | 36 | 3905348
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Fairbury to Harbine 115 kV Rebuild | TBD | Rebuild the Fairbury to Harbine 115 kV 9.82 mile line to a minimum rating of 136 MVA | NPPD | 36 | 6980448.8
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (Non-shared NU) (BEPC) | 156962 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | BEPC | 24 | 4316195
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Sidney 345 kV Substation GEN-2020-001 Interconnection (TOIF) (BEPC) | 156963 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-001 (200/Solar), into the Point of Interconnection (POI) at Sidney 345 kV Substation | BEPC | 24 | 1643596
Current Study | Steady State | 01 - North | DISIS-2020-001 | ERIS | Ft. Thompson 345/230 kV Install Third Transformer | TBD | Install a third 345/230 kV transformer at Ft. Thompson | WAPA | 36 | 12000000
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (Non-shared NU) (OPPD) | 143685 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 36 | 9079099
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1226 to Substation 1237, 161kV Tap GEN-2020-078 Interconnection (TOIF) (OPPD) | 143684 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-078 (100/Solar), into the Point of Interconnection (POI) at Substation 1226 to Substation 1237, 161kV Tap | OPPD | 36 | 5539550
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-025 Interconnection (TOIF) (OPPD) | 156388 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-028 Interconnection (TOIF) (OPPD) | 156389 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-028 (255/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-031 Interconnection (TOIF) (OPPD) | 156968 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-031 (303/Thermal), into the Point of Interconnection (POI) at Substation 1363; 161kV Substation | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 1363; 161kV Substation GEN-2020-027, GEN-2020-030, and GEN-2020-033 Interconnection (TOIF) (OPPD) | 156955 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facilities, GEN-2020-027 (50/Hybrid), GEN-2020-030 (50/Hybrid), and GEN-2020-033 (50/Hybrid), into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 36 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-036 Interconnection (TOIF) (OPPD) | 156969 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Hybrid), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 2949006
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-036, GEN-2020-038 Interconnection (DISIS-2020-001) (OPPD) | 156970 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-036, GEN-2020-038 (303/Hybrid and 303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 24 | 1882732
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation 3740; 345kV GEN-2020-038 Interconnection (TOIF) (OPPD) | 156971 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-038 (303/Thermal), into the Point of Interconnection (POI) at Substation 3740; 345kV | OPPD | 36 | 2949006
Interconnection | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Substation S1363 GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033 Interconnection (DISIS-2020-001) (OPPD) | 156393 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-025, GEN-2020-027, GEN-2020-028, GEN-2020-030, GEN-2020-031, GEN-2020-033, into the Point of Interconnection (POI) at S1281-S1362 161kV (S1363) | OPPD | 36 | 41063166
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (Non-shared NU) (EDE) | 156877 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EDE | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | 4544 Stateline CC 161kV Substation GEN-2020-064 Interconnection (TOIF) (EDE) | 156878 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-064 (64/Thermal), into the Point of Interconnection (POI) at 4544 Stateline CC 161kV Substation | EDE | 0 | 0
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | GEN-2017-151 to GEN-2018-015 345 kV Rebuild | TBD | Rebuild the GEN-2017-151 to GEN-2018-015 345 kV 77 mile line to a minimum rating of 1220 MVA | SPS | 36 | 88122188
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | GEN-2018-015 to GEN-2018-092 345 kV Rebuild | TBD | Rebuild the GEN-2018-015 to GEN-2018-092 345 kV 23.2 mile line ro a minimum rating of 1240 MVA | SPS | 36 | 26551100.8
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-076 Interconnection (TOIF) (WERE) | 156883 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-076 (200/Battery/Storage), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36 | 1705963
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345 kV Line GEN-2020-086 Interconnection (TOIF) (WERE) | 156884 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-086 (500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36 | 1705963
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Benton to Wolf Creek 345kV Line GEN-2020-076, GEN-2020-086 Interconnection (DISIS-2020-001) (WERE) | 156885 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-076, GEN-2020-086 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Benton to Wolf Creek 345 kV Line | WERE | 36 | 22839878
Contingent | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Blackberry - Wolf Creek 345 kV | 122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | NEET | 36 | 87298154
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (Non-shared NU) (SPS) | 156895 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 36 | 1636674
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Corporation Carpenter 345kV Substation GEN-2020-008 Interconnection (TOIF) (SPS) | 156896 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-008 (250/Hybrid), into the Point of Interconnection (POI) at Corporation Carpenter 345kV Substation | SPS | 36 | 2424709
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Hays to Great Bend 230 kV Rebuild | TBD | Rebuild the Hays to Great Bemd 230 kV 39.2 mile line to a minimum rating of 489 MVA | MIDW | 36 | 34633552.8
Contingent | Steady State | 03 - Central | DISIS-2017-002 | NRIS | Craig to Lenexa 161 kV Ckt 1 Rebuild (DISIS-2017-002) | 156461 | Rebuild the Craig to Lenexa 161 kV Ckt 1 2.95 mile line | KCPL | 36 | 2915107.52
Contingent | Steady State | 03 - Central | DISIS-2017-002 | NRIS | Craig to Lenexa 161 kV Ckt 2 Rebuild (DISIS-2017-002) | 156461 | Rebuild the Craig to Lenexa 161 kV Ckt 2 2.95 mile line | KCPL | 36 | 2915107.52
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (Non-shared NU) (KCPL) | 156897 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | KCPL | 36 | 22856898
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Craig-West Gardner 345 kV GEN-2020-057 and GEN-2020-058 Interconnection (TOIF) (KCPL) | 156898 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-057 (424.5/Solar) and GEN-2020-058 (424.5/Solar), into the Point of Interconnection (POI) at Craig-West Gardner 345 kV | KCPL | 36 | 1705964
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (Non-shared NU) (WERE) | 156899 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | WERE | 36 | 591562
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Dakota 161 kV Substation GEN-2020-089 Interconnection (TOIF) (WERE) | 156900 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-089 (104/Solar), into the Point of Interconnection (POI) at Dakota 161 kV Substation | WERE | 36 | 648515
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (Non-shared NU) (KPP) | 156901 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 24 | 1250000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | East Substation 69 kV GEN-2020-003 Interconnection (TOIF) (KPP) | 156902 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-003 (58/Thermal), into the Point of Interconnection (POI) at East Substation 69 kV | KPP | 24 | 30000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (Non-shared NU) (KCPL) | 156903 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 36 | 21420834
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Evergy La Cygne to Wolf Creek 345kV Substation GEN-2020-007 Interconnection (TOIF) (KCPL) | 156904 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-007 (650/Hybrid), into the Point of Interconnection (POI) at Evergy La Cygne to Wolf Creek 345kV Substation | KCPL | 36 | 1705964
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Holcomb Substation 115KV GEN-2020-022 Interconnection (Non-shared NU) (SUNC) | 156911 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-022 (125/Solar), into the Point of Interconnection (POI) at Holcomb Substation 115KV | SUNC | 30 | 4500000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Holcomb Substation 115KV GEN-2020-022 Interconnection (TOIF) (SUNC) | 156912 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-022 (125/Solar), into the Point of Interconnection (POI) at Holcomb Substation 115KV | SUNC | 30 | 1500000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (Non-shared NU) (EDE) | 156915 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EDE | 36 | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | La Russell 161 kV Substation GEN-2020-088 Interconnection (TOIF) (EDE) | 156916 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-088 (150/Solar), into the Point of Interconnection (POI) at La Russell 161 kV Substation | EDE | 36 | 2500000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Liberal 115 kV Substation GEN-2020-082 Interconnection (Non-shared NU) (SUNC) | 156924 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-082 (20/Solar), into the Point of Interconnection (POI) at Liberal 115 kV Substation | SUNC | 32 | 9000000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Liberal 115 kV Substation GEN-2020-082 Interconnection (TOIF) (SUNC) | 156925 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-082 (20/Solar), into the Point of Interconnection (POI) at Liberal 115 kV Substation | SUNC | 32 | 500000
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs to GEN-2020-065 230 kV Build Second Line | TBD | Build a second 230 kV line from Hobbs to GEN-2020-065 (17.6 miles) | SPS | 36 | 20375273.6
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs to GEN-2020-065 230 kV Rebuild | TBD | Rebuild the Hobbs to GEN-2020-065 230 kV 17.6 mile line to minimum rating of 760 MVA | SPS | 36 | 15549758.4
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Holdrege to G20-013-TAP 115 kV Rebuild | TBD | Rebuild the Holdrege to G20-013-TAP 115 kV 0.39 mile line to a minimum rating of 211 MVA | NPPD | 36 | 277227.6
Current Study | Steady State | 03 - Central / 05 - Southwest | DISIS-2020-001 | NRIS | Install Second Yoakum 345-230 kV Transformer | TBD | Install a second 345-230 kV transformer at Yoakum | SPS | 36 | 9435938
Current Study | Steady State | 03 - Central / 04 - Southeast / 05 - Southwest | DISIS-2020-001 | NRIS | Install Third Tuco 345-230 kV Transformer | TBD | Install a third 345-230 kV transformer at Tuco | SPS | 36 | 9435938
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (Non-shared NU) (WERE) | 156933 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | WERE | 36 | 22839882
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Neosho-Delaware 345 kV GEN-2020-052 Interconnection (TOIF) (WERE) | 156934 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-052 (251/Wind), into the Point of Interconnection (POI) at Neosho-Delaware 345 kV | WERE | 36 | 1705965
Current Study | Steady State | 03 - Central / 05 - Southwest | DISIS-2020-001 | NRIS | Install Third Yoakum 345-230 kV Transformer | TBD | Install a third 345-230 kV transformer at Yoakum | SPS | 36 | 9435938
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (Non-shared NU) (GMO) | 156943 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 0 | 0
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Hill 345/161/69 kV Substation GEN-2020-061 Interconnection (TOIF) (GMO) | 156944 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-061 (29/Thermal), into the Point of Interconnection (POI) at Pleasant Hill 345/161/69 kV Substation | GMO | 0 | 0
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Kirby to Conway 115 kV Rebuild | TBD | Rebuild the Kirby to Conway 115 kV 25.18 mile line to a minimum rating of 195 MVA | SPS | 36 | 17898951.2
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton Eastside to G17-171-Tap 345 kV Build Second Line | TBD | Build a second 345 kV line from Lawton Eastside to G17-171-Tap (14.4 miles) | SPS | 36 | 21594168
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (EDE) | TBD | Rebuild the Litchfield to Asbury Plant 161 kV 5.24 mile line to a minumum of 254 MVA (EDE) | EDE | 36 | 5121980.864
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (Non-shared NU) (EDE) | 156951 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EDE | 36 | 8850000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Riverton-Neosho 161kV line GEN-2020-079 Interconnection (TOIF) (EDE) | 156952 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-079 (225/Hybrid), into the Point of Interconnection (POI) at Riverton-Neosho 161kV line | EDE | 36 | 8850000
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (Non-shared NU) (SUNC) | 144325 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 18 | 219182
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Russell 115 kV Substation GEN-2020-056 Interconnection (TOIF) (SUNC) | 144324 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-056 (20/Solar), into the Point of Interconnection (POI) at Russell 115 kV Substation | SUNC | 18 | 2352460
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (Non-shared NU) (KCPL) | 156958 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | KCPL | 36 | 10619884
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | SE Ottawa to Pleasant Valley 161kV GEN-2020-073 Interconnection (TOIF) (KCPL) | 156959 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-073 (190/Hybrid), into the Point of Interconnection (POI) at SE Ottawa to Pleasant Valley 161kV | KCPL | 36 | 842712
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Litchfield to Asbury Plant 161 kV Rebuild (KCPL) | TBD | Rebuild the Litchfield to Asbury Plant 161 kV 1.56 mile line to a minumum of 254 MVA (KCPL) | KCPL | 36 | 1529942.336
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Marmaton 161 kV Bus-Tie Upgrade | TBD | Updated the Marmaton 161 kV Bus-Tie to a minimum rating of 228 MVA | WERE | 36 | 566485
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Marmaton 161 kV Terminal Equipment Upgrade | TBD | Install terminal equipment upgrade at Marmaton 161 kV to connect the second Marmaton to Dakota 161 kV line | WERE | 36 | 566485
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (Non-shared NU) (WERE) | 156972 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | WERE | 36 | 22839880
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Swissvale to Morris 230 KV line GEN-2020-071 Interconnection (TOIF) (WERE) | 156973 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-071 (252/Wind), into the Point of Interconnection (POI) at Swissvale to Morris 230 KV line | WERE | 36 | 1705965
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Marmaton to Dakota 161 kV Build Second Line | TBD | Build a second 161 kV 10.5 mile line from Marmaton to Dakota with a minimum rating of 281 MVA | KCPL | 36 | 11546786.5
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (Non-shared NU) (GMO) | 156986 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 36 | 10565920
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Windsor to AEC Sedalia 161 kV line GEN-2020-072 Interconnection (TOIF) (GMO) | 156987 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-072 (150/Hybrid), into the Point of Interconnection (POI) at Windsor to AEC Sedalia 161 kV line | GMO | 36 | 842710
Contingent | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Wolf Creek 345kV Terminal Equipment | 112509 | Install terminal equipment at Wolf Creek to support 345kV line from Wolf Creek to Blackberry rated at 1792 MVA | EKC | 36 | 17884513
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (Non-shared NU) (WERE) | 156988 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | WERE | 36 | 21420836
Interconnection | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Wolf Creek- Blackberry 345 kV Substation GEN-2020-090 Interconnection (TOIF) (WERE) | 156989 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-090 (204.3/Solar), into the Point of Interconnection (POI) at Wolf Creek- Blackberry 345 kV Substation | WERE | 36 | 1705965
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | N. Hebron to G20-077-TAP 115 kV Rebuild | TBD | Rebuild the N. Hebron to G20-077-TAP 115 kV 11.27 mile line to a minimum rating of 149 MVA | NPPD | 36 | 8011166.8
Contingent | Steady State | 03 - Central / 05 - Southwest | DISIS-2020-001 | NRIS | Crossroads-Hobbs-Roadrunner RFP | TBD | Build double circuit 345 kV line from Crossroads-Hobbs-Roadrunner | SPS | 36 | 395000000
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Newhart to Plant X 230 kV Rebuild | TBD | Rebuild the Newhart to Plant X 230 kV 39.59 mile line to a minmum rating of 570 MVA | SPS | 36 | 34978121.31
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Hill 345 kV Terminal Equiment Upgrade | TBD | Upgrade the existing Pleasant Hill 345 kV terminal equiment to 956 MVA | KCPL | 36 | 1200000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Pleasant Valley to West Gardner 161 kV Build Second Line | TBD | Build a second 161 kV 12.05 line from Pleasant Valley to West Gardner with a minimum of 351 MVA | KCPL | 36 | 12601203.15
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Post Oak to Clinton PLT2 69 kV Rebuild | TBD | Rebuild the Post Oak to Clinton PLT2 69 kV 13.6 mile line to a minimum rating of 81 MVA | KCPL | 36 | 12361706.4
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Post Rock 345/230 kV Install Second Transformer | TBD | Install a second 345/230 kV transformer at Post Rock | MIDW | 36 | 9435938
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | NRIS | Replace Carlisle 230-115 kV Transformer | TBD | Replace the Carlisle 230-115 kV Transformer to a minimum of 211 MVA | SPS | 36 | 6621188
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Replace Snyder 138-69 kV Transformer | TBD | Replace Snyder 138-69 kV Transformer to a minimum of 90 MVA | AEPW | 36 | 3128743
Current Study | Steady State | 03 - Central / 05 - Southwest | DISIS-2020-001 | NRIS | Replace Tuco 345-230 kV Transformer #1 | TBD | Replace the Tuco 345-230 kV Transformer #1 to a minimum of 609 MVA | SPS | 36 | 8302968
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-075 Interconnection (TOIF) (AEP) | 156888 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-075 (200/Battery/Storage), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345 kV Line GEN-2020-087 Interconnection (TOIF) (AEP) | 156889 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-087 (500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Cimmarron to Lawton 345kV Line GEN-2020-075, GEN-2020-087 Interconnection (DISIS-2020-001) (AEP) | 156890 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-075, GEN-2020-087 (200/Battery/Storage and 500/Solar), into the Point of Interconnection (POI) at Cimmarron to Lawton 345 kV Line | AEP | 36 | 21000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (Non-shared NU) (OGE) | 156913 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | OGE | 24 | 2000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Johnston County 345 kV Substation GEN-2020-015 Interconnection (TOIF) (OGE) | 156914 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-015 (104/Solar), into the Point of Interconnection (POI) at Johnston County 345 kV Substation | OGE | 24 | 1000000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Riverton to G20-079-TAP 161kV Rebuild | TBD | Rebuild the Riverton to G20-079-TAP 161kV mile 5.47 line to a minumum of 570 MVA | MEDE | 36 | 5350885.28
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345 kV Line GEN-2020-085 Interconnection (TOIF) (AEP) | 156919 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-085 (500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Line | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345 kV Substation GEN-2020-074 Interconnection (TOIF) (AEP) | 156920 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-074 (200/Battery/Storage), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lawton to Sunnyside 345kV Line GEN-2020-074, GEN-2020-085 Interconnection (DISIS-2020-001) (AEP) | 156921 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-074, GEN-2020-085 (200/Battery/Storage, 500/Solar), into the Point of Interconnection (POI) at Lawton to Sunnyside 345 kV Substation | AEP | 36 | 21000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lydia 345 kV Station GEN-2020-054, GEN-2020-055 Interconnection (TOIF) (AEP) | 156929 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-054 (298/Solar) and GEN-2020-055 (71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | AEP | 36 | 1500000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Lydia 345kV Station GEN-2020-054, GEN-2020-055 Interconnection (DISIS-2020-001) (AEP) | 156930 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-054, GEN-2020-055 (298/Solar and 71/Battery/Storage), into the Point of Interconnection (POI) at Lydia 345 kV Station | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (Non-shared NU) (AEP) | 156947 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEP | 36 | 10000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Pryor Junction - Midwest Carbide 138kV line GEN-2020-092 Interconnection (TOIF) (AEP) | 156948 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-092 (100/Solar), into the Point of Interconnection (POI) at Pryor Junction - Midwest Carbide 138kV line | AEP | 36 | 1500000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Russett to Glasses 138 kV Rebuild | TBD | Rebuild the Russett to Glasses 138 kV mile 8.33 line to a minumum of 176 MVA | OGE | 36 | 8031444.47
Contingent | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Russett - South Brown 138 kV Ckt 1 Rebuild | 112443 | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | WFEC | 36 | 10267390.81
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | S1362 to S1363 161 kV Build Second Line | TBD | Build a second 5.44 mile line from S1363 to S1362 161 kV with a minimum rating of 601 MVA | OPPD | 36 | 5688841.92
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (Non-shared NU) (WFEC) | 156960 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 36 | 4900000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Seiling-Taloga Substations 138kV GEN-2020-010 Interconnection (TOIF) (WFEC) | 156961 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-010 (140/Hybrid), into the Point of Interconnection (POI) at Seiling-Taloga Substations 138kV | WFEC | 36 | 400000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (Non-shared NU) (WFEC) | 156964 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | WFEC | 36 | 4900000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder SW-Cache 138 kV line GEN-2020-016 Interconnection (TOIF) (WFEC) | 156965 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-016 (202/Wind), into the Point of Interconnection (POI) at Snyder SW-Cache 138 kV line | WFEC | 36 | 400000
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | San Juan to Oasis 230 kV Rebuild | TBD | Rebuild the San Juan to Oasis 230 kV 46.2 mile line to a minimum rating of 335 MVA | SPS | 36 | 40818115.8
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (Non-shared NU) (AEP) | 156966 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEP | 36 | 10000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder-Altus Jct. 138kV GEN-2020-012 Interconnection (TOIF) (AEP) | 156967 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-012 (113/Hybrid), into the Point of Interconnection (POI) at Snyder-Altus Jct. 138kV | AEP | 36 | 1500000
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Shawnee to Lenexa 161 kV Rebuild | TBD | Rebuild the Shawnee to Lenexa 161 kV mile line to a minumum of 456 MVA | KCPL | 36 | 3824855.84
Current Study | Steady State | 02 - Nebraska | DISIS-2020-001 | ERIS | Sidney 345/230 kV Transformer Replacement | TBD | Replace the existing 345/230 kV transformer at Sidney to a minimum of 604 MVA | BEPC | 36 | 8302968
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (Non-shared NU) (AEP) | 156993 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEP | 36 | 17000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tap the 345 kV Northwest Texarkana - Valliant line GEN-2020-020 Interconnection (TOIF) (AEP) | 156974 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-020 (201.6/Hybrid), into the Point of Interconnection (POI) at Tap the 345 kV Northwest Texarkana - Valliant line | AEP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (Non-shared NU) (AEP) | 156975 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEP | 36 | 4000000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Tenaska Switching Substation 345kV GEN-2020-081 Interconnection (TOIF) (AEP) | 156976 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-081 (200/Battery/Storage), into the Point of Interconnection (POI) at Tenaska Switching Substation 345kV | AEP | 36 | 3000000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Snyder to G20-016-Tap 138 kV Build Second Line | TBD | Build a second 138 kV line from Snyder to G20-016-Tap (14.61 miles) | SPS | 36 | 12176952.87
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Springfield to LA Russell 161 kV Build Second Line | TBD | Build a second 161 kV 43.1 line from Springfield to LA Russell with a minimum rating of 189 MVA | SWPA | 36 | 45071523.3
Current Study | Steady State | 03 - Central | DISIS-2020-001 | NRIS | Stilwell to Hickman 161 kV Terminal Equiment Upgrade | TBD | Upgrade existing terminal equipment at Stilwell to Hickman 161 kV to 334 MVA | KCPL | 36 | 300000
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Sunnyside to G20-085-Tap 345 kV Build Second Line | TBD | Build a second 345 kV line from Sunnyside to G20-085-Tap (11.79 miles) | SPS | 36 | 17680225.05
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Sunnyside to Uniroyal 138 kV Rebuild | TBD | Rebuild the Sunnyside to Uniroyal 138 kV mile 5.58 line to a minumum of 268 MVA | OGE | 36 | 5380007.22
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (Non-shared NU) (OGE) | 156990 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | OGE | 24 | 4500000
Interconnection | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Woodring 345 KV Station GEN-2020-023 Interconnection (TOIF) (OGE) | 156991 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-023 (202/Battery/Storage), into the Point of Interconnection (POI) at Woodring 345 KV Station | OGE | 24 | 1000000
Contingent | Steady State | 04 - Southeast / 05 - Southwest | DISIS-2020-001 | NRIS | Anadarko - Gracemont 138 kV Ckt 1 Rebuild | 122577 | Rebuild 5.09-mile 138 kV line from Anadarko to Gracemont as a double circuit and install/upgrade any necessary terminal equipment to increase the summer emergency rating to 353 MVA for each circuit | WFEC | 36 | 5750000
Contingent | Steady State | 04 - Southeast / 05 - Southwest | DISIS-2020-001 | NRIS | Anadarko - Gracemont 138 kV Ckt 2 Rebuild | 122753 | Rebuild 5.09-mile 138kV line from Anadarko to Gracemont as double circuit and add/upgrade any necessary equipment to increase the achieve a summer emergency rating of 353 MVA for each circuit | WFEC | 36 | 1750000
Contingent | Steady State | 04 - Southeast / 05 - Southwest | DISIS-2020-001 | NRIS | Gracemont 138 kV Ckt 2 Terminal Equipment | 122755 | Install terminal equipment at Gracemont 138 kV to support a second 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 353 MVA | OGE | 36 | 1124593
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (Non-shared NU) (SPS) | 156875 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | SPS | 36 | 10594150
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | 230kV Lamb County Interchange GEN-2020-017 Interconnection (TOIF) (SPS) | 156876 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-017 (74.88/Solar), into the Point of Interconnection (POI) at 230kV Lamb County Interchange | SPS | 36 | 1017923
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Conway 115 kV Line (524079) GEN-2020-005 Interconnection (Non-shared NU) (SPS) | 156893 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-005 (150/Wind), into the Point of Interconnection (POI) at Conway 115 kV Line (524079) | SPS | 36 | 14515481
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Conway 115 kV Line (524079) GEN-2020-005 Interconnection (TOIF) (SPS) | 156894 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-005 (150/Wind), into the Point of Interconnection (POI) at Conway 115 kV Line (524079) | SPS | 36 | 624130
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Treasild7 to G20-075-Tap 345 kV Rebuild | TBD | Rebuild the Treasild7 to G20-075-Tap 345 kV 30.63 mile line to a minimum rating of 1345 MVA | SPS | 36 | 13939327.92
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Treasild7 to Gracemont 345 kV Build Second Line | TBD | Build a second 345 kV line from Treasild7 to Gracemont (14.74 miles) | SPS | 36 | 22104030.3
Current Study | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to GEN-2017-151 345 kV Rebuild | TBD | Rebuild the Tuco to GEN-2017-151 345 kV 26 mile line to a minimum rating of 1070 MVA | SPS | 36 | 29755544
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Uniroyal to Ardmore West 138 kV Rebuild | TBD | Rebuild the Uniroyal to Ardmore West 138 kV mile 0.57 line to a minumum of 244 MVA | OGE | 36 | 549570.63
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (Non-shared NU) (SPS) | 156909 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 36 | 30437222
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Hobbs-Andrews 345 kV Line GEN-2020-065 Interconnection (TOIF) (SPS) | 156910 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-065 (1003/Thermal), into the Point of Interconnection (POI) at Hobbs-Andrews 345 kV Line | SPS | 36 | 1532799
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | NRIS | Walters2 to Walters-2 69 kV Rebuild | TBD | Rebuild the Walters2 to Walters-2 69 kV mile 5.13 line to a minumum of 56 MVA | WFEC | 36 | 4662908.37
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (Non-shared NU) (AEP) | 156917 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | AEP | 36 | 17000000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lawton East Side to Oklaunion 345kV GEN-2020-009 Interconnection (TOIF) (AEP) | 156918 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-009 (300/Hybrid), into the Point of Interconnection (POI) at Lawton East Side to Oklaunion 345kV | AEP | 36 | 3000000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (Non-shared NU) (SPS) | 156926 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 36 | 9772056
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Lubbock East Substation 230 kV GEN-2020-060 Interconnection (TOIF) (SPS) | 156927 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-060 (200/Battery/Storage), into the Point of Interconnection (POI) at Lubbock East Substation 230 kV | SPS | 36 | 1947926
Current Study | Steady State | 03 - Central | DISIS-2020-001 | ERIS | Warrensburg to Post Oak 69 kV Rebuild | TBD | Rebuild the Warrensburg to Post Oak 69 kV 13.7 mile line to a minimum rating of 81 MVA | KCPL | 36 | 12452601.3
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (Non-shared NU) (SPS) | 156937 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | SPS | 36 | 9895590
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | OASIS 230kV Substation GEN-2020-062 Interconnection (TOIF) (SPS) | 156938 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-062 (256/Solar), into the Point of Interconnection (POI) at OASIS 230kV Substation | SPS | 36 | 1852814
Current Study | Steady State | 04 - Southeast | DISIS-2020-001 | ERIS | Welsh to Wilkes 345 kV Rebuild | TBD | Rebuild the Welsh to Wilkes 345 kV 30.63 mile line to a minimum rating of 1345 MVA | SPS | 36 | 35054319.72
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | San Juan Mesa 230 kV Line GEN-2020-063 Interconnection (Non-shared NU) (SPS) | 156956 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-063 (184/Solar), into the Point of Interconnection (POI) at San Juan Mesa 230 kV Line | SPS | 36 | 3488419
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | San Juan Mesa 230 kV Line GEN-2020-063 Interconnection (TOIF) (SPS) | 156957 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-063 (184/Solar), into the Point of Interconnection (POI) at San Juan Mesa 230 kV Line | SPS | 36 | 1211256
Current Study | Steady State | 01 - North | DISIS-2020-001 | ERIS | Whitlock to Oahe 230 kV New Line Build | TBD | Build a new 40.38 mile 230 kV line from Whitlock to Oahe with a minimum rating of 264 MVA | WAPA | 36 | 47880330.68
Contingent | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Sweetwater to Chisholm 230 kV Rebuild | TBD | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile line to a minimum winter/emergency rating of 796 MVA. | AEP | 36 | 33000000
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco Interchange 345 kV Substation GEN-2020-080 Interconnection (Non-shared NU) (SPS) | 156977 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-080 (200/Battery/Storage), into the Point of Interconnection (POI) at Tuco Interchange 345 kV Substation | SPS | 36 | 8073719
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco Interchange 345 kV Substation GEN-2020-080 Interconnection (TOIF) (SPS) | 156978 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-080 (200/Battery/Storage), into the Point of Interconnection (POI) at Tuco Interchange 345 kV Substation | SPS | 36 | 8252153
Current Study | Steady State | 03 - Central / 05 - Southwest | DISIS-2020-001 | NRIS | Yoakum to Ink Basin 230 kV Rebuild | TBD | Rebuild the Yoakum to Ink Basin 230 kV mile 17.29 line to a minumum of 702 MVA | SPS | 36 | 15275870.61
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067 Interconnection (TOIF) (SPS) | 156979 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-067 (352.5/Wind), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 36 | 690867
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-067, GEN-2020-068 Interconnection (DISIS-2020-001) (SPS) | 156980 | Interconnection upgrades and cost estimates needed to interconnect the following IC facility, GEN-2020-067, GEN-2020-068 (352.5/Wind and 400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 36 | 2763470
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco to Yoakum 345kV line GEN-2020-068 Interconnection (TOIF) (SPS) | 156981 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-068 (400/Solar), into the Point of Interconnection (POI) at Tuco to Yoakum 345kV line | SPS | 36 | 690867
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (Non-shared NU) (SPS) | 156982 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (500/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | SPS | 36 | 15573312
Interconnection | Steady State | 05 - Southwest | DISIS-2020-001 | ERIS | Tuco-Yoakum-Hobbs 345 kV GEN-2020-059 Interconnection (TOIF) (SPS) | 156983 | Interconnection upgrades and cost estimates needed to interconnect the following Interconnection Customer facility, GEN-2020-059 (500/Hybrid), into the Point of Interconnection (POI) at Tuco-Yoakum-Hobbs 345 kV | SPS | 36 | 1381735
2120664711.35

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00ALL | 0 | 24SP | GEN-2020-065 | " | Non-Converge |  |  | 0.83453 |  | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1
Non-Converge | 00ALL | 0 | 27SP | GEN-2020-065 | " | Non-Converge |  |  | 0.83464 |  | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1
Non-Converge | 00ALL | 0 | 27WP | GEN-2020-065 | " | Non-Converge |  |  | 0.83472 |  | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1
Non-Converge | 00NR | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 00NR | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 01NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 02NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 03NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 04NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 24SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27SP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05ALL | 0 | 27WP | N/A | " | Non-Converge |  |  |  |  | None
Non-Converge | 05NR | 0 | 27L | N/A | " | Non-Converge |  |  |  |  | None
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.19833 | 100.18 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.21409 | 127.74 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.21378 | 127.65 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-065 | TO -> FROM | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1 |  | 606 | 0.83472 | 120.18 | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 2
Thermal | 00ALL | 1 | 24SP | GEN-2020-065 | TO -> FROM | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1 |  | 545 | 0.83456 | 116.96 | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 2
Thermal | 00ALL | 1 | 27SP | GEN-2020-065 | TO -> FROM | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 1 |  | 545 | 0.83464 | 118.51 | 527894 HOBBS_INT 6 230 764930 G20-065-TAP 230 2
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25542 | 104.01 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25542 | 104.01 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25542 | 104.01 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25818 | 110.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25818 | 110.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25818 | 110.4 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25496 | 114.97 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25496 | 114.97 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646249 S1249 5 161 646254 S1254 5 161 1 |  | 298 | 0.25496 | 114.97 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83195 | 226.63 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83195 | 226.63 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83195 | 226.63 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 107.87 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45793 | 112.37 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83067 | 208.11 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83067 | 208.11 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83067 | 208.11 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 110.87 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45564 | 104.88 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83169 | 207.08 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83169 | 207.08 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.83169 | 207.08 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646254 S1254 5 161 646281 S1281 5 161 1 |  | 298 | 0.45799 | 100.64 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.72 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.72 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.72 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.56 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.56 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.56 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.48 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.48 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646281 S1281 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.48 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:LX009::S1214.S1287.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 102.58 | P12:161:OPPD:S1214-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:S1281-S1287:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.54207 | 104.35 | P12:161:OPPD:LX010::S1287.S1281.CKT1::
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82801 | 126.08 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53961 | 101.23 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53961 | 101.23 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.53961 | 101.23 | P12:161:OPPD:S1249-S1254:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 164.74 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.25 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 24SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82788 | 114.38 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.43 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.43 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.43 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 1 | 151.42 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P21:161:OPPD:S1281-S1254:::HV:
Thermal | 00ALL | 1 | 27SP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 1 |  | 558 | 0.82775 | 115.78 | P12:161:OPPD:S1254-S1281:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03485 | 122.52 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03485 | 121.19 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03485 | 119.03 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.0385 | 108.96 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.0385 | 108.96 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03909 | 107.58 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03909 | 107.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03909 | 107.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03909 | 107.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03909 | 107.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03736 | 105.97 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03736 | 104.16 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03018 | 100.78 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03018 | 100.78 | P23:345:AEPW:PITTSBURG CB 3425A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03524 | 122.52 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03524 | 121.19 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03524 | 119.03 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03897 | 108.96 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03897 | 108.96 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03959 | 107.58 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03959 | 107.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03959 | 107.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03959 | 107.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03959 | 107.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03781 | 105.97 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03781 | 104.16 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.0305 | 100.78 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.0305 | 100.78 | P23:345:AEPW:PITTSBURG CB 3425A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04307 | 122.52 | 515150 CANEYCK4 138 515151 LTLCITY4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04307 | 121.19 | 515151 LTLCITY4 138 515152 BROWNTP4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.04307 | 119.03 | P12:138:OKGE:BKRBKR261::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05148 | 108.96 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05148 | 108.96 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05356 | 107.58 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05356 | 107.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05356 | 107.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05356 | 107.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.05356 | 107.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03527 | 105.97 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03527 | 104.16 | 515136 SUNNYSD7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03459 | 100.78 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03459 | 100.78 | P23:345:AEPW:PITTSBURG CB 3425A NBTB::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03396 | 109.51 | 515120 RUSSET-4 138 515147 GLASSES4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03396 | 106.06 | 515147 GLASSES4 138 515149 MADINDT4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | TO -> FROM | 505602 S BROWN4 138 521044 RUSSETT4 138 1 |  | 136 | 0.03396 | 103.5 | P12:138:OKGE:BKRBKR248::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03155 | 117.77 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03157 | 117.76 | P12:138:AEPW:DUNCAN-4:L.E.S.-4:::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03155 | 117.74 | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04525 | 115.61 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04514 | 114.89 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03152 | 114.13 | P12:138:AEPW:DUNCAN-4:L.E.S.-4:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03149 | 114.13 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03149 | 114.12 | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03099 | 110.79 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03099 | 110.78 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03103 | 109.89 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03103 | 109.89 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03009 | 106.14 | P12:138:WFEC:ANADRKO_COMANCHE::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03236 | 105.34 | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03001 | 103.06 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03001 | 101.77 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03127 | 100.81 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04367 | 100.12 | 520404 MDCPRK4 138 521190 CACHEJ4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03203 | 100.09 | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04022 | 117.77 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04024 | 117.76 | P12:138:AEPW:DUNCAN-4:L.E.S.-4:::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04022 | 117.74 | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.06235 | 115.61 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0625 | 114.89 | P12:69:AEPW:COMANC-2:L.E.S.-2:::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04034 | 114.13 | P12:138:AEPW:DUNCAN-4:L.E.S.-4:::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04032 | 114.13 | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04032 | 114.12 | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03987 | 110.79 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03987 | 110.78 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04011 | 109.89 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04011 | 109.89 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03776 | 106.14 | P12:138:WFEC:ANADRKO_COMANCHE::::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04069 | 105.34 | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03783 | 103.06 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03783 | 101.77 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03945 | 100.81 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.06303 | 100.12 | 520404 MDCPRK4 138 521190 CACHEJ4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.04047 | 100.09 | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0381 | 111.14 | P13:69-138:AEPW:DUNCAN-2::::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03794 | 108.51 | 520814 ANADARK4 138 520923 GEORGIA4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03816 | 108.43 | P13:69-138:AEPW:DUNCAN-2::::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03787 | 107.38 | 520814 ANADARK4 138 520923 GEORGIA4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0381 | 106.68 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03794 | 106.53 | 520912 FLETCH-4 138 520923 GEORGIA4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03765 | 105.44 | P12:138:WFEC:ANADRKO_COMANCHE::::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03787 | 105.36 | 520912 FLETCH-4 138 520923 GEORGIA4 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0381 | 104.98 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03816 | 103.94 | 511452 DUNCAN-2 69.0 511457 DUNTOS TP2 69.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0381 | 103.47 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2:::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.0381 | 103.31 | P12:069:WFEC:COM-TAP2_COMANCHE::::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03751 | 102.81 | 515150 CANEYCK4 138 521067 TEXOMAJ4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03776 | 102.36 | 520900 EMPIRE 4 138 520912 FLETCH-4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03816 | 102.23 | 511457 DUNTOS TP2 69.0 511498 COM-TAP2 69.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 | 40 |  | 0.03844 | 101.96 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03776 | 101.02 | 520864 COMANCH4 138 520900 EMPIRE 4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03816 | 100.79 | P12:69:WFEC-AEPW:COMANCH2:DUNCAN-2:::
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511434 WALTRS-2 69.0 521086 WALTERS2 69.0 1 |  | 45 | 0.03816 | 100.63 | P12:069:WFEC:COM-TAP2_COMANCHE::::
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | FROM -> TO | 511435 SNYDER-4 138 997966 SNYDER 69.0 1 |  | 75 | 0.15577 | 117.92 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | FROM -> TO | 511435 SNYDER-4 138 997966 SNYDER 69.0 1 |  | 75 | 0.15607 | 115.03 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | FROM -> TO | 511435 SNYDER-4 138 997966 SNYDER 69.0 1 |  | 75 | 0.11538 | 117.92 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 511435 SNYDER-4 138 997966 SNYDER 69.0 1 |  | 75 | 0.11536 | 115.03 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511475 SNYDER-2 69.0 997966 SNYDER 69.0 1 |  | 75 | 0.15577 | 117.89 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511475 SNYDER-2 69.0 997966 SNYDER 69.0 1 |  | 75 | 0.15607 | 115.01 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511475 SNYDER-2 69.0 997966 SNYDER 69.0 1 |  | 75 | 0.11538 | 117.89 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511475 SNYDER-2 69.0 997966 SNYDER 69.0 1 |  | 75 | 0.11536 | 115.01 | 511440 ALTUSJT4 138 765230 G20-012-TAP 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-015 | FROM -> TO | 515120 RUSSET-4 138 515147 GLASSES4 138 1 |  | 153 | 0.03186 | 104.69 | P12:138:OKGE:BKRBKR345::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04333 | 106.15 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04333 | 106.13 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04085 | 101.37 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04085 | 101.35 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03889 | 101.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03889 | 101.18 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07603 | 117.23 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07378 | 112.65 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10929 | 106.15 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10929 | 106.13 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06908 | 103.57 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06806 | 101.4 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10663 | 101.37 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10663 | 101.35 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06631 | 101.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06631 | 101.18 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07215 | 100.37 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07725 | 117.23 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07498 | 112.65 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.11094 | 106.15 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.11094 | 106.13 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07018 | 103.57 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06917 | 101.4 | 515164 ROCKYPT4 138 515172 SPRNDAL4 138 1
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10828 | 101.37 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.10828 | 101.35 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06697 | 101.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.06697 | 101.18 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.07322 | 100.37 | 521157 HUGO 7 345 560088 G16-063-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03693 | 106.15 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03693 | 106.13 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.0343 | 101.37 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.0343 | 101.35 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04048 | 101.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04048 | 101.18 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03693 | 106.15 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.03693 | 106.13 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.0343 | 101.37 | P12:345:OKGE:BKRBKR21::::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.0343 | 101.35 | P42:345:OKGE:SB_JOCO7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04048 | 101.19 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 |  | 225 | 0.04048 | 101.18 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07605 | 108 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2020-074 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07381 | 103.22 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07727 | 108 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 27SP | GEN-2020-085 | FROM -> TO | 515137 UNIROY 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07501 | 103.22 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 |  | 191 | 0.04515 | 103.67 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515138 CARTER 4 138 515171 CHIKSAW4 138 1 |  | 191 | 0.04587 | 103.67 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07612 | 102.96 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515138 CARTER 4 138 515372 ARDWEST4 138 1 |  | 222 | 0.07735 | 102.96 | P12:138:OKGE:BKRBKR257::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12859 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.10004 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.10004 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.10004 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.09488 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06358 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04631 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04631 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04631 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-074 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04333 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06178 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04488 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04488 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04488 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-085 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04196 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.1634 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.11876 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.1634 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.12551 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.11876 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.04727 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.03135 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.03142 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-015 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.03148 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-016 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.03005 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.06328 | 151.43 | P42:345:OKGE:SB_GRNT7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.08571 | 127.01 | P42:345:OKGE:SB_MICO7311::::
Thermal | 00NR | 1 | 24SP | GEN-2020-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.08571 | 126.86 | P42:345:OKGE:SB_MICO7381::::
Thermal | 00NR | 1 | 24SP | GEN-2020-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.08571 | 126.75 | P12:345:OKGE:BKRBKR367::::
Thermal | 00NR | 1 | 24SP | GEN-2020-010 | FROM -> TO | 515802 GRACMNT4 138 520814 ANADARK4 138 1 |  | 234 | 0.08565 | 121.7 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.07572 | 119.15 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.07226 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.07226 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.06162 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.06162 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.28106 | 119.15 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.28106 | 119.15 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.2811 | 119.15 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.31367 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.31367 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.12465 | 119.15 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.13014 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997622 UPDATE LATER 230 1 |  | 559 | 0.13014 | 100.35 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.04997 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03581 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.0304 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03031 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.0304 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03592 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.0464 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.0464 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05014 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03004 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03021 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03004 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.03021 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.12484 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.1091 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07909 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07858 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07909 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.12112 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07123 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07123 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13886 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07337 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06046 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06117 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06555 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05415 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05415 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07047 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07047 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07337 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07323 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.07337 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.11874 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.12958 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.11105 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07125 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07125 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13276 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16545 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05688 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05758 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06636 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05056 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.05056 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07129 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07129 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06979 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.06965 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.06979 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.30363 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.40464 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.21754 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.41667 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31765 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16555 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16625 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17666 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17832 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.17846 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.30363 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.40464 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.21754 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.41667 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31765 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16555 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16625 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17666 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17832 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.17846 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.53817 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.4047 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.33046 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32917 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.33046 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.41672 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31869 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31869 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.55218 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31631 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.3034 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.3041 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31646 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.29708 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.29708 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32138 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32138 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31631 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.31617 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.31631 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.22393 | 176.26 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.17952 | 172.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13927 | 130.54 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.1386 | 117.83 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13927 | 116.62 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.19154 | 116.04 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.12776 | 108.67 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.12776 | 108.67 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.23794 | 105.75 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13162 | 113.51 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.1187 | 111.25 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.11941 | 111.13 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.15854 | 109.5 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.11239 | 108.89 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.11239 | 108.88 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16347 | 108.88 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.16347 | 108.85 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.74 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.74 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.74 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13162 | 108.06 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 |  | 559 | 0.13147 | 107.82 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997623 UPDATE LATER 230 1 | 559 |  | 0.13162 | 103.19 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.04857 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.0312 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.12135 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.09508 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.11542 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.29513 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.35263 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.29513 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.35263 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.52311 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.35268 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.21766 | 149.15 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997624 SIEM 8743066 230 2 |  | 643 | 0.15645 | 130.42 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997624 UPDATE LATER 230 1 |  | 559 | 0.07478 | 111.9 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997624 UPDATE LATER 230 1 |  | 559 | 0.28005 | 111.9 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997624 UPDATE LATER 230 1 |  | 559 | 0.28005 | 111.9 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997624 UPDATE LATER 230 1 |  | 559 | 0.28008 | 111.9 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997624 UPDATE LATER 230 1 |  | 559 | 0.1236 | 111.9 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.05095 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03587 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03058 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03112 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03058 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03012 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03012 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.04702 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.04702 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03074 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03074 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.12163 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.10773 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07695 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07665 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07695 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07186 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07188 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06919 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06919 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07135 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0548 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.07063 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06272 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0511 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0511 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06817 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06817 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.1461 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13053 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13855 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.09643 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.09639 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08733 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08733 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16489 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06916 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08499 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08198 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06545 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.06545 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08743 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.08743 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.31797 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.40319 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.23366 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19236 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19234 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18652 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16998 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18581 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18426 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.31797 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.40319 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.23366 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19236 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19234 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18652 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16998 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18581 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18426 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.54213 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.40324 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32927 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.33336 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32927 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32043 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32043 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32049 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32049 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.31802 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.30148 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.31731 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.31758 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.29777 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.29777 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32303 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32303 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.22219 | 169.21 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.178 | 161.6 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13724 | 121.7 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13797 | 116.39 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13724 | 108.61 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13129 | 106.49 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.1313 | 106.26 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.1265 | 104.41 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.1265 | 104.41 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.13034 | 107.82 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.1138 | 107.51 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.12963 | 104.99 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.15706 | 104.9 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.11009 | 104.41 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.11009 | 104.41 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16251 | 104.28 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.16251 | 104.25 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 104.12 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 104.12 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 104.12 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.04955 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.03126 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.11829 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.09388 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.14209 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.30924 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.35137 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.30924 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.35137 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.52725 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.35141 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.21609 | 143.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 525830 TUCO_INT 6 230 997626 SIEM 8743066 230 2 |  | 643 | 0.15512 | 122.43 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.07572 | 118.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.07226 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.07226 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.06162 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.06162 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.28106 | 118.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.28106 | 118.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.17066 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.2811 | 118.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.31367 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.31367 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.12465 | 118.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.13014 | 100 | 525832 TUCO_INT 7 345 3WXFMR TUCO TR3 3
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997622 UPDATE LATER 230 1 |  | 559 | 0.13014 | 100 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.04997 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03581 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.0304 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03031 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.0304 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03592 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.0464 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.0464 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05014 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03004 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03021 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03004 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03926 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.03021 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.12484 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.1091 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07909 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07858 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07909 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.12112 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07123 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07123 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13886 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07337 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06046 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06117 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06555 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05415 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05415 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07047 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07047 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.04651 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07337 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07323 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.07337 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.11874 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.12958 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.11105 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07125 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07125 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13276 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16545 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05688 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05758 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06636 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05056 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.05056 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07129 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07129 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.07394 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06979 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.06965 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.06979 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.30363 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.40464 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.21754 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.41667 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31765 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16555 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16625 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17666 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17832 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.17846 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.30363 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.40464 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.21754 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.20975 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.41667 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18034 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31765 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16555 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16625 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17666 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.15923 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18159 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.18445 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17846 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17832 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.17846 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.53817 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.4047 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.33046 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32917 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.33046 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.41672 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31869 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31869 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.55218 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31631 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.3034 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.3041 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31646 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.29708 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.29708 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32138 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32138 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.32451 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31631 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.31617 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.31631 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.22393 | 175.48 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.17952 | 170.23 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13927 | 130.05 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.1386 | 117.5 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13927 | 116.17 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.19154 | 115.37 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.12776 | 108.12 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.12776 | 108.12 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.23794 | 105.93 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13162 | 112.7 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.1187 | 110.76 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.11941 | 110.64 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.15854 | 109.05 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.11239 | 108.46 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.11239 | 108.46 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16347 | 108.43 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.16347 | 108.4 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.31 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.31 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.14255 | 108.31 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13162 | 107.63 | 525830 TUCO_INT 6 230 525840 ANTELOPE_1 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 |  | 559 | 0.13147 | 107.37 | 527149 MUSTANG 6 230 527151 GS-MUSTANG 6 230 @1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997623 UPDATE LATER 230 1 | 559 |  | 0.13162 | 102.85 | System Intact
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.04857 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.0312 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.12135 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.09508 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.11542 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.29513 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.35263 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.29513 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.35263 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.52311 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.35268 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.21766 | 148.39 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997624 SIEM 8743066 230 2 |  | 643 | 0.15645 | 128.97 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997624 UPDATE LATER 230 1 |  | 559 | 0.07478 | 111.2 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997624 UPDATE LATER 230 1 |  | 559 | 0.28005 | 111.2 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997624 UPDATE LATER 230 1 |  | 559 | 0.28005 | 111.2 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997624 UPDATE LATER 230 1 |  | 559 | 0.28008 | 111.2 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997624 UPDATE LATER 230 1 |  | 559 | 0.1236 | 111.2 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.05095 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03587 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03058 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03112 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03058 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03012 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03012 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.04702 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.04702 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03074 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-075 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03074 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-087 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.03978 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.12163 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.10773 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07695 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07665 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07695 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07186 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07188 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06919 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06919 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07135 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0548 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.07063 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06272 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0511 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0511 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06817 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06817 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.04393 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.1461 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13053 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13855 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.09643 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.09639 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08733 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08733 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16489 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06916 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08499 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08198 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06545 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.06545 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08743 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.08743 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.0903 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.31797 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.40319 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.23366 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19236 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19234 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18652 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16998 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18581 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18426 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.31797 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.40319 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.23366 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.20985 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19236 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19234 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18852 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18652 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16998 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18581 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18426 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16627 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.18971 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.19277 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.54213 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.40324 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32927 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.33336 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32927 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32043 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32043 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32049 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32049 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.31802 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.30148 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.31731 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.31758 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.29777 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.29777 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32303 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32303 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.32634 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.22219 | 169.02 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.178 | 160.06 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13724 | 121.46 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13797 | 116.28 | 526936 YOAKUM 7 345 3WXFMR SPX WT04221 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13724 | 108.43 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13129 | 106.36 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.1313 | 106.14 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.1265 | 104.11 | P12:345:AEPW-OKGE:L.E.S.-7:GRACMNT7:::
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.1265 | 104.11 | 511409 TREASILD7 345 764550 G20-075-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.13034 | 107.31 | 764840 GEN-2020-059 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.1138 | 107.29 | 525531 TOLK 6 230 525561 TOLK_1 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.12963 | 104.79 | 525531 TOLK 6 230 525562 TOLK_2 1 24.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.15706 | 104.73 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.11009 | 104.25 | 526337 JONES 6 230 526331 JONES_1 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.11009 | 104.24 | 526337 JONES 6 230 526332 JONES_2 1 22.0 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16251 | 104.11 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.16251 | 104.08 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 103.95 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 103.95 | 523777 WHEELER 6 230 523779 STLN-DEMARC6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997625 UPDATE LATER 230 1 |  | 559 | 0.14133 | 103.95 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6:::
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.04955 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-009 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.03126 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.11829 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.09388 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.14209 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.30924 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.35137 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.30924 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.35137 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.52725 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.35141 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.21609 | 143.01 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 525832 TUCO_INT 7 345 997626 SIEM 8743066 230 2 |  | 643 | 0.15512 | 121.27 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 526160 CARLISLE 3 115 997613 SIEM 0136201 115 1 |  | 168 | 0.03923 | 122.6 | 526161 CARLISLE 6 230 526525 WOLFFORTH 6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526160 CARLISLE 3 115 997615 SIEM 0136201 115 1 |  | 168 | 0.03906 | 120.26 | 526161 CARLISLE 6 230 526525 WOLFFORTH 6 230 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526161 CARLISLE 6 230 997613 SIEM 0136201 115 1 |  | 168 | 0.03923 | 126.51 | 526161 CARLISLE 6 230 526525 WOLFFORTH 6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526161 CARLISLE 6 230 997615 SIEM 0136201 115 1 |  | 168 | 0.03906 | 126.23 | 526161 CARLISLE 6 230 526525 WOLFFORTH 6 230 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.05148 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.04359 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.04639 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.03895 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.16012 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.17543 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.1381 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.14954 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.12752 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.13611 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.11133 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.11746 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.12752 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.13611 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.11133 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.11746 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.07843 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.07691 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.07101 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.06917 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.05764 | 111.14 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 625 | 0.05121 | 107.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.05203 | 114.15 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526935 YOAKUM 6 230 527028 INK_BASIN 6 230 1 |  | 547 | 0.04588 | 108.88 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.03441 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.32694 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.22929 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.22929 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.08227 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997591 YOAKUM TR2 230 1 |  | 641 | 0.04545 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.03441 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.32694 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.22929 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.22929 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.08227 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997592 SPX WT04221 230 1 |  | 641 | 0.04545 | 102.16 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.06525 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.07174 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.06525 | 133.38 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.07174 | 106.06 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.59916 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.60564 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 133.38 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 106.06 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 133.38 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 106.06 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.16144 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.16792 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.16144 | 133.38 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.16792 | 106.06 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.08752 | 188.5 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.094 | 156.63 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 641 | 0.08752 | 133.38 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997593 SPX WT04221 230 1 |  | 697 | 0.094 | 106.06 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.03523 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.3228 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.22659 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.22659 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.08174 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997593 YOAKUM TR2 230 1 |  | 641 | 0.04594 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.03523 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.3228 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.22659 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.22659 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.08174 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997594 SPX WT04221 230 1 |  | 641 | 0.04594 | 101.19 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.06671 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.06671 | 129.27 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.03228 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.03229 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.5928 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.34255 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.34253 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 129.27 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.2911 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.29109 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 129.27 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.2911 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.29109 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.16059 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.16059 | 129.27 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.09675 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.09675 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.08841 | 187.07 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.08841 | 129.27 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.04721 | 103.19 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 526935 YOAKUM 6 230 997595 SPX WT04221 230 1 |  | 641 | 0.04722 | 103.17 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.03441 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.32694 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.22929 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.22929 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.08227 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997591 YOAKUM TR2 230 1 |  | 641 | 0.04545 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.03441 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.32694 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.22929 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.22929 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.08227 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997592 SPX WT04221 230 1 |  | 641 | 0.04545 | 102.98 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.06525 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.07174 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.06525 | 133.24 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.07174 | 106.14 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.59916 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.60564 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 133.24 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 106.14 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.42446 | 133.24 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.43094 | 106.14 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.16144 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.16792 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.16144 | 133.24 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.16792 | 106.14 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.08752 | 191.59 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.094 | 158 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 641 | 0.08752 | 133.24 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997593 SPX WT04221 230 1 |  | 697 | 0.094 | 106.14 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.03523 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.3228 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.22659 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.22659 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.08174 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997593 YOAKUM TR2 230 1 |  | 641 | 0.04594 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.03523 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.3228 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.22659 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.22659 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.08174 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997594 SPX WT04221 230 1 |  | 641 | 0.04594 | 101.87 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.06671 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.06671 | 129.08 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.03228 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.03229 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.5928 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.34255 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.34253 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 129.08 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.2911 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.29109 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.4203 | 129.08 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.2911 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.29109 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.16059 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.16059 | 129.08 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.09675 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.09675 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.08841 | 189.82 | 527896 HOBBS_INT 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.08841 | 129.08 | 526936 YOAKUM 7 345 764866 G20-05-TAP1 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.04721 | 103.63 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 526936 YOAKUM 7 345 997595 SPX WT04221 230 1 |  | 641 | 0.04722 | 103.6 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.03571 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.03577 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.18476 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.18463 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.12162 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.12156 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.12162 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.12156 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.06827 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.06828 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.04317 | 104.61 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 |  | 478 | 0.04322 | 104.54 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.04601 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.04596 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.32714 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.32725 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.1686 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.16865 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.1686 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.16865 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.08379 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.08378 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.05471 | 116.32 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | TO -> FROM | 527894 HOBBS_INT 6 230 997560 HICO 68759-1 230 1 |  | 607 | 0.05467 | 115.24 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.04601 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-005 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.04596 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.32714 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-059 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.32725 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.1686 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-067 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.16865 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.1686 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-068 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.16865 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.08379 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-080 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.08378 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.05471 | 114.52 | P42:345:SPS:KIOWA:J20####_SLG::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-008 | FROM -> TO | 527896 HOBBS_INT 7 345 997560 HICO 68759-1 230 1 |  | 607 | 0.05467 | 113.41 | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-079 | FROM -> TO | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.20775 | 100.88 | 547469 RIV4525 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-088 | FROM -> TO | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.03447 | 100.88 | 547469 RIV4525 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM -> TO | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.03148 | 100.88 | 547469 RIV4525 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | FROM -> TO | 532932 LITCH 5 161 547476 ASB349 5 161 1 |  | 251 | 0.21651 | 100.88 | 547469 RIV4525 161 764310 G20-079-TAP 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.03644 | 101.98 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.03798 | 101.08 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.03099 | 101.98 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.0322 | 101.08 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.03653 | 101.98 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 541340 BELTONS5 161 541342 PECULR 5 161 1 |  | 281 | 0.03766 | 101.08 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03465 | 106.3 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0332 | 105.46 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03465 | 103.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0332 | 103.08 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03465 | 102.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04037 | 102.1 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0332 | 101.57 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03846 | 100.45 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04927 | 106.3 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04876 | 105.46 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03448 | 104.68 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04927 | 103.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04876 | 103.08 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03461 | 102.84 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04927 | 102.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04852 | 102.1 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04876 | 101.57 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04807 | 100.45 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05012 | 106.3 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04988 | 105.46 | 542969 STILWEL5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.0392 | 104.68 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05012 | 103.87 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04988 | 103.08 | 543002 MARTCIT5 161 543053 REDEL 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.03951 | 102.84 | 541210 MARTCTY5 161 542993 STHTOWN5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.05012 | 102.35 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04865 | 102.1 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04988 | 101.57 | P12:161:KCPL-GMO:REDEL-MARTINCITY-MAR:::HV:
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542969 STILWEL5 161 542994 HICKMAN5 161 1 |  | 223 | 0.04864 | 100.45 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.04292 | 126.12 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.04184 | 122.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.0345 | 108.4 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.08637 | 126.12 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.08732 | 122.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07997 | 108.4 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.0638 | 126.12 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.06487 | 122.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.05752 | 108.4 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.08637 | 126.12 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.08732 | 122.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.07997 | 108.4 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.0346 | 126.12 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | FROM -> TO | 542978 CRAIG 5 161 543038 LENEXA 5 161 2 |  | 374 | 0.03634 | 122.28 | 542978 CRAIG 5 161 543038 LENEXA 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04534 | 119.37 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04146 | 115.4 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04485 | 115 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04146 | 113.1 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04085 | 111.28 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04085 | 108.89 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04857 | 107.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03916 | 104.55 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04565 | 104.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04487 | 103.58 | 543032 MERRIAM5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03916 | 101.88 | 543034 KNLWRTH5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0501 | 100.93 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03856 | 100.68 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04969 | 100.65 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04044 | 100.41 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-007 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03787 | 100.36 | 533261 PENTAGN3 115 533282 MUND 3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08647 | 119.37 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08231 | 115.4 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08807 | 115 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08231 | 113.1 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08364 | 111.28 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08364 | 108.89 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08731 | 107.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07732 | 104.55 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08656 | 104.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0851 | 103.58 | 543032 MERRIAM5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07732 | 101.88 | 543034 KNLWRTH5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08299 | 100.93 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07854 | 100.68 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08302 | 100.65 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08367 | 100.41 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-058 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07187 | 100.36 | 533261 PENTAGN3 115 533282 MUND 3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08274 | 119.37 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06023 | 115.4 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08447 | 115 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06023 | 113.1 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06168 | 111.28 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06168 | 108.89 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06564 | 107.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.05779 | 104.55 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06504 | 104.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06949 | 103.58 | 543032 MERRIAM5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.05779 | 101.88 | 543034 KNLWRTH5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0646 | 100.93 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.05912 | 100.68 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.06465 | 100.65 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08006 | 100.41 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.05175 | 100.36 | 533261 PENTAGN3 115 533282 MUND 3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08647 | 119.37 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08231 | 115.4 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08807 | 115 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08231 | 113.1 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08364 | 111.28 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08364 | 108.89 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08731 | 107.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07732 | 104.55 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08656 | 104.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0851 | 103.58 | 543032 MERRIAM5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07732 | 101.88 | 543034 KNLWRTH5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08299 | 100.93 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07854 | 100.68 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08302 | 100.65 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.08367 | 100.41 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-057 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.07187 | 100.36 | 533261 PENTAGN3 115 533282 MUND 3 115 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04081 | 119.37 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03425 | 115.4 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04323 | 115 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03425 | 113.1 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03634 | 111.28 | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03634 | 108.89 | 542979 PFLUMM 5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04089 | 107.08 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03266 | 104.55 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04104 | 104.26 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03949 | 103.58 | 543032 MERRIAM5 161 543047 OVERLPK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03266 | 101.88 | 543034 KNLWRTH5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04089 | 100.93 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 00NR | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.0346 | 100.68 | 543038 LENEXA 5 161 543052 REEDER 5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.04077 | 100.65 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 00NR | 1 | 27WP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03882 | 100.41 | 543031 SHWNMSN5 161 543049 CEDRCRK5 161 1
Thermal | 00NR | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543031 SHWNMSN5 161 543038 LENEXA 5 161 1 |  | 334 | 0.03145 | 100.36 | 533261 PENTAGN3 115 533282 MUND 3 115 1
Thermal | 00NR | 1 | 27WP | GEN-2020-079 | TO -> FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 557 | 0.85307 | 102.15 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-088 | TO -> FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 557 | 0.12014 | 102.15 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-052 | TO -> FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 557 | 0.04676 | 102.15 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-090 | TO -> FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 |  | 557 | 0.04242 | 102.15 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 00NR | 1 | 27WP | GEN-2020-002 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.14025 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-025 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-027 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-027 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-027 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-027 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-028 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-030 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-030 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-030 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-030 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-031 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-033 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.56096 | 107.75 | 646362 S1362 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-033 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | 646281 S1281 5 161 646363 S1363 5 161 1
Thermal | 00NR | 1 | 27WP | GEN-2020-033 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1281-S1362:::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-033 | TO -> FROM | 646362 S1362 5 161 646363 S1363 5 161 2 |  | 557 | 0.59285 | 100.75 | P12:161:OPPD:S1260-S1281:LS::HV:
Thermal | 00NR | 1 | 27WP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03214 | 161.14 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 27WP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03214 | 161.14 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 24SP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03184 | 146.5 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 24SP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03184 | 146.5 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 27SP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03218 | 143.93 | P21:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 00NR | 1 | 27SP | GEN-2020-006 | FROM -> TO | 661008 BEULAH 7 115 661011 BEULAH27 115 Z |  | 149 | 0.03218 | 143.93 | P12:345:OTP:AUTO-SINGLE:CENTER3:COYOTE3:1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.05449 | 100.13 | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652421 WILISTN7 115 652651 FAIRVIEW 7 115 1 |  | 119 | 0.58215 | 100.13 | P12:230:UMZ:# 20052 #:: PROPER N-1 FOR TAP MEDORA__-UM4:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 104.54 | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 104.29 | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 104.21 | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 103.96 | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 108.48 | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 108.22 | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 108.11 | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 107.86 | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 100.91 | P12:230:UMZW:# 4059 #:: OA-SB IN SD. FAULT FOR TRANSMISSION CIRCUIT (OA-SB).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1 |  | 264 | 0.99983 | 100.42 | P12:230:UMZW:# 4059 #:: OA-SB IN SD. FAULT FOR TRANSMISSION CIRCUIT (OA-SB).:HV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.7 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.33 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.7 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.34 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.7 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.33 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.7 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.33 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.7 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.34 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.7 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.33 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.7 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.33 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.7 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.34 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.7 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.33 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.7 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.33 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.7 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.34 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.7 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.33 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.7 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.33 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.7 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.34 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.7 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.33 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.29 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.66 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.29 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.66 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.29 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.66 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.29 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.66 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.29 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.66 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.29 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.66 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.29 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.66 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.29 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.66 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.29 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.66 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.29 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.66 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.29 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.66 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.29 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.66 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.29 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.66 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.29 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.66 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.29 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.66 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.88 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.88 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.88 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.88 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.88 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.88 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.88 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.88 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.88 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.88 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.88 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.88 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.88 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.88 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.88 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.49 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 100.09 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 100.1 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.5 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.49 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.49 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 100.09 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 100.1 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.5 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.49 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.49 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 100.09 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 100.1 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.5 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.49 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.49 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 100.09 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 100.1 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.5 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.49 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.49 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 100.09 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 100.1 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.5 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652506 FTTHOMP3 345 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.49 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.53 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.28 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.53 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.28 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07107 | 119.53 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.07209 | 107.27 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.53 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.28 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.53 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.28 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06214 | 119.53 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06186 | 107.27 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.53 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.28 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.53 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.28 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06305 | 119.53 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06523 | 107.27 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.23084 | 102.11 | 652506 FTTHOMP3 345 3WXFMR FT2 KU1A 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.53 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.28 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.53 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.28 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13515 | 119.53 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.13485 | 107.27 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.53 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.28 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.53 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.28 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06317 | 119.53 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996640 FT2 KU1B 230 1 |  | 313 | 0.06551 | 107.27 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.11 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.6 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.12 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.6 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07261 | 122.11 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.07365 | 109.6 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.11 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.6 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.12 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.6 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06348 | 122.11 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.0632 | 109.6 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.11 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.6 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.12 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.6 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06441 | 122.11 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06664 | 109.6 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.23235 | 102.81 | 652506 FTTHOMP3 345 3WXFMR FT2 KU1B 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.11 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.6 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.12 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.6 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13807 | 122.11 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.13777 | 109.6 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.11 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.6 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.12 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.6 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 27SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06453 | 122.11 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 27WP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996641 FT2 KU1A 230 1 |  | 313 | 0.06693 | 109.6 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.74 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.74 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.07128 | 120.74 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.74 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.74 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06281 | 120.74 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.74 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.74 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.06248 | 120.74 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.23087 | 101.3 | 652506 FTTHOMP3 345 3WXFMR FT2 KU1A 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.74 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.74 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.13552 | 120.74 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.74 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.74 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996643 FT2 KU1B 230 1 |  | 313 | 0.0629 | 120.74 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.35 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 100.12 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.35 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.07282 | 123.35 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.35 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 100.12 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.35 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06417 | 123.35 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.35 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 100.12 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.35 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06383 | 123.35 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.23239 | 102.01 | 652506 FTTHOMP3 345 3WXFMR FT2 KU1B 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.35 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 100.12 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.35 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.13845 | 123.35 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.35 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 100.26 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 100.12 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 100.26 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.35 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | FROM -> TO | 652507 FTTHOMP4 230 996644 FT2 KU1A 230 1 |  | 313 | 0.06426 | 123.35 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07288 | 106.74 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 128.3 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 117.35 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 117.2 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 117.34 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 128.31 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07491 | 128.3 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 128.3 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.37 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 117.35 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06578 | 106.74 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 117.2 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 114.73 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.38 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.38 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.05414 | 107.7 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.39 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.38 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 106.38 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 117.34 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 128.31 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 128.3 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06998 | 114.73 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.07014 | 108.89 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06431 | 107.05 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.99983 | 109.33 | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.99983 | 113.81 | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 128.3 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.37 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 117.35 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.71855 | 106.74 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 117.2 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 114.73 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.38 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.38 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 107.7 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.39 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.38 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 106.38 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 117.34 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 128.31 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 128.3 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72074 | 114.73 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72089 | 108.89 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.72098 | 107.05 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 128.3 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.37 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 117.35 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06752 | 106.74 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 117.2 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 114.73 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.38 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.38 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.05294 | 107.7 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.39 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.38 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 106.38 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 117.34 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 128.31 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 128.3 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.068 | 114.73 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06816 | 108.89 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 |  | 239 | 0.06245 | 107.05 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07288 | 114.02 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 |  | 0.03127 | 103.49 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 135.57 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 124.62 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 124.48 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 124.62 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 135.57 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07491 | 135.57 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 135.57 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.65 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 124.62 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06578 | 114.02 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 124.48 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 122.01 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.66 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.66 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.05414 | 115.02 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.66 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.66 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 113.66 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 124.62 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 135.57 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 135.57 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06998 | 122.01 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.07014 | 116.18 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06431 | 114.33 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 |  | 0.05405 | 103.49 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.99983 | 116.59 | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.99983 | 121.05 | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 135.57 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.65 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 124.62 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.71855 | 114.02 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 124.48 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 122.01 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.66 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.66 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 115.02 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.66 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.66 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 113.66 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 124.62 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 135.57 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 135.57 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72074 | 122.01 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72089 | 116.18 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.72098 | 114.33 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 |  | 0.72065 | 103.49 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 135.57 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.65 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 124.62 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06752 | 114.02 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 124.48 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 122.01 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.66 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.66 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.05294 | 115.02 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.66 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.66 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 113.66 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 124.62 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 135.57 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 135.57 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.068 | 122.01 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06816 | 116.18 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z |  | 239 | 0.06245 | 114.33 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 239 |  | 0.05284 | 103.49 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07288 | 112.52 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-006 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 | 239 |  | 0.03127 | 102.04 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 133.96 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 123.07 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 122.93 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 123.07 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 133.97 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-021 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07491 | 133.96 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 133.96 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.15 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 123.07 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06578 | 112.52 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 122.93 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 120.48 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.16 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.16 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.05414 | 113.58 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.16 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.16 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.16 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 123.07 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 133.97 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 133.96 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06998 | 120.48 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.07014 | 114.69 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06431 | 112.82 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-091 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 | 239 |  | 0.05405 | 102.04 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.99983 | 115.06 | 652426 BISMARK4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.99983 | 119.46 | 652499 CAMPBELL 4 230 659171 WINCHSTR-BE4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 133.96 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.15 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 123.07 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.71855 | 112.52 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 122.93 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 120.48 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.16 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.16 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 113.58 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.16 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.16 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.16 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 123.07 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 133.97 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 133.96 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72074 | 120.48 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72089 | 114.69 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.72098 | 112.82 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-093 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 | 239 |  | 0.72065 | 102.04 | System Intact
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 133.96 | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.15 | 659101 ANTELOPE-BE3 345 659420 AV.LS-BD-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 123.07 | 659130 CHAPELLE-BE3 345 659428 CC.LS-LO-BE3 345 Z
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06752 | 112.52 | 659351 BISON___-GE4 230 661047 HETINGR4 230 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 122.93 | 659428 CC.LS-LO-BE3 345 764220 G20-021-TAP 345 1
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 120.48 | P12:345:UMZB:# 103 #:: LOS FT IN ND. LELAND OLDS-FORT THOMPSON :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.16 | P12:345:UMZB:# 98 #:: AVS BD IN ND. ANTELOPE VALLEY-BROADLAND :EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.16 | P12:345:UMZB:# 99 #:: BD IN SD. BROADLAND-ANTELOPE VALLEY:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.05294 | 113.58 | P13:230:UMZ:# 20120 #:: PROPER N-1 FOR GLENHAM PARALLEL TRANSFORMERS:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.16 | P13:345:UMZB:# 233 #:: BD IN SD. BROADLAND TX:HV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.16 | P14:345:UMZ:# 7209 #:: PROPER TAKE LINE WITH ANTELOPE VALLEY LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.16 | P14:345:UMZ:# 7210 #:: PROPER TAKE LINE WITH BROADLAND LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 123.07 | P14:345:UMZ:# 7218 #:: PROPER TAKE LINE WITH CHAPPELLE LINE REACTOR:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 133.97 | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 133.96 | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.068 | 120.48 | P23:345:UMZB:# 7131 #:: CHA IN SD. BREAKER FAULT (4392,4496,4492):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06816 | 114.69 | P42:345:UMZB:# 2493 #:: LO IN ND. STUCK BREAKER (2596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 |  | 239 | 0.06245 | 112.82 | P42:345:UMZB:# 2503 #:: AVS IN ND. STUCK BREAKER (4596):EHV:
Thermal | 01ALL | 1 | 24SP | GEN-2020-083 | TO -> FROM | 655510 SB.LS-WK-ER4 230 655765 WHITLOCK_-RM 230 1 | 239 |  | 0.05284 | 102.04 | System Intact
Thermal | 01NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05443 | 130.63 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05724 | 115.23 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05721 | 115.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05443 | 130.63 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05724 | 115.23 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05721 | 115.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05388 | 130.13 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05666 | 115.2 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05669 | 114.83 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.06229 | 106.12 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.06421 | 101.27 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.06427 | 100.71 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.06229 | 106.12 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.06421 | 101.27 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.06427 | 100.71 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.09635 | 130.63 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09918 | 115.23 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09916 | 115.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.09635 | 130.63 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09918 | 115.23 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09916 | 115.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.09591 | 130.13 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09873 | 115.2 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-011 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.09875 | 114.83 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05121 | 106.12 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05314 | 101.27 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05319 | 100.71 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.05121 | 106.12 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05314 | 101.27 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.05319 | 100.71 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.07894 | 130.63 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08178 | 115.23 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08175 | 115.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.07894 | 130.63 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08178 | 115.23 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08175 | 115.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.0785 | 130.13 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08132 | 115.2 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.08135 | 114.83 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.15572 | 106.12 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.15757 | 101.27 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.1577 | 100.71 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.15572 | 106.12 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.15757 | 101.27 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.1577 | 100.71 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.24069 | 130.63 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24344 | 115.23 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24352 | 115.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.24069 | 130.63 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24344 | 115.23 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24352 | 115.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 319 | 0.24016 | 130.13 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24299 | 115.2 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-070 | FROM -> TO | 530582 S HAYS6 230 539679 GRTBEND6 230 1 |  | 297 | 0.24292 | 114.83 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.10218 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.10218 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.10193 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.18886 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.18886 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.18866 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.15316 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.15316 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.15296 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08335 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08335 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08319 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08112 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08112 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.08101 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.48377 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.48377 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.48353 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06157 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06157 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06149 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05848 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05848 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.0584 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05976 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05976 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.05968 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06032 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06032 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06025 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06317 | 109.6 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06317 | 109.6 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | TO -> FROM | 530583 POSTROCK7 345 997534 POSTROCK T1 230 1 |  | 600 | 0.06309 | 109.48 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.10218 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.10218 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.10193 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.18886 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.18886 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-011 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.18866 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.15316 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.15316 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.15296 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08335 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08335 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-069 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08319 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08112 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08112 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.08101 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.48377 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.48377 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-070 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.48353 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06157 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06157 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-002 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06149 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-027 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-030 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06003 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-033 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05995 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05848 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05848 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-036 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.0584 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05976 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05976 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-078 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.05968 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06032 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06032 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-084 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06025 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06317 | 110.22 | P12:345:MIDW-SUNC:POSTROCK7-SPERVIL7:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06317 | 110.22 | P23:345:ITCGP:SV_BRK382:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-094 | FROM -> TO | 530584 POSTROCK6 230 997534 POSTROCK T1 230 1 |  | 600 | 0.06309 | 110.09 | P23:345:ITCGP:SV_BRK388:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.36983 | 104.27 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.36983 | 104 | 533322 BAILEYV3 115 533337 SENECA 3 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.73018 | 102.3 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.34278 | 101.33 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.43871 | 127.47 | P12:115:WERE:KNOB-NPPD-115:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.44138 | 100.23 | P12:115:WERE:KNOB-NPPD-115:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 |  | 99 | 0.34244 | 101.83 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48365 | 103.75 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48357 | 103.2 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48618 | 122.36 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48672 | 110.89 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48405 | 106.07 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48443 | 100.84 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48338 | 101.12 | 533303 MARSHAL3 115 3WXFMR MRSHL WF 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48358 | 103.68 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48358 | 103.67 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48357 | 103.74 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48334 | 103.2 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48332 | 103.56 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48333 | 104.08 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48618 | 108.57 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48618 | 116.02 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48672 | 104.72 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.46908 | 104.1 | 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69218 | 119.6 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69218 | 110.65 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69218 | 121.93 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69218 | 118.18 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69252 | 108.23 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.69254 | 106.76 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.49218 | 106.12 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.49233 | 105.1 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 115.3 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48362 | 106.1 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.49218 | 106.61 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.49233 | 105.21 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 103.37 | 640179 GENEVA 8 69.0 3WXFMR GENEVA T2 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48381 | 105.73 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48414 | 101.03 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 137.3 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 127.01 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 121.28 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 1 | 120.95 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 104.84 | 640221 HEBRON 9 34.5 3WXFMR HEBRON T1 _1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48481 | 103.23 | 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4841 | 119.62 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48411 | 124.42 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4841 | 108.19 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48411 | 105.94 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.54931 | 102.26 | 640313 PAULINE7 115 640583 ROSEMONT 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 103.83 | 640415 CARLJCT8 69.0 3WXFMR CARLN.JCT T2 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48263 | 110.58 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48301 | 108.08 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48263 | 110.59 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48301 | 108.1 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48352 | 104.55 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48372 | 102.4 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 107.95 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48362 | 110.14 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 107.95 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48362 | 110.14 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48338 | 101.12 | P11:115:WERE:MCWF-GEN:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48362 | 101.02 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.46165 | 106.68 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.46908 | 105.07 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48122 | 107.56 | P12:161:OPPD:HUMBOLT-S1280:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 103.38 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48216 | 104.58 | P12:161:OPPD:S1280-COOPER:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 101.44 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48345 | 103.51 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 101.44 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4833 | 100.82 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48273 | 109.42 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48285 | 107.71 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48433 | 100.97 | P12:345:NPPD:LN003B::COOPER.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48627 | 115.28 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48636 | 114.06 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48346 | 103.77 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48405 | 105.99 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4846 | 112.58 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48506 | 104.02 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48381 | 105.8 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48409 | 101.59 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 103.41 | P21:161:OPPD:HUMBOLT-S1398:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48359 | 103.38 | P21:161:OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 103.4 | P21:161:OPPD:S1399-S1398:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48346 | 103.77 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48346 | 103.77 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4838 | 105.19 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48389 | 104.88 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48326 | 104.41 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48325 | 103.92 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48336 | 104.27 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48361 | 101.04 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48336 | 101.08 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48337 | 101.25 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4867 | 106.61 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48413 | 104.97 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48433 | 102.91 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48386 | 104.92 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48612 | 114.95 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4862 | 114.13 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48374 | 111.65 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48378 | 112.61 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48607 | 115.47 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48617 | 114.04 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.484 | 119.71 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48401 | 124.68 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48607 | 115.47 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48617 | 114.04 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48612 | 114.95 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.4862 | 114.13 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 |  | 99 | 0.48366 | 103.8 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 99 |  | 0.48337 | 101.11 | System Intact
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48365 | 126.47 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48423 | 108.78 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48427 | 108.88 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48357 | 125.91 | 523823 CARPENTER 7 345 523853 FINNEY 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48618 | 145.58 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48672 | 123.41 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48689 | 122.95 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48695 | 123.65 | 530583 POSTROCK7 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48405 | 128.84 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48443 | 113.22 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48467 | 109.29 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48472 | 109.39 | 531451 MINGO 7 345 531465 SETAB 7 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48254 | 109.01 | 532913 KELLY 5 161 532920 TECHILL5 161 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48282 | 104.44 | 532913 KELLY 5 161 532920 TECHILL5 161 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48225 | 121.52 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48254 | 109.02 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48282 | 104.46 | 532920 TECHILL5 161 3WXFMR TECUMSEH HILL 1 TX 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48338 | 113.76 | 533303 MARSHAL3 115 3WXFMR MRSHL WF 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48358 | 126.55 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48415 | 108.51 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48419 | 108.7 | 541197 MULLNCR7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48358 | 126.54 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48415 | 108.49 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48419 | 108.69 | 541197 MULLNCR7 345 541510 HOLT 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4836 | 125.95 | 541199 ST JOE 7 345 640139 COOPER 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48357 | 126.63 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48414 | 108.55 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48419 | 108.74 | 541201 SIBLEY 7 345 541500 KETCHEM7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48334 | 125.96 | 542955 LAC G1 1 22.0 542981 LACYGNE7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48332 | 126.32 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48388 | 108.5 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48393 | 108.55 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48333 | 126.82 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 109.1 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48393 | 109.3 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48618 | 131.39 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48689 | 110.14 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48695 | 110.21 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48618 | 139.04 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48672 | 117.18 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48689 | 117.04 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48695 | 117.46 | 560082 G16-050-TAP 345 765035 G20-070-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 108.88 | 562711 G15_023_1 345 640510 HOLT.CO3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 120.63 | 587351 G16-050XFMR1 34.5 587350 GEN-2016-050 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 107.96 | 587351 G16-050XFMR1 34.5 587350 GEN-2016-050 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.08 | 587351 G16-050XFMR1 34.5 587350 GEN-2016-050 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 103.25 | 587351 G16-050XFMR1 34.5 587350 GEN-2016-050 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 108.98 | 587680 GEN-2016-074 345 640374 SWEET W3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 108.96 | 587681 G16-074XFMR1 34.5 587680 GEN-2016-074 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4851 | 108.95 | 640065 AXTELL 3 345 640312 PAULINE3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 120.54 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.02 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 103.25 | 640075 BEAT. S9 34.5 3WXFMR BEATRICE.ST1 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47924 | 108.34 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47929 | 108.55 | 640076 BEATRCE7 115 640088 BPS SUB7 115 2
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.29158 | 118.81 | 640076 BEATRCE7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.29163 | 119.5 | 640076 BEATRCE7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.46908 | 126.95 | 640088 BPS SUB7 115 640111 CLATONA7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69218 | 133.34 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69218 | 132.13 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69252 | 124.44 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69254 | 123.23 | 640105 CARLJCT7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69218 | 140.96 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69218 | 134.51 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69252 | 137.75 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.69254 | 136.62 | 640105 CARLJCT7 115 640218 HEBRN N7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49218 | 128.87 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49233 | 117.48 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49277 | 108.74 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49282 | 108.95 | 640153 CRETE__7 115 640174 FRIEND 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 115.49 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 106.32 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49218 | 129.36 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49233 | 117.58 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49277 | 109.54 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49282 | 109.74 | 640174 FRIEND 7 115 640178 GENEVA 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.49046 | 104.21 | 640178 GENEVA 7 115 640372 SUTTON 7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 126.05 | 640179 GENEVA 8 69.0 3WXFMR GENEVA T2 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 110.32 | 640179 GENEVA 8 69.0 3WXFMR GENEVA T2 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 110.5 | 640179 GENEVA 8 69.0 3WXFMR GENEVA T2 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 128.5 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48414 | 113.43 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48441 | 110.19 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48446 | 110.47 | 640183 GENTLMN3 345 640325 REDWILO3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.54986 | 108.49 | 640206 GUIDE R7 115 640368 SUPEROR7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.55003 | 110.15 | 640218 HEBRN N7 115 640220 HEBRON 7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.55007 | 110.18 | 640218 HEBRN N7 115 640220 HEBRON 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.96 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.95 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.81 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.81 | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 127.5 | 640221 HEBRON 9 34.5 3WXFMR HEBRON T1 _1 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 109.68 | 640221 HEBRON 9 34.5 3WXFMR HEBRON T1 _1 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 109.84 | 640221 HEBRON 9 34.5 3WXFMR HEBRON T1 _1 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48366 | 109.01 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48481 | 125.99 | 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48536 | 108.99 | 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4854 | 109.15 | 640272 MCCOOL 7 115 640413 YORK SW7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4841 | 142.25 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48411 | 136.7 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48466 | 121.04 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48471 | 121.17 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4841 | 130.91 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48411 | 118.27 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48466 | 111.19 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48471 | 111.33 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.54921 | 121.69 | 640313 PAULINE7 115 640583 ROSEMONT 7 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.54931 | 114.59 | 640313 PAULINE7 115 640583 ROSEMONT 7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 108.61 | 640373 SUTTON 8 69.0 3WXFMR SUTTON T1 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 108.8 | 640373 SUTTON 8 69.0 3WXFMR SUTTON T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 126.59 | 640415 CARLJCT8 69.0 3WXFMR CARLN.JCT T2 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 111.06 | 640415 CARLJCT8 69.0 3WXFMR CARLN.JCT T2 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 111.28 | 640415 CARLJCT8 69.0 3WXFMR CARLN.JCT T2 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48263 | 123.83 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48301 | 131.4 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48379 | 109.44 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48383 | 109.52 | 640426 STEELEC7 115 640558 S.FLATS.PLT7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.46 | 640427 STEELEC9 4.16 640426 STEELEC7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48437 | 121.72 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4847 | 107.85 | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48263 | 123.84 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48301 | 131.42 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48379 | 109.45 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48383 | 109.52 | 640558 S.FLATS.PLT7 115 3WXFMR STL.FLTS GSU 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 108.43 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48351 | 118.84 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 106.71 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48405 | 101.47 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48409 | 101.78 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 108.84 | 763406 GEN-2018-125 345 763410 G18-125-TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 108.84 | 763407 G18-125-XFM1 34.5 763406 GEN-2018-125 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.81 | 763659 GEN-2019-029 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 107.79 | 763659 GEN-2019-029 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.63 | 764255 GEN-2020-001 230 764265 G20-001-TAP 230 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 104.12 | 764255 GEN-2020-001 230 764265 G20-001-TAP 230 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.28 | 764255 GEN-2020-001 230 764265 G20-001-TAP 230 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.63 | 764258 G20-001-XFM1 34.5 764255 GEN-2020-001 230 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 104.12 | 764258 G20-001-XFM1 34.5 764255 GEN-2020-001 230 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.28 | 764258 G20-001-XFM1 34.5 764255 GEN-2020-001 230 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 119.05 | 764420 GEN-2020-011 345 764430 G20-011-TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 101.51 | 764420 GEN-2020-011 345 764430 G20-011-TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 101.68 | 764420 GEN-2020-011 345 764430 G20-011-TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 119.6 | 764435 GEN-2020-013 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 101.93 | 764435 GEN-2020-013 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 102.12 | 764435 GEN-2020-013 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48352 | 127.26 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48372 | 114.79 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4841 | 109.3 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48414 | 109.63 | 9980 UTICAJC3 345 9999 WHST3 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 131.13 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 123.25 | P11:1:NPPD:S.FLATS.:W:83::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 131.13 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 123.25 | P11:1:NPPD:S.FLATS.GENW:W:83::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48338 | 113.76 | P11:115:WERE:MCWF-GEN:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48378 | 111.19 | P11:14:NPPD:BPS GT1G:1:90::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48382 | 111.28 | P11:14:NPPD:BPS GT1G:1:90::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48378 | 111.19 | P11:14:NPPD:BPS GT2G:2:90::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48382 | 111.28 | P11:14:NPPD:BPS GT2G:2:90::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48376 | 111.8 | P11:14:NPPD:BPS ST3G:3:110::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 111.89 | P11:14:NPPD:BPS ST3G:3:110::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.8 | P11:20:OTP:AUTO-SINGLE:CENTER2G:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.1 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 109.01 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.65 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 103.82 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.09 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.64 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 103.8 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48384 | 109.6 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 109.77 | P11:230:WERE:JECU1-GEN:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.45 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.79 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.43 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.79 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.43 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.23 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.72 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 103.86 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48385 | 109.52 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 109.6 | P11:345:WERE:JECU2-GEN:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48385 | 109.44 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 109.64 | P11:345:WERE:JECU3-GEN:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48362 | 113.51 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 109.56 | P11:345:WERE:WOLFU1-GEN:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.55003 | 110.31 | P12:115:NPPD:1173:SUPEROR7-HEBRN N7:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.55007 | 110.36 | P12:115:NPPD:1173:SUPEROR7-HEBRN N7:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.46165 | 129.66 | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.46908 | 127.95 | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48122 | 130.31 | P12:161:OPPD:HUMBOLT-S1280:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48182 | 112.47 | P12:161:OPPD:HUMBOLT-S1280:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48186 | 112.74 | P12:161:OPPD:HUMBOLT-S1280:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 126.28 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48418 | 108.78 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48422 | 109.14 | P12:161:OPPD:HUMBOLT-S1398-S1399:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48216 | 127.31 | P12:161:OPPD:S1280-COOPER:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48272 | 109.49 | P12:161:OPPD:S1280-COOPER:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48276 | 109.57 | P12:161:OPPD:S1280-COOPER:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48278 | 108.38 | P12:161:WERE:TECH-KELL-OPPD-161:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48282 | 108.54 | P12:161:WERE:TECH-KELL-OPPD-161:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48278 | 108.37 | P12:161:WERE-OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48282 | 108.53 | P12:161:WERE-OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 113.88 | P12:230:MIDW-WERE:SMOKYHL6-SUMMIT6:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48345 | 126.27 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 113.88 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48402 | 108.49 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48406 | 108.56 | P12:230:WERE:SUMM-MWE-230:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48273 | 132.12 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48285 | 120.06 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48336 | 112.34 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48342 | 112.62 | P12:345:NPPD:LN003A::MOORE.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48433 | 113.46 | P12:345:NPPD:LN003B::COOPER.MONOLITH.CKT1::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48627 | 127.8 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48636 | 136.77 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48705 | 115.72 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48711 | 115.9 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48346 | 126.47 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48403 | 108.66 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48407 | 108.85 | P12:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48405 | 128.77 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48443 | 113.18 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48467 | 109.26 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4846 | 135.53 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48506 | 116.47 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48528 | 114.3 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48533 | 114.67 | P12:345:SUNC-NPPD:MINGO-REDWILLOW::531451-640325(1):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47663 | 121.64 | P13:115-161:NPPD:HUMBOLDT T2:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47696 | 107.14 | P13:115-161:NPPD:HUMBOLDT T2:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47722 | 102.52 | P13:115-161:NPPD:HUMBOLDT T2:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.47726 | 102.69 | P13:115-161:NPPD:HUMBOLDT T2:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.29 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.83 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.29 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.83 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 128.6 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48409 | 113.99 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48439 | 110.55 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48443 | 110.75 | P13:230-345:MIDW:POST ROCK:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 121.37 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 103.87 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48396 | 104.01 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 126.31 | P21:161:OPPD:HUMBOLT-S1398:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48418 | 108.81 | P21:161:OPPD:HUMBOLT-S1398:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48422 | 109.16 | P21:161:OPPD:HUMBOLT-S1398:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48359 | 126.43 | P21:161:OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48417 | 108.8 | P21:161:OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48422 | 109.2 | P21:161:OPPD:S1399-KELLY:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 126.3 | P21:161:OPPD:S1399-S1398:::HV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48418 | 108.8 | P21:161:OPPD:S1399-S1398:::HV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48422 | 109.15 | P21:161:OPPD:S1399-S1398:::HV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48437 | 121.65 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4847 | 107.79 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48487 | 103.66 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4849 | 103.8 | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48346 | 126.47 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48403 | 108.66 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48407 | 108.85 | P22:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48346 | 126.47 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48403 | 108.66 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48407 | 108.85 | P23:345:OPPD:S3458-COOPER:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4838 | 127.92 | P23:345:SUNC:HLC_BRK188:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48389 | 127.59 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48437 | 121.65 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4847 | 107.8 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48487 | 103.66 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4849 | 103.8 | P23:345:UMZW:# 2432 #:: GI IN NE. GI 1092 BKR FAULT:EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48326 | 127.26 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48384 | 109.53 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48388 | 109.63 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48325 | 126.76 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 109.19 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48385 | 109.4 | P23:345:WERE:JEC-345-20:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48252 | 120.81 | P23:345:WERE:SUMM-345-218:::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48336 | 127.1 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48361 | 113.54 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48392 | 109.07 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48395 | 109.47 | P23:345:WERE:WOLF-345-50:::EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48336 | 113.39 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48337 | 113.55 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4867 | 129.43 | P42:345:NPPD:BKR-AXT-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48413 | 127.64 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48433 | 115.26 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4847 | 109.31 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48476 | 109.56 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48386 | 127.67 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48446 | 109.48 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4845 | 109.79 | P42:345:NPPD:BKR-GGS-3322::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48612 | 127.46 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4862 | 136.86 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48689 | 115.75 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48695 | 115.99 | P42:345:NPPD:BKR-MOR-3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48374 | 134.3 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48378 | 125.01 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48438 | 113.74 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48445 | 113.94 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+):::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48607 | 127.98 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48617 | 136.75 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48687 | 115.5 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48693 | 115.73 | P42:345:NPPD:BKR-MOR-3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.484 | 142.36 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48401 | 136.96 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48457 | 121.03 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48462 | 121.17 | P42:345:NPPD:BKR-MOR-3312::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48607 | 127.98 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48617 | 136.75 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48687 | 115.5 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48693 | 115.73 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310::::
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48612 | 127.46 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.4862 | 136.86 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48689 | 115.75 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48695 | 115.99 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306::::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48366 | 126.53 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48424 | 108.45 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48428 | 108.54 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48352 | 118.86 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48381 | 106.74 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48405 | 101.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 |  | 99 | 0.48409 | 101.79 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 99 |  | 0.48337 | 123.83 | System Intact
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 99 |  | 0.48362 | 111.03 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 99 |  | 0.48392 | 106.27 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | FROM -> TO | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1 | 99 |  | 0.48396 | 106.46 | System Intact
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 135.97 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 126.5 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 119.35 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 118.13 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.77 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.77 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.75 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.74 | 640169 FAIRBRY7 115 764490 G20-077-TAP 115 1
Thermal | 02ALL | 1 | 27L | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.62 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 24SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.6 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27SP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.59 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2020-077 | TO -> FROM | 640218 HEBRN N7 115 764490 G20-077-TAP 115 1 |  | 99 | 1 | 149.59 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB::
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.69 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.67 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.64 | 640310 ORLEANS7 115 764445 G20-013-TAP 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.5 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.49 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 1 | 175.46 | 640311 ORLEANS8 69.0 3WXFMR ORLEANS T1 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.7 | 764438 G20-013-XFM1 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.1 | 764438 G20-013-XFM1 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.05 | 764438 G20-013-XFM1 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.7 | 764441 G20-013-XFM2 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.1 | 764441 G20-013-XFM2 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.05 | 764441 G20-013-XFM2 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 105.7 | 764444 G20-013-XFM3 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.1 | 764444 G20-013-XFM3 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 104.05 | 764444 G20-013-XFM3 34.5 764435 GEN-2020-013 115 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.99988 | 161.97 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 160.56 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 |  | 120 | 0.9999 | 160.54 | P11:69:NPPD:ORLEANS8:2:4::
Thermal | 02ALL | 1 | 27WP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 |  | 0.99988 | 164.2 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 |  | 0.9999 | 162.64 | System Intact
Thermal | 02ALL | 1 | 24SP | GEN-2020-013 | TO -> FROM | 640224 HOLDREG7 115 764445 G20-013-TAP 115 1 | 120 |  | 0.9999 | 162.58 | System Intact
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO -> FROM | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 |  | 91 | 0.1094 | 123.18 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO -> FROM | 653312 MORRILL7 115 659821 GERINGT_-TS7 115 1 |  | 91 | 0.1095 | 120.36 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV:
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | FROM -> TO | 659133 SIDNEY__-MB3 345 996549 SDQ KV2A 230 1 |  | 500 | 0.68682 | 108.67 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | FROM -> TO | 659133 SIDNEY__-MB3 345 996549 SDQ KV2A 230 1 |  | 496 | 0.68873 | 117.16 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-069 | FROM -> TO | 659133 SIDNEY__-MB3 345 996549 SDQ KV2A 230 1 |  | 496 | 0.051 | 117.16 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | FROM -> TO | 659133 SIDNEY__-MB3 345 996552 SDQ KV2A 230 1 |  | 496 | 0.68908 | 119 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-069 | FROM -> TO | 659133 SIDNEY__-MB3 345 996552 SDQ KV2A 230 1 |  | 496 | 0.05138 | 119 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27WP | GEN-2020-001 | TO -> FROM | 659210 SIDNEY__-MB4 230 996549 SDQ KV2A 230 1 |  | 500 | 0.68682 | 109.29 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-001 | TO -> FROM | 659210 SIDNEY__-MB4 230 996549 SDQ KV2A 230 1 |  | 496 | 0.68873 | 117.75 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 27SP | GEN-2020-069 | TO -> FROM | 659210 SIDNEY__-MB4 230 996549 SDQ KV2A 230 1 |  | 496 | 0.051 | 117.75 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-001 | TO -> FROM | 659210 SIDNEY__-MB4 230 996552 SDQ KV2A 230 1 |  | 496 | 0.68908 | 119.63 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02ALL | 1 | 24SP | GEN-2020-069 | TO -> FROM | 659210 SIDNEY__-MB4 230 996552 SDQ KV2A 230 1 |  | 496 | 0.05138 | 119.63 | 640252 KEYSTON3 345 763666 G19-029 TAP 345 1
Thermal | 02NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 27WP | GEN-2020-079 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.05567 | 104.17 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-079 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.05533 | 103.91 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-079 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.06087 | 108.76 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.21095 | 104.17 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.21063 | 103.91 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | TO -> FROM | 505492 SPRGFLD5 161 547479 LAR382 5 161 1 |  | 167 | 0.30678 | 108.76 | 547479 LAR382 5 161 547480 MON383 5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03021 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-088 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03135 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03008 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05471 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05397 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05212 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.0364 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03834 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-072 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03707 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19303 | 108.87 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19181 | 105.38 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19483 | 108.95 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19389 | 109.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19271 | 106.29 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.23817 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.23665 | 121.59 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19382 | 109.31 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19234 | 104.85 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.23725 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19025 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.18878 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.18797 | 104.5 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25428 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19607 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19449 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.23725 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19025 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.18878 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.23725 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19025 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.18878 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24902 | 127.18 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19907 | 109.65 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.1979 | 104.99 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25263 | 131.05 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.20123 | 112.5 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.20014 | 108.06 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.2396 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25428 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.47447 | 162.36 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31645 | 119.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31632 | 115.49 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25428 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19607 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19449 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.35823 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.26767 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.26581 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.24289 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19405 | 109.28 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19257 | 104.83 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19227 | 104.35 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25512 | 126.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.25357 | 131.87 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.20174 | 113.02 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.20068 | 108.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.4745 | 162.47 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31679 | 120.22 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.31667 | 115.91 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19026 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.18878 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19405 | 109.28 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19257 | 104.83 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.19371 | 108.83 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.23748 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.19011 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.18884 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05374 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05221 | 121.59 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05433 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05275 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06117 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05433 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05275 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08205 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06437 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06251 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05528 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.05338 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04483 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04355 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05115 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0593 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05362 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05215 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06498 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05241 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05083 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0593 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05362 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05215 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0593 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05362 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05215 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05186 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06498 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06498 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05241 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05083 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07743 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06388 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06202 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05046 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05363 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05215 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.05089 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04494 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04367 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03054 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05374 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05221 | 121.59 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05433 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05275 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06348 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05527 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06117 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07149 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05433 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05275 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.08205 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06437 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06251 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05425 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05528 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0538 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.05338 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04483 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04355 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74422 | 108.87 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.743 | 105.38 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74483 | 108.95 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74492 | 109.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74374 | 106.29 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76712 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7656 | 121.59 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74439 | 109.31 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74292 | 104.85 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73718 | 104.5 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74255 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74097 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77059 | 127.18 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74546 | 109.65 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74429 | 104.99 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77275 | 131.05 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74685 | 112.5 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74576 | 108.06 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76724 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85974 | 162.36 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7883 | 119.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78817 | 115.49 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74255 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74097 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77881 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74211 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74026 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74455 | 109.28 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74307 | 104.83 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74291 | 104.35 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77213 | 126.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77336 | 131.87 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74719 | 113.02 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74613 | 108.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85974 | 162.47 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78846 | 120.22 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78833 | 115.91 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73504 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74455 | 109.28 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74307 | 104.83 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74435 | 108.83 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.76605 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.74205 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.74078 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74422 | 108.87 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.743 | 105.38 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74483 | 108.95 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74492 | 109.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74374 | 106.29 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76712 | 123.78 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7656 | 121.59 | 300739 7BLACKBERRY 345 532797 WOLFCRK7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74439 | 109.31 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74292 | 104.85 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 125.71 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73718 | 104.5 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74255 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74097 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 126.65 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.75895 | 125.72 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73503 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.57 | 533623 ATHENS 2 69.0 533631 CC4VERN2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.76 | 533626 BURLJCT2 69.0 533630 CC3WEST2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 126.05 | 533626 BURLJCT2 69.0 533653 WOLFCRK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.71 | 533630 CC3WEST2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 125.61 | 533631 CC4VERN2 69.0 533636 GREEN 2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77059 | 127.18 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74546 | 109.65 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74429 | 104.99 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77275 | 131.05 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74685 | 112.5 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74576 | 108.06 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76724 | 125.89 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 127.19 | 542981 LACYGNE7 345 760921 G17-209-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85974 | 162.36 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.7883 | 119.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78817 | 115.49 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77027 | 131.54 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74255 | 110.14 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74097 | 106.11 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77881 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74211 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74026 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.76879 | 126.04 | P12:69:WERE:ATHE-WOLF-69:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74455 | 109.28 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74307 | 104.83 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74291 | 104.35 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77213 | 126.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.77336 | 131.87 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74719 | 113.02 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74613 | 108.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.85974 | 162.47 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78846 | 120.22 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.78833 | 115.91 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73504 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.73356 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74455 | 109.28 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74307 | 104.83 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.74435 | 108.83 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.76605 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.74205 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.74078 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05129 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0552 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05334 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03583 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.04065 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03938 | 102.29 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05576 | 108.87 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05454 | 105.38 | 300045 7MORGAN 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05747 | 108.95 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05684 | 109.56 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05566 | 106.29 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05997 | 109.31 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0585 | 104.85 | 510380 DELWARE7 345 765110 G20-052-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05436 | 109.48 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05289 | 104.56 | 532768 EMPEC 7 345 532803 BURNS 7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05102 | 104.5 | 532771 RENO 7 345 587884 G16-111-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.12574 | 134.5 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09696 | 111.79 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.09538 | 107.77 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05436 | 110.4 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05289 | 105.57 | 532796 WICHITA7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05436 | 109.48 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05289 | 104.54 | 532803 BURNS 7 345 562476 G14_001T 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05703 | 127.18 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06128 | 109.65 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06011 | 104.99 | 542965 W.GRDNR7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05959 | 131.05 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0631 | 112.5 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06202 | 108.06 | 542968 STILWEL7 345 542981 LACYGNE7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06632 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.07051 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06865 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06036 | 109.28 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05889 | 104.83 | P23:345:AEPW:DELAWARE CB 3405A NBTB::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05815 | 104.35 | P23:345:AEPW:NES CB 3441A NBTB::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0631 | 126.21 | P23:345:KCPL:WGARDNER-R10-12:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06029 | 131.87 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06356 | 113.02 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0625 | 108.63 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05437 | 109.36 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05289 | 104.56 | P23:345:WERE:EMPR-345-300:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.06036 | 109.28 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05889 | 104.83 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT::::
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05959 | 108.83 | P42:345:AEPW:NES CB 3445A NBTB+FAULT::::
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.0469 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.05244 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.05117 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05813 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05588 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27WP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05402 | 123.47 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03858 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03961 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | ASGI-2020-002 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03834 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | ASGI-2020-001 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.0552 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 27SP | ASGI-2020-001 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05125 | 129.71 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-001 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03643 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | ASGI-2020-001 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03618 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | ASGI-2020-001 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03491 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | ASGI-2020-003 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 |  | 956 | 0.05257 | 159.93 | P12:345:WERE:ROSE-WOLF-345:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-003 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03457 | 123.35 | System Intact
Thermal | 03ALL | 1 | 27SP | ASGI-2020-003 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03393 | 106.79 | System Intact
Thermal | 03ALL | 1 | 27WP | ASGI-2020-003 | TO -> FROM | 532791 BENTON 7 345 765155 G20-076-TAP 345 1 | 956 |  | 0.03266 | 102.29 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-072 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05492 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.3609 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.48164 | 104.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.48163 | 104.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.08416 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.07868 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.08416 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.41305 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12066 | 104.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12065 | 104.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.41305 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12066 | 104.76 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.12065 | 104.69 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.06245 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-002 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05851 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-001 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05586 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-003 | TO -> FROM | 532794 ROSEHIL7 345 532797 WOLFCRK7 345 1 |  | 1016 | 0.05337 | 130.95 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10784 | 113.11 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10841 | 112.55 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10723 | 110.03 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10781 | 113.41 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10837 | 112.93 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.10717 | 110.24 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.56419 | 113.11 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.56393 | 112.55 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.56357 | 110.03 | 532930 JAYHAWK5 161 532934 MARMTNE5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.56415 | 113.41 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.5639 | 112.93 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM -> TO | 532934 MARMTNE5 161 532935 MARMTNW5 161 Z1 |  | 189 | 0.56351 | 110.24 | 532930 JAYHAWK5 161 532938 FRANKLIN5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.0301 | 101.42 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.13035 | 110.69 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.12839 | 104.51 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23847 | 101.39 | 542969 STILWEL5 161 543057 BUCYRUS5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23847 | 104.55 | 543057 BUCYRUS5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23847 | 105.66 | 543067 CENTENL5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23847 | 108.94 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23885 | 101.72 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.13035 | 105.28 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.23847 | 103.48 | P12:161:KCPL:STILWELL-BUCYRUS-NLOUISBUR:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.1224 | 101.42 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.12178 | 101.28 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.0301 | 101.42 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.62933 | 110.69 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.63069 | 104.51 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73878 | 101.39 | 542969 STILWEL5 161 543057 BUCYRUS5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73878 | 104.55 | 543057 BUCYRUS5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99977 | 107.36 | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99977 | 107.35 | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73878 | 105.66 | 543067 CENTENL5 161 543068 WAGSTAF5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73878 | 108.94 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.7383 | 101.72 | 543067 CENTENL5 161 543069 PAOLA 5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.62933 | 105.28 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.73878 | 103.48 | P12:161:KCPL:STILWELL-BUCYRUS-NLOUISBUR:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.63239 | 101.42 | System Intact
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 532934 MARMTNE5 161 543650 DAKOTA_5 161 1 | 250 |  | 0.63298 | 101.28 | System Intact
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10798 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09542 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09984 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08737 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-007 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09186 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.1516 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.14884 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10871 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10608 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-058 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.11056 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09002 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08831 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09173 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08988 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09436 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05326 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27WP | GEN-2020-052 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05238 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.1516 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.14884 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10871 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.10608 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-057 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.11056 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05753 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.055 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07518 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07243 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-071 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07691 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06301 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05614 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06226 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0553 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-076 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05979 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06301 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05614 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06226 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0553 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-086 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.05979 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06391 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06516 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06138 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06251 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.06699 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08882 | 105.49 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.09015 | 102.08 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.07987 | 113.18 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.08112 | 111.07 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-090 | FROM -> TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 |  | 717 | 0.0856 | 104.27 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV:
Thermal | 03ALL | 1 | 24SP | ASGI-2020-002 | TO -> FROM | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1 |  | 74 | 1 | 108.57 | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1
Thermal | 03ALL | 1 | 27SP | ASGI-2020-002 | TO -> FROM | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1 |  | 74 | 1 | 108.39 | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1
Thermal | 03ALL | 1 | 24SP | ASGI-2020-002 | FROM -> TO | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1 |  | 74 | 1 | 108.59 | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1
Thermal | 03ALL | 1 | 27SP | ASGI-2020-002 | FROM -> TO | 541300 POSTOAK2 69.0 541301 CLNTPLT2 69.0 1 |  | 74 | 1 | 108.38 | 541268 WBURGP 2 69.0 541300 POSTOAK2 69.0 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06764 | 122.93 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.067 | 122.63 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.15158 | 122.93 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.15114 | 122.63 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.06764 | 122.93 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | FROM -> TO | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 |  | 334 | 0.067 | 122.63 | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-079 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05205 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11601 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11905 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.12032 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10827 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.1263 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11305 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11523 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09885 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11103 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09977 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09108 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08056 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10459 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11905 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09676 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08646 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0962 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.12943 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.1153 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.12561 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11494 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09769 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.37002 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38708 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3867 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38425 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.39195 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38923 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38203 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3654 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38841 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3862 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.45155 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.44935 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.37135 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38708 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3487 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34671 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34391 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.39008 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38766 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.57552 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.57361 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-058 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34963 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06197 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06433 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06258 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06378 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06186 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06225 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06278 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06123 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10572 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06197 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06158 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06005 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.15211 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.15084 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05267 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06071 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06431 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06186 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06582 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05939 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05059 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05409 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05756 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0546 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05147 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06314 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06695 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06336 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-052 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06677 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.37002 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38708 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3867 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38425 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.39195 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38923 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38203 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3654 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38841 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3862 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.45155 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.44935 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.37135 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38708 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.3487 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34671 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34391 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.39008 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.38766 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.57552 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.57361 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-057 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.34963 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0541 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05119 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05435 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05156 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05297 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0506 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08975 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08737 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0541 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0542 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05192 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0711 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05317 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05055 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-071 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05513 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10819 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0609 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06811 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06158 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07127 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06408 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0652 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05508 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06328 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05717 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05869 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05282 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05904 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0609 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06216 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05643 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.064 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07261 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06502 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05125 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06308 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10819 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0609 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06811 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06158 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07127 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06408 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0652 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05508 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06328 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05717 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05869 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05282 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05904 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0609 | 100.44 | 760921 G17-209-TAP 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06216 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05643 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.064 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07261 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06502 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05125 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06308 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05253 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05357 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05108 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05224 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05164 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05193 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.05061 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0519 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06346 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.06466 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0896 | 100.2 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.1765 | 103.04 | 532793 NEOSHO 7 345 765200 G20-090-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10309 | 103.67 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10425 | 101.5 | 541198 PECULR 7 345 541200 PHILL 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.1071 | 107.57 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10834 | 105.05 | 541198 PECULR 7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09955 | 100.12 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08542 | 101.25 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.0937 | 103.04 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09489 | 100.28 | 542965 W.GRDNR7 345 3WXFMR WEST GARDN11 11
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07371 | 107.47 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07475 | 105.5 | 542965 W.GRDNR7 345 542968 STILWEL7 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.09078 | 101.53 | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08 | 104.08 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08109 | 102.45 | P12:345:WERE:HOYT-JEC-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.07851 | 100.62 | P12:345:WERE:HOYT-STRA-345:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.10974 | 109.04 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11051 | 106.13 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11441 | 106.21 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.11577 | 103.89 | P23:345:KCPL-WERE:241WGARDNER-R12-13:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-090 | TO -> FROM | 542977 CRAIG 7 345 765125 G20-057-TAP 345 1 |  | 1195 | 0.08093 | 100.99 | P23:345:WERE:JEC-345-16:::EHV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-007 | TO -> FROM | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 |  | 1195 | 0.61234 | 113.74 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-076 | TO -> FROM | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 |  | 1195 | 0.55585 | 113.74 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-086 | TO -> FROM | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1 |  | 1195 | 0.55585 | 113.74 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | FROM -> TO | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 |  | 255 | 0.99977 | 108.97 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | FROM -> TO | 543065 CNTRVIL5 161 543069 PAOLA 5 161 1 |  | 255 | 0.99977 | 108.81 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99977 | 107.19 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543065 CNTRVIL5 161 543650 DAKOTA_5 161 1 |  | 281 | 0.99977 | 107.14 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | FROM -> TO | 543066 S.OTTWA5 161 543069 PAOLA 5 161 1 |  | 167 | 0.9992 | 100.97 | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.73751 | 122.39 | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.73751 | 111.2 | 543077 PLSTVAL5 161 764400 G20-073-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-073 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.36637 | 175.03 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-073 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.36711 | 151.39 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-073 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.3667 | 147.38 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.33974 | 122.39 | 542966 WGARDNR5 161 543077 PLSTVAL5 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.33974 | 111.2 | 543077 PLSTVAL5 161 764400 G20-073-TAP 161 1
Thermal | 03ALL | 1 | 27SP | GEN-2020-089 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.69748 | 175.03 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-089 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.69822 | 151.39 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 24SP | GEN-2020-089 | TO -> FROM | 543067 CENTENL5 161 543069 PAOLA 5 161 1 |  | 167 | 0.6978 | 147.38 | P12:161:WERE:MARM-KCPL-161:::HV:
Thermal | 03ALL | 1 | 27WP | GEN-2020-088 | FROM -> TO | 547479 LAR382 5 161 547480 MON383 5 161 1 |  | 223 | 0.40882 | 103.46 | 505492 SPRGFLD5 161 547479 LAR382 5 161 1
Thermal | 03ALL | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 03NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08165 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08165 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.17533 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.17533 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2613 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2613 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2613 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.2613 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07799 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07799 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07858 | 111.93 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07858 | 111.93 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08313 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08313 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.17684 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.17684 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26287 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26287 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26287 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.26287 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07962 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.07962 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05047 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05047 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08021 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.08021 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05047 | 105.35 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 970 | 0.05047 | 105.35 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.08147 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.08147 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.17517 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-020 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.17517 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.2612 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-054 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.2612 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.2612 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-055 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.2612 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07795 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07795 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07854 | 107.41 | P23:345:AEPW:WELSH CB 11990 NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 508359 WELSH 7 345 508841 WILKES 7 345 1 |  | 1220 | 0.07854 | 107.41 | P42:345:AEPW:WELSH CB 11990 NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-092 | TO -> FROM | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 |  | 188 | 0.24918 | 119.38 | 510419 PRY-JCT4 138 764160 G20-092-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.23419 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17571 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17571 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17571 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.1777 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.1777 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.1777 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.1995 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14956 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14956 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14956 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10533 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10533 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10533 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.09045 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.61611 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29173 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29173 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29173 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.68387 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.0704 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.0704 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.0704 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.61611 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28645 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28645 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28645 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.68387 | 110.95 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.6 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.55 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.60722 | 101.48 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.23428 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17727 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17727 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17727 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17495 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17495 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.17495 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.19714 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14817 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14817 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.14817 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10169 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10169 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.10169 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.08701 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.62071 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29225 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29225 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.29225 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.68906 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.06727 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.06727 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.06727 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.62071 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28684 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28684 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.28684 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.68906 | 110.96 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.45 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.43 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 515800 GRACMNT7 345 1 |  | 1541 | 0.6149 | 104.39 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.23419 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.1995 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.61611 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.68387 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.61611 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.68387 | 102.84 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.23428 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.19714 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.62071 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.68906 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.62071 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.68906 | 102.76 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.18123 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.18123 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.18123 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.19202 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.19202 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.19202 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.16654 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.16654 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.16654 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.11279 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.11279 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.11279 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.0965 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.29515 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.29515 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.29515 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.07473 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.07473 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.07473 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.28946 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.28946 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.28946 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.88 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.76 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511409 TREASILD7 345 764550 G20-075-TAP 345 1 |  | 1176 | 0.65304 | 101.68 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.06317 | 116.31 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.06143 | 113.43 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11477 | 116.31 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11045 | 113.43 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.22225 | 116.31 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.21276 | 113.43 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11237 | 116.31 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.10816 | 113.43 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.22225 | 116.31 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.21276 | 113.43 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.06242 | 113.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.06117 | 109.24 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11468 | 113.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11062 | 109.24 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.22252 | 113.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.2128 | 109.24 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.11226 | 113.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.10833 | 109.24 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.22252 | 113.13 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511467 L.E.S.-4 138 997967 LES 5 138 2 |  | 515 | 0.2128 | 109.24 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.39 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.39 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.57 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 132.57 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1549 | 1 | 111.27 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1 |  | 1549 | 1 | 111.27 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.8 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.74 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.8 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.74 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.93 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.93 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 764550 G20-075-TAP 345 1 |  | 1176 | 1 | 101.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.06317 | 116.15 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.06143 | 112.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11477 | 116.15 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11045 | 112.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.22225 | 116.15 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.21276 | 112.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11237 | 116.15 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.10816 | 112.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.22225 | 116.15 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.21276 | 112.84 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.06242 | 112.89 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.06117 | 108.95 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11468 | 112.89 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11062 | 108.95 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.22252 | 112.89 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.2128 | 108.95 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.11226 | 112.89 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.10833 | 108.95 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.22252 | 112.89 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 511468 L.E.S.-7 345 997967 LES 5 138 2 |  | 515 | 0.2128 | 108.95 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.27 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.27 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.42 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1 |  | 1301 | 1 | 113.42 | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28888 | 123.61 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28888 | 123.61 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.43 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.23254 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.23254 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.085 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.085 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.1249 | 123.61 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.1249 | 123.61 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.43 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09732 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09732 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.05123 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.05123 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12667 | 123.61 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12667 | 123.61 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.48 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.48 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.48 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.48 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.43 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09883 | 108.45 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09883 | 108.45 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28986 | 124.27 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28986 | 124.27 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.82 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.82 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.81 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.81 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.69 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.23322 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.23322 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.08521 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.08521 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12592 | 124.27 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12592 | 124.27 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.82 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.82 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.81 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.81 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.69 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09813 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09813 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.05125 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.05125 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12775 | 124.27 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12775 | 124.27 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.82 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.82 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.81 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.81 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.69 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09969 | 110.6 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.09969 | 110.6 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28953 | 116.7 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28953 | 116.7 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.17 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.17 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.17 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.17 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.11 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12559 | 116.7 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12559 | 116.7 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.17 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.17 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.17 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.17 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.11 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12742 | 116.7 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12742 | 116.7 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.17 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.17 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.17 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.17 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514808 JOHNCO 4 138 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.11 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28888 | 123.23 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28888 | 123.23 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.05 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.05 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.05 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 122.05 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28459 | 121.94 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.23254 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.23254 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.085 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-020 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.085 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-054 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-055 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.06996 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.1249 | 123.23 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.1249 | 123.23 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.05 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.05 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.05 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 122.05 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12092 | 121.94 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09732 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09732 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.05123 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-081 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.05123 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12667 | 123.23 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12667 | 123.23 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.05 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.05 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.05 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 122.05 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12262 | 121.94 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09883 | 107.97 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09883 | 107.97 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28986 | 124.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28986 | 124.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.97 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.97 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.96 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.96 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28573 | 122.78 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.23322 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.23322 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.08521 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-020 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.08521 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-054 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-055 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.07008 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12592 | 124.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12592 | 124.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.97 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.97 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.96 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.96 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12212 | 122.78 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09813 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09813 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.05125 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-081 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.05125 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12775 | 124.48 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12775 | 124.48 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.97 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.97 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.96 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.96 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12388 | 122.78 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09969 | 110.69 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.09969 | 110.69 | P23:345:AEPW:PITTSBURG CB 3441A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28953 | 116.94 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28953 | 116.94 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.37 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.37 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.37 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.37 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-015 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.28559 | 117.26 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12559 | 116.94 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12559 | 116.94 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.37 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.37 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.37 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.37 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12199 | 117.26 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12742 | 116.94 | P42:345:AEPW:PITTSBURG CB 3429A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12742 | 116.94 | P23:345:AEPW:PITTSBURG CB 3429A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.37 | P23:345:AEPW:PITTSBURG CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.37 | P42:345:AEPW:PITTSBURG CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.37 | P12:345:AEPW-OKGE:PITTSB-7:JOHNCO7:::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.37 | P12:345:OKGE-AEPW:BKRBKR343::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 514809 JOHNCO 7 345 997889 JOHNCOT3 138 3 |  | 478 | 0.12374 | 117.26 | P42:345:OKGE:SB_JOCO7311::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05837 | 111.44 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.0592 | 111.44 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05722 | 109.52 | System Intact
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515135 SUNNYSD4 138 515137 UNIROY 4 138 1 | 194 |  | 0.05805 | 109.52 | System Intact
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.22592 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.19896 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.20763 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.17865 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.31 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68773 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.6799 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44135 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42417 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 144.9 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.31 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.69324 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68562 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44135 | 107.96 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42417 | 105.3 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.22527 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.19646 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.20745 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.17584 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.3 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.3 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.29 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.39 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68711 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.67974 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44057 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42292 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.3 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.3 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.29 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.39 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.69263 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68549 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44057 | 106.69 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42292 | 103.65 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.22759 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-012 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.19864 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.20977 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.17801 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.5 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68943 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68191 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44289 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-075 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42509 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 145.48 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 122.5 | 511568 TERRYRD7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.69495 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-085 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.68767 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.44289 | 108.06 | P42:345:OKGE:SB_GRNT7313::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-087 | TO -> FROM | 515136 SUNNYSD7 345 764145 G20-085-TAP 345 1 |  | 1195 | 0.42509 | 105.61 | P12:345:OKGE-AEPW:BKRBKR365::::
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 520814 ANADARK4 138 521129 CHERRYRD 4 138 1 |  | 169 | 0.71661 | 101.25 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 520926 GRANFLD2 69.0 997733 GRNDFLD 69.0 1 |  | 56 | 0.2784 | 109.95 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO -> FROM | 520926 GRANFLD2 69.0 997733 GRNDFLD 69.0 1 |  | 56 | 0.27825 | 115.45 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 520926 GRANFLD2 69.0 997733 GRNDFLD 69.0 1 |  | 56 | 0.2776 | 135.81 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 520926 GRANFLD2 69.0 997735 GRNDFLD 69.0 1 |  | 56 | 0.28021 | 105.27 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.43 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.45 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 0.81592 | 117.62 | P12:138:WFEC:ANADRKO_CHRYRD::::
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.29 | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 521106 GRNDFLD4 138 997733 GRNDFLD 69.0 1 |  | 56 | 0.2784 | 108.39 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-016 | TO -> FROM | 521106 GRNDFLD4 138 997733 GRNDFLD 69.0 1 |  | 56 | 0.27825 | 114.04 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 521106 GRNDFLD4 138 997733 GRNDFLD 69.0 1 |  | 56 | 0.2776 | 132.99 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 521106 GRNDFLD4 138 997735 GRNDFLD 69.0 1 |  | 56 | 0.28021 | 103.84 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-016 | TO -> FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.45 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27SP | GEN-2020-016 | TO -> FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.52 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 27L | GEN-2020-016 | TO -> FROM | 521190 CACHEJ4 138 764505 G20-016-TAP 138 1 |  | 169 | 1 | 117.3 | 521052 SNYDER 4 138 764505 G20-016-TAP 138 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.49 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.49 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 24SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.49 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.73 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.73 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27SP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.73 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.84 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.84 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 04ALL | 1 | 27WP | GEN-2020-074 | TO -> FROM | 764115 G20-074-TAP 345 764145 G20-085-TAP 345 1 |  | 1195 | 1 | 102.84 | 511468 L.E.S.-7 345 760938 G17-171-TAP 345 1
Thermal | 04NR | 1 | 27L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.30636 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.30636 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.27305 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.27305 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26891 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26891 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.25314 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.2936 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.29365 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.29403 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.24709 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.25988 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.25988 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.25986 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26824 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26479 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26835 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26465 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12651 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12651 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12251 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12251 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12853 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12853 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11952 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12072 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12077 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12115 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10369 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09312 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09312 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09309 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09795 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09493 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09805 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09479 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1033 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1033 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10886 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10886 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1167 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1167 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10721 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0996 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09965 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10004 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08926 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07621 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07621 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07618 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07996 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07715 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08005 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07702 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10062 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10062 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10742 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10742 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11548 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11548 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1059 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09716 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09721 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0976 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08769 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07436 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07436 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07434 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07797 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07519 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07806 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07506 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12835 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12835 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12358 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12358 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12945 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12945 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12048 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12238 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12244 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12282 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10483 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09444 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09444 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09442 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09937 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09633 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09946 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09619 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12306 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12306 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12047 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12047 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12676 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12676 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11768 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11757 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11762 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11801 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10154 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09059 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09059 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09057 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09527 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09228 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09536 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09214 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09054 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09054 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10134 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10134 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11019 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11019 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10043 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.088 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08805 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08843 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08132 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06691 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06691 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06688 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07006 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06737 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07015 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06724 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09054 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09054 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10134 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10134 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11019 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11019 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10043 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.088 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08805 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08843 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08132 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06691 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06691 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06688 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07006 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06737 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07015 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.06724 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07455 | 146.17 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07455 | 145.5 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09193 | 128.21 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09193 | 123.37 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10203 | 121.18 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10203 | 120.58 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09193 | 118.86 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07346 | 112.9 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07351 | 112.66 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.0739 | 109.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07137 | 106.85 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05526 | 106.44 | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05526 | 106.44 | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05523 | 103.99 | 511468 L.E.S.-7 345 764070 G20-009-TAP 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05766 | 100.96 | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05512 | 100.62 | P23:345:SUNC:HLC_BRK282:::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05774 | 100.24 | P42:345:SPS:CARPENTER:OR335_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.05499 | 100.17 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV:
Thermal | 05ALL | 1 | 27L | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.29263 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.29263 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11187 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11187 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09353 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09353 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08754 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08754 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11389 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11389 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10935 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10935 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07907 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07907 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07907 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07907 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27L | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.06171 | 130.3 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27L | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.06171 | 129.63 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.30579 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.30579 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.27268 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.27268 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26857 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.27268 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.26857 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.25308 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.29305 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.2931 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.29347 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.24702 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12503 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12503 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12166 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12166 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12777 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12166 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12777 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11901 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11932 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11937 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11975 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10299 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10669 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10669 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11088 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11088 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11843 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11088 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11843 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1093 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10263 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10268 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10306 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09158 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1007 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1007 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10749 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10749 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11553 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10749 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11553 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10625 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09719 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09724 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09762 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08796 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12705 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12705 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12284 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12284 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12878 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12284 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12878 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12007 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12115 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.1212 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12158 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10423 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12251 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12251 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12017 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12017 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12647 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12017 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.12647 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11767 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11702 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11707 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11745 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10141 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09223 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09223 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11106 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11106 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10163 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08948 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08953 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08991 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08259 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09223 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09223 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11106 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10237 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.11106 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10163 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08948 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08953 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08991 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.08259 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07487 | 139.79 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07487 | 139.57 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09215 | 126.1 | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09215 | 122.53 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10221 | 116.48 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09215 | 116.43 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.10221 | 115.99 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.09243 | 113.09 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07369 | 107.83 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07374 | 107.45 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07412 | 104.54 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 353 | 0.07179 | 101.9 | P12:345:OKGE-AEP:BKRBKR4291::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.30668 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.30668 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.2728 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.2728 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.26873 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.26873 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.25319 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.29334 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.29341 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12592 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12592 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12178 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12178 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12793 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12793 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11913 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11962 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11968 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10758 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10758 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11099 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11099 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11859 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11859 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10941 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10293 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.103 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10159 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10159 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10761 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10761 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11569 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11569 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10636 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09748 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09755 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12794 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12794 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12295 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12295 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12894 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12894 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12018 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12145 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12151 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.1234 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.1234 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12029 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12029 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12663 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.12663 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11778 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11732 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11738 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09312 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09312 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10248 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10248 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11122 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11122 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10174 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08978 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08984 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09312 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09312 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10248 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10248 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11122 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.11122 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10174 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08978 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.08984 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07576 | 127.96 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07576 | 127.49 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09227 | 118.47 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09227 | 112.58 | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10237 | 108.99 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.10237 | 108.27 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.09254 | 108.1 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07399 | 101.92 | 523097 HITCHLAND 7 345 523961 POTTER_CO 7 345 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 |  | 439 | 0.07405 | 101.8 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV:
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.36751 | 116.22 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.38201 | 108.24 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.38201 | 108.18 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.37641 | 100.07 | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.36736 | 112.32 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.38188 | 104.75 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 159 | 0.38188 | 104.57 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 524079 CONWAY 3 115 524088 KIRBY 3 115 1 |  | 173 | 0.36786 | 105.52 | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 |  | 319 | 1 | 104.3 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 524875 OASIS 6 230 524885 SN_JUAN_TAP6 230 1 |  | 319 | 1 | 103.47 | 524885 SN_JUAN_TAP6 230 527483 CHAVES_CNTY6 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.21022 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.21022 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.14836 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.14836 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.09506 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.09506 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.19864 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.19864 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.19065 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.19065 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11354 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11354 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11354 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11354 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.07056 | 106.99 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.07056 | 102.79 | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.20426 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.16027 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.09493 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.19348 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.18834 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11926 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.11926 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 |  | 456 | 0.07127 | 100.92 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.14728 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.14522 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.14728 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36794 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36677 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36794 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.4022 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.40098 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.4022 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.41378 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.41255 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.41378 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36413 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36297 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.36413 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.37262 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.37144 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.37262 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42919 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42793 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42919 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42919 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42793 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.42919 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.46158 | 105.51 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.46028 | 105.43 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 |  | 997.3 | 0.46158 | 105.07 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14776 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14563 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14776 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3668 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36558 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3668 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41017 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.40889 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41017 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41556 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41427 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41556 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36333 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36212 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36333 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37322 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.372 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37322 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43397 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43265 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43397 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43397 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43265 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.43397 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46379 | 109.17 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46242 | 109.03 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46379 | 108.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14693 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14693 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14487 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36758 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36758 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36642 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.40184 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.40184 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.40063 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41343 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41343 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.4122 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36377 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36377 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36262 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37226 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37226 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3711 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42883 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42883 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42758 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42883 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42883 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42758 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46123 | 102.39 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46123 | 102.08 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.45993 | 101.99 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14728 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14522 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.14728 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.15826 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.15826 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36794 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36677 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36794 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3005 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3005 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.4022 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.40098 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.4022 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.32062 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.32062 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41378 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41255 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.41378 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3274 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3274 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36413 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36297 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.36413 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.29826 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.29826 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37262 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37144 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.37262 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.30325 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.30325 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42919 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42793 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42919 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.33647 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.33647 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42919 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42793 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.42919 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.33647 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.33647 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46158 | 120.57 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46028 | 120.5 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.46158 | 119.85 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3555 | 109.35 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 |  | 997.3 | 0.3555 | 108.94 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14776 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14563 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14776 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.15811 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.15811 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3668 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36558 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3668 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.2993 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.2993 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41017 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.40889 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41017 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.32476 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.32476 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41556 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41427 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41556 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3279 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3279 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36333 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36212 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36333 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.29726 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.29726 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37322 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.372 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37322 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.30307 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.30307 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43397 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43265 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43397 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33873 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33873 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43397 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43265 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.43397 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33873 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33873 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46379 | 118.91 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46242 | 118.76 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46379 | 118.4 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.35624 | 106.75 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 24SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.35624 | 106.26 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14693 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14693 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14487 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36758 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36758 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36642 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.40184 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.40184 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.40063 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41343 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41343 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.4122 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36377 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36377 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36262 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37226 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37226 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3711 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42883 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42883 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42758 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42883 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42883 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42758 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46123 | 111.8 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46123 | 111.57 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27SP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.45993 | 111.42 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14728 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14522 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.14728 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.15826 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-005 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.15826 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36794 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36677 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36794 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3005 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-017 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3005 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.4022 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.40098 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.4022 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.32062 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-059 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.32062 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41378 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41255 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.41378 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3274 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-060 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3274 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36413 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36297 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.36413 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.29826 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-062 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.29826 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37262 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37144 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.37262 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.30325 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-063 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.30325 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42919 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42793 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42919 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33647 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-067 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33647 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42919 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42793 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.42919 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33647 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-068 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.33647 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46158 | 122.94 | P12:345:OKGE-SPS:BKRBKR430::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46028 | 122.87 | P42:345:OKGE:SB_BOER7384::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.46158 | 122.3 | P12:345:OKGE:BKRBKR429::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3555 | 111.26 | P42:345:OKGE:SB_BAER7388::::
Thermal | 05ALL | 1 | 27WP | GEN-2020-080 | TO -> FROM | 762467 G18-015-TAP 345 763215 G18-092-TAP 345 1 |  | 997.3 | 0.3555 | 110.83 | P42:345:OKGE:SB_BAER7314::::
Thermal | 05NR | 1 | 27L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 00NR | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 01NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 24SP | ASGI-2020-001 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.0367 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | ASGI-2020-002 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.03882 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | ASGI-2020-003 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.03489 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-003 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.08897 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-003 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.08897 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-007 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.23868 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-007 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.50136 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-007 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.50136 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-008 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.03481 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-008 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.03481 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-052 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.07218 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-057 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.05268 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-058 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.05268 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-061 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.04957 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-064 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.03849 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-072 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.03665 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-073 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.05117 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-076 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.77067 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-076 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.19629 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-076 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.19629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-079 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.04603 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-082 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.03269 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-082 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.03269 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-086 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.77067 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-086 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.19629 | 542981 LACYGNE7 345 764360 G20-007-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-086 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.19629 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 24SP | GEN-2020-089 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.03463 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-090 | WOLFCRK7 | 1.015 | 0.9476 | -0.0674 | 1.0097 | 0.985 | 1.03 | 0.04699 | 532791 BENTON 7 345 765155 G20-076-TAP 345 1
Voltage | 03ALL | 2 | 24SP | GEN-2020-090 | WOLFCRK7 | 1.015 | 0.9646 | -0.0504 | 1.0097 | 0.985 | 1.03 | 0.14295 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV:
Voltage | 03ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 24SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27L | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27SP | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | 27WP | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | 27L | N/A | None | [7 empty] | None

## Short Circuit Ratio
Study Request | Current Cluster | Cluster Group | Transmission Owner | Capacity | Service Type | Generation Type | Point of Interconnection | GEN Bus # | Gen ID | POI Bus # | DIS201TC00ALL-27SP3.sav |  | DIS201TC01ALL-27L3.sav |  | DIS201TC01ALL-27SP3.sav |  | DIS201TC02ALL-27L3.sav |  | DIS201TC02ALL-27SP3.sav |  | DIS201TC03ALL-27L3.sav |  | DIS201TC03ALL-27SP3.sav |  | DIS201TC04ALL-27L3.sav |  | DIS201TC04ALL-27SP3.sav |  | DIS201TC05ALL-27L3.sav |  | DIS201TC05ALL-27SP3.sav
[11 empty] | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio | Short Circuit (MVA) | Short Circuit Ratio
GEN-2020-006 | DISIS-2020-01 | 01 NORTH | BEPC | 250 | ER/NR | Solar | Bowman 230kV substation | 764166 | 1 | 659339 | 1492.78 | 14.93 | 1352.41 | N/A | 1488.81 | 5.96 | 1278.99 | N/A | 1415.44 | 14.15 | 1278.78 | N/A | 1415.29 | 14.15 | 1278.78 | N/A | 1415.29 | 14.15 | 1278.78 | N/A | 1415.29 | 14.15
GEN-2020-014 | DISIS-2020-01 | 01 NORTH | BEPC | 45 | ER/NR | Thermal | Lonesome Creek 115kV | 764181 | 1 | 659346 | 1115.62 | 24.79 | 560.48 | N/A | 1031.37 | N/A | 556.75 | N/A | 1029.39 | N/A | 556.74 | N/A | 1029.39 | N/A | 556.74 | N/A | 1029.39 | N/A | 556.74 | N/A | 1029.39 | N/A
GEN-2020-021 | DISIS-2020-01 | 01 NORTH | BEPC | 235 | ER/NR | Wind | LeLand Olds-Chapelle Creek 345kV line | 764211 | 1 | 764220 | 2371.57 | 50.46 | 2345.36 | 9.98 | 2389.93 | 10.17 | 2257.27 | 16.01 | 2308.5 | 49.12 | 2250.8 | 15.96 | 2303.86 | 49.02 | 2250.71 | 15.96 | 2303.84 | 49.02 | 2250.71 | 15.96 | 2303.84 | 49.02
GEN-2020-083 | DISIS-2020-01 | 01 NORTH | WAPA | 74.5 | ER/NR | Solar | Fairview 115kV Substation | 765071 | 1 | 652651 | 1141.81 | 38.32 | 786.02 | N/A | 1140.76 | 15.31 | 774.33 | N/A | 1072.31 | 35.98 | 774.32 | N/A | 1072.3 | 35.98 | 774.32 | N/A | 1072.3 | 35.98 | 774.32 | N/A | 1072.3 | 35.98
GEN-2020-083 | DISIS-2020-01 | 01 NORTH | WAPA | 74.5 | ER/NR | Solar | Fairview 115kV Substation | 765074 | 1 | 652651 | 1141.81 | 46.6 | 786.02 | N/A | 1140.76 | 46.56 | 774.33 | N/A | 1072.31 | N/A | 774.32 | N/A | 1072.3 | N/A | 774.32 | N/A | 1072.3 | N/A | 774.32 | N/A | 1072.3 | N/A
GEN-2020-091 | DISIS-2020-01 | 01 NORTH | BEPC | 150 | ER/NR | Solar | Patent Gate Substation 345 kV | 764226 | 1 | 659390 | 5029.15 | 83.82 | 4135.29 | N/A | 5003.04 | 33.35 | 3962.43 | N/A | 4885.41 | 81.42 | 3962.01 | N/A | 4885.25 | 81.42 | 3962 | N/A | 4885.25 | 81.42 | 3962 | N/A | 4885.25 | 81.42
GEN-2020-093 | DISIS-2020-01 | 01 NORTH | BEPC | 150 | ER/NR | Solar | Whitlock Substation 230 kV | 764241 | 1 | 655765 | 1810.61 | 30.1768 | 2476.76 | N/A | 2799.3 | 18.662 | 1597.57 | N/A | 1768.06 | 29.4677 | 1595.8 | N/A | 1767.18 | 29.453 | 1595.76 | N/A | 1767.18 | 29.453 | 1595.76 | N/A | 1767.18 | 29.453
GEN-2020-001 | DISIS-2020-01 | 02 NEBRASKA | BEPC | 200 | ER/NR | Solar | Sidney 345 kV Substation | 764256 | 1 | 764265 | 3859.62 | 48.25 | 3267.82 | N/A | 3613.56 | 45.17 | 3501.29 | N/A | 3940.89 | 19.7 | 3262.82 | N/A | 3603.9 | 45.05 | 3261.85 | N/A | 3603.45 | 45.04 | 3261.97 | N/A | 3603.49 | 45.04
GEN-2020-002 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 81 | ER/NR | Solar | 6846 Substation 69 kV | 764571 | 1 | 647846 | 917.81 | 28.33 | 810.64 | N/A | 914.45 | 28.22 | 811.67 | N/A | 915.67 | 11.3 | 810.9 | N/A | 914.51 | 28.23 | 810.47 | N/A | 914.41 | 28.22 | 810.47 | N/A | 914.41 | 28.22
GEN-2020-011 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 80 | ER/NR | Solar | Axtell-Sweetwater Substation 345kV | 764421 | 1 | 764430 | 5806.83 | 181.46 | 4603.88 | N/A | 5135.45 | 160.48 | 5143.81 | N/A | 5804.61 | 72.56 | 4610.96 | N/A | 5141.72 | 160.68 | 4599.03 | N/A | 5132.98 | 160.41 | 4599.13 | N/A | 5133.02 | 160.41
GEN-2020-011 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 80 | ER/NR | Solar | Axtell-Sweetwater Substation 345kV | 764424 | 1 | 764430 | 5806.83 | 72.59 | 4603.88 | N/A | 5135.45 | N/A | 5143.81 | N/A | 5804.61 | 72.56 | 4610.96 | N/A | 5141.72 | N/A | 4599.03 | N/A | 5132.98 | N/A | 4599.13 | N/A | 5133.02 | N/A
GEN-2020-011 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 80 | ER/NR | Solar | Axtell-Sweetwater Substation 345kV | 764427 | 1 | 764430 | 5806.83 | 181.46 | 4603.88 | N/A | 5135.45 | 160.48 | 5143.81 | N/A | 5804.61 | 72.56 | 4610.96 | N/A | 5141.72 | 160.68 | 4599.03 | N/A | 5132.98 | 160.41 | 4599.13 | N/A | 5133.02 | 160.41
GEN-2020-011 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 80 | ER/NR | Solar | Axtell-Sweetwater Substation 345kV | 765290 | 1 | 764430 | 5806.83 | 72.59 | 4603.88 | N/A | 5135.45 | N/A | 5143.81 | N/A | 5804.61 | 72.56 | 4610.96 | N/A | 5141.72 | N/A | 4599.03 | N/A | 5132.98 | N/A | 4599.13 | N/A | 5133.02 | N/A
GEN-2020-013 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 71.66 | ER/NR | Solar | Orleans-Holdrege Substation 115kV | 764436 | 1 | 764445 | 1435.72 | 50.09 | 1111.95 | N/A | 1422.87 | 49.64 | 1135.14 | N/A | 1444.35 | 20.16 | 1112.16 | N/A | 1423.01 | 49.64 | 1111.67 | N/A | 1422.77 | 49.64 | 1111.68 | N/A | 1422.77 | 49.64
GEN-2020-013 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 71.66 | ER/NR | Solar | Orleans-Holdrege Substation 115kV | 764439 | 1 | 764445 | 1435.72 | 50.09 | 1111.95 | N/A | 1422.87 | 49.64 | 1135.14 | N/A | 1444.35 | 20.16 | 1112.16 | N/A | 1423.01 | 49.64 | 1111.67 | N/A | 1422.77 | 49.64 | 1111.68 | N/A | 1422.77 | 49.64
GEN-2020-013 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 71.66 | ER/NR | Solar | Orleans-Holdrege Substation 115kV | 764442 | 1 | 764445 | 1435.72 | 50.09 | 1111.95 | N/A | 1422.87 | 49.64 | 1135.14 | N/A | 1444.35 | 20.16 | 1112.16 | N/A | 1423.01 | 49.64 | 1111.67 | N/A | 1422.77 | 49.64 | 1111.68 | N/A | 1422.77 | 49.64
GEN-2020-025 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 255 | ER/NR | Thermal | Substation 1363; 161kV Substation | 764601 | 1 | 646363 | 8043.53 | 34.23 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | N/A | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-027 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 8 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764616 | 1 | 646363 | 8043.53 | 2513.6 | 5231.5 | N/A | 6244.75 | 1951.48 | 5273.01 | N/A | 6441.39 | 805.17 | 5246.02 | N/A | 6250.31 | 1953.22 | 5224.17 | N/A | 6242.75 | 1950.86 | 5224.11 | N/A | 6242.75 | 1950.86
GEN-2020-027 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 8 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764619 | 1 | 646363 | 8043.53 | 191.51 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | 153.37 | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-028 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 255 | ER/NR | Thermal | Substation 1363; 161kV Substation | 764631 | 1 | 646363 | 8043.53 | 34.23 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | N/A | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-030 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 14 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764646 | 1 | 646363 | 8043.53 | 1436.34 | 5231.5 | N/A | 6244.75 | 1115.13 | 5273.01 | N/A | 6441.39 | 460.1 | 5246.02 | N/A | 6250.31 | 1116.13 | 5224.17 | N/A | 6242.75 | 1114.78 | 5224.11 | N/A | 6242.75 | 1114.78
GEN-2020-030 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 14 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764649 | 1 | 646363 | 8043.53 | 223.43 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | 178.93 | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-031 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 1363; 161kV Substation | 764661 | 1 | 646363 | 8043.53 | 31.18 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | N/A | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-033 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 11 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764676 | 1 | 646363 | 8043.53 | 1828.07 | 5231.5 | N/A | 6244.75 | 1419.26 | 5273.01 | N/A | 6441.39 | 585.58 | 5246.02 | N/A | 6250.31 | 1420.52 | 5224.17 | N/A | 6242.75 | 1418.81 | 5224.11 | N/A | 6242.75 | 1418.81
GEN-2020-033 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 11 | ER/NR | Solar | S1281 - S1362 161kV (S1363) | 764679 | 1 | 646363 | 8043.53 | 206.24 | 5231.5 | N/A | 6244.75 | N/A | 5273.01 | N/A | 6441.39 | 165.16 | 5246.02 | N/A | 6250.31 | N/A | 5224.17 | N/A | 6242.75 | N/A | 5224.11 | N/A | 6242.75 | N/A
GEN-2020-036 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 14 | ER/NR | Solar | Substation 3740; 345kV | 764691 | 1 | 645740 | 13363.77 | 2386.39 | 9291.08 | N/A | 12729.69 | 2273.16 | 9411.45 | N/A | 13085.85 | 934.7 | 9358.12 | N/A | 12772.29 | 2280.77 | 9271.07 | N/A | 12722.91 | 2271.95 | 9270.85 | N/A | 12722.9 | 2271.95
GEN-2020-036 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 14 | ER/NR | Solar | Substation 3740; 345kV | 764694 | 1 | 645740 | 13363.77 | 46.24 | 9291.08 | N/A | 12729.69 | N/A | 9411.45 | N/A | 13085.85 | 45.28 | 9358.12 | N/A | 12772.29 | N/A | 9271.07 | N/A | 12722.91 | N/A | 9270.85 | N/A | 12722.9 | N/A
GEN-2020-038 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 303 | ER/NR | Thermal | Substation 3740; 345kV | 764706 | 1 | 645740 | 13363.77 | 51.8 | 9291.08 | N/A | 12729.69 | N/A | 9411.45 | N/A | 13085.85 | N/A | 9358.12 | N/A | 12772.29 | N/A | 9271.07 | N/A | 12722.91 | N/A | 9270.85 | N/A | 12722.9 | N/A
GEN-2020-043 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 56.52 | ER/NR | Thermal | Between Substation 1209 and 1252; 161kV | 764721 | 1 | 646347 | 7606.52 | 134.58 | 5939.25 | N/A | 7200.43 | N/A | 5990.22 | N/A | 7292.13 | N/A | 5953.12 | N/A | 7205.05 | N/A | 5928.29 | N/A | 7197 | N/A | 5928.23 | N/A | 7197 | N/A
GEN-2020-044 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 56.52 | ER/NR | Thermal | Between Substation 1209 and 1252; 161kV | 764736 | 1 | 646347 | 7606.52 | 134.58 | 5939.25 | N/A | 7200.43 | N/A | 5990.22 | N/A | 7292.13 | N/A | 5953.12 | N/A | 7205.05 | N/A | 5928.29 | N/A | 7197 | N/A | 5928.23 | N/A | 7197 | N/A
GEN-2020-045 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 56.52 | ER/NR | Thermal | Between Substation 1209 and 1252; 161kV | 764751 | 1 | 646347 | 7606.52 | 134.58 | 5939.25 | N/A | 7200.43 | N/A | 5990.22 | N/A | 7292.13 | N/A | 5953.12 | N/A | 7205.05 | N/A | 5928.29 | N/A | 7197 | N/A | 5928.23 | N/A | 7197 | N/A
GEN-2020-069 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 52.85 | ER/NR | Wind | Cody to Valentine 115kV line | 764466 | 1 | 764475 | 292.7 | 27.69 | 290.42 | 9.16 | 291.71 | 27.6 | 291.33 | 5.51 | 292.53 | 5.54 | 290.25 | 9.15 | 291.52 | 27.58 | 290.25 | 9.15 | 291.52 | 27.58 | 290.25 | 9.15 | 291.52 | 27.58
GEN-2020-077 | DISIS-2020-01 | 02 NEBRASKA | NPPD | 151.2 | ER | Wind | North Hebron to Fairbury 115 kV | 764481 | 1 | 764490 | 1005.75 | 33.26 | 895.96 | 9.88 | 997.99 | 33 | 1026.81 | 6.79 | 1117.28 | 7.39 | 896.75 | 9.88 | 998.36 | 33.01 | 895.85 | 9.87 | 997.97 | 33 | 895.85 | 9.87 | 997.97 | 33
GEN-2020-078 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 100 | ER/NR | Solar | Substation 1226 to Substation 1237, 161kV Tap | 764766 | 1 | 764775 | 4290.28 | 107.26 | 3747.81 | N/A | 4215.03 | 105.38 | 3775.01 | N/A | 4257.8 | 42.58 | 3751.55 | N/A | 4215.88 | 105.4 | 3742.74 | N/A | 4213.43 | 105.34 | 3742.72 | N/A | 4213.43 | 105.34
GEN-2020-084 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 175 | ER/NR | Solar | Raun - Fort Calhoun 345 kV | 764781 | 1 | 762780 | 7830.25 | 111.86 | 6365.89 | N/A | 7317.4 | 104.53 | 6567.94 | N/A | 7966.95 | 45.53 | 6363.34 | N/A | 7313.18 | 104.47 | 6345.12 | N/A | 7307.84 | 104.4 | 6345.07 | N/A | 7307.84 | 104.4
GEN-2020-084 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 175 | ER/NR | Solar | Raun - Fort Calhoun 345 kV | 764784 | 1 | 762780 | 7830.25 | 111.86 | 6365.89 | N/A | 7317.4 | 104.53 | 6567.94 | N/A | 7966.95 | 45.53 | 6363.34 | N/A | 7313.18 | 104.47 | 6345.12 | N/A | 7307.84 | 104.4 | 6345.07 | N/A | 7307.84 | 104.4
GEN-2020-094 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 125 | ER/NR | Solar | Neb. City - 103rd & Rokeby 345 kV | 764796 | 1 | 764805 | 9493.75 | 189.875 | 7793.74 | N/A | 9269.21 | 185.3842 | 7934.96 | N/A | 9408.65 | 75.2692 | 7867.42 | N/A | 9317.85 | 186.357 | 7783.06 | N/A | 9266.23 | 185.3246 | 7782.83 | N/A | 9266.22 | 185.3244
GEN-2020-094 | DISIS-2020-01 | 02 NEBRASKA | OPPD | 125 | ER/NR | Solar | Neb. City - 103rd & Rokeby 345 kV | 764799 | 1 | 764805 | 9493.75 | 189.875 | 7793.74 | N/A | 9269.21 | 185.3842 | 7934.96 | N/A | 9408.65 | 75.2692 | 7867.42 | N/A | 9317.85 | 186.357 | 7783.06 | N/A | 9266.23 | 185.3246 | 7782.83 | N/A | 9266.22 | 185.3244
ASGI-2020-001 | DISIS-2020-01 | 03 CENTRAL | KCPL | 35 | ER | Solar | Swavrly 69 kV Substation | 765236 | 1 | 543094 | 547.6 | 39.1143 | 433.56 | N/A | 508.74 | 36.3386 | 433.57 | N/A | 508.74 | 36.3386 | 434.75 | N/A | 548.12 | 15.6606 | 433.56 | N/A | 508.74 | 36.3386 | 433.55 | N/A | 508.74 | 36.3386
ASGI-2020-001 | DISIS-2020-01 | 03 CENTRAL | KCPL | 10 | ER | Battery/Storage | Swavrly 69 kV Substation | 765239 | 1 | 543094 | 547.6 | 54.76 | 433.56 | N/A | 508.74 | N/A | 433.57 | N/A | 508.74 | N/A | 434.75 | N/A | 548.12 | 54.812 | 433.56 | N/A | 508.74 | N/A | 433.55 | N/A | 508.74 | N/A
ASGI-2020-002 | DISIS-2020-01 | 03 CENTRAL | KCPL | 35 | ER | Solar | Postoak 69 kV Substation | 765251 | 1 | 541300 | 668.64 | 47.76 | 491.6 | N/A | 569.45 | 40.675 | 491.62 | N/A | 569.45 | 40.675 | 566.79 | N/A | 751.9 | 21.4829 | 491.61 | N/A | 569.45 | 40.675 | 491.58 | N/A | 569.45 | 40.675
ASGI-2020-002 | DISIS-2020-01 | 03 CENTRAL | KCPL | 10 | ER | Battery/Storage | Postoak 69 kV Substation | 765254 | 1 | 541300 | 668.64 | 66.864 | 491.6 | N/A | 569.45 | N/A | 491.62 | N/A | 569.45 | 0 | 566.79 | N/A | 751.9 | 75.19 | 491.61 | N/A | 569.45 | N/A | 491.58 | N/A | 569.45 | N/A
ASGI-2020-003 | DISIS-2020-01 | 03 CENTRAL | KCPL | 35 | ER | Solar | Carol 69kV Substation | 765266 | 1 | 543060 | 1339.28 | 95.6629 | 1190.47 | N/A | 1295.3 | 92.5214 | 1190.57 | N/A | 1295.31 | 92.5221 | 1196.01 | N/A | 1339.19 | 38.2626 | 1190.47 | N/A | 1295.3 | 92.5214 | 1190.42 | N/A | 1295.3 | 92.5214
ASGI-2020-003 | DISIS-2020-01 | 03 CENTRAL | KCPL | 10 | ER | Battery/Storage | Carol 69kV Substation | 765269 | 1 | 543060 | 1339.28 | 133.928 | 1190.47 | N/A | 1295.3 | N/A | 1190.57 | N/A | 1295.31 | N/A | 1196.01 | N/A | 1339.19 | 133.919 | 1190.47 | N/A | 1295.3 | N/A | 1190.42 | N/A | 1295.3 | N/A
GEN-2008-129 | DISIS-2020-01 | 03 CENTRAL | MIPU | 14.1 | ER | CT | Pleasant Hill 161kV | 541162 | X2 | 541225 | 9459.83 | 34.98 | 5778.22 | N/A | 9253.47 | 104.49 | 5781.3 | N/A | 9253.98 | 110.3 | 5889.79 | N/A | 9358.6 | 142.01 | 5777.31 | N/A | 9253.06 | 122.48 | 5774.49 | N/A | 9252.78 | 106.4
GEN-2008-129 | DISIS-2020-01 | 03 CENTRAL | MIPU | 14.1 | ER | CT | Pleasant Hill 161kV | 541163 | X2 | 541225 | 9459.83 | 46.28 | 5778.22 | 51.03 | 9253.47 | 78.94 | 5781.3 | 51.38 | 9253.98 | 82.21 | 5889.79 | 52.59 | 9358.6 | 83.56 | 5777.31 | 50.84 | 9253.06 | 81.58 | 5774.49 | 51.13 | 9252.78 | 81.19
GEN-2008-129 | DISIS-2020-01 | 03 CENTRAL | MIPU | 14.1 | ER | CT | Pleasant Hill 161kV | 541164 | X2 | 541225 | 9459.83 | 46.28 | 5778.22 | N/A | 9253.47 | 79.16 | 5781.3 | N/A | 9253.98 | 82.72 | 5889.79 | N/A | 9358.6 | 84.08 | 5777.31 | N/A | 9253.06 | 82.07 | 5774.49 | N/A | 9252.78 | 81.42
GEN-2020-003 | DISIS-2020-01 | 03 CENTRAL | KPP | 58 | ER/NR | Thermal | East Substation 69 kV | 765086 | 1 | 533990 | 677.06 | 11.67 | 538.2 | N/A | 581.77 | N/A | 538.21 | N/A | 581.77 | N/A | 541.67 | N/A | 584.64 | N/A | 550.21 | N/A | 592.1 | N/A | 538.21 | N/A | 581.77 | N/A
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 765282 | 1 | 764360 | 8629.56 | 292.06 | 7794.93 | N/A | 8668.62 | 293.38 | 7796.9 | N/A | 8668.85 | 293.39 | 7776.26 | N/A | 8619.61 | 116.69 | 7673.56 | N/A | 8532.87 | 288.79 | 7653.95 | N/A | 8524.77 | 288.52
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 765281 | 1 | 764360 | 8629.56 | 97.36 | 7794.93 | N/A | 8668.62 | N/A | 7796.9 | N/A | 8668.85 | N/A | 7776.26 | N/A | 8619.61 | 97.25 | 7673.56 | N/A | 8532.87 | N/A | 7653.95 | N/A | 8524.77 | N/A
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 765280 | 1 | 764360 | 8629.56 | 292.06 | 7794.93 | N/A | 8668.62 | 293.38 | 7796.9 | N/A | 8668.85 | 293.39 | 7776.26 | N/A | 8619.61 | 116.69 | 7673.56 | N/A | 8532.87 | 288.79 | 7653.95 | N/A | 8524.77 | 288.52
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 764370 | 1 | 764360 | 8629.56 | 97.36 | 7794.93 | N/A | 8668.62 | N/A | 7796.9 | N/A | 8668.85 | N/A | 7776.26 | N/A | 8619.61 | 97.25 | 7673.56 | N/A | 8532.87 | N/A | 7653.95 | N/A | 8524.77 | N/A
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 764369 | 1 | 764360 | 8629.56 | 292.06 | 7794.93 | N/A | 8668.62 | 293.38 | 7796.9 | N/A | 8668.85 | 293.39 | 7776.26 | N/A | 8619.61 | 116.69 | 7673.56 | N/A | 8532.87 | 288.79 | 7653.95 | N/A | 8524.77 | 288.52
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 764368 | 1 | 764360 | 8629.56 | 97.36 | 7794.93 | N/A | 8668.62 | N/A | 7796.9 | N/A | 8668.85 | N/A | 7776.26 | N/A | 8619.61 | 97.25 | 7673.56 | N/A | 8532.87 | N/A | 7653.95 | N/A | 8524.77 | N/A
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 764367 | 1 | 764360 | 8629.56 | 292.06 | 7794.93 | N/A | 8668.62 | 293.38 | 7796.9 | N/A | 8668.85 | 293.39 | 7776.26 | N/A | 8619.61 | 116.69 | 7673.56 | N/A | 8532.87 | 288.79 | 7653.95 | N/A | 8524.77 | 288.52
GEN-2020-007 | DISIS-2020-01 | 03 CENTRAL | KCPL | 73.87 | ER/NR | Solar | Evergy La Cygne to Wolf Creek 345kV Substation | 764366 | 1 | 764360 | 8629.56 | 97.36 | 7794.93 | N/A | 8668.62 | N/A | 7796.9 | N/A | 8668.85 | N/A | 7776.26 | N/A | 8619.61 | 97.25 | 7673.56 | N/A | 8532.87 | N/A | 7653.95 | N/A | 8524.77 | N/A
GEN-2020-008 | DISIS-2020-01 | 03 CENTRAL | SPS | 250 | ER/NR | Solar | Corporation Carpenter 345kV Substation | 764981 | 1 | 523823 | 3949.29 | 39.49 | 3367.12 | N/A | 3655.62 | 36.56 | 3371.15 | N/A | 3657.84 | 36.58 | 3404.05 | N/A | 3766.98 | 22.6 | 3386.66 | N/A | 3673.81 | 36.74 | 3517.07 | N/A | 3795.48 | 37.95
GEN-2020-008 | DISIS-2020-01 | 03 CENTRAL | SPS | 250 | ER/NR | Solar | Corporation Carpenter 345kV Substation | 764984 | 1 | 523823 | 3949.29 | 31.59 | 3367.12 | N/A | 3655.62 | N/A | 3371.15 | N/A | 3657.84 | N/A | 3404.05 | N/A | 3766.98 | 45.2 | 3386.66 | N/A | 3673.81 | N/A | 3517.07 | N/A | 3795.48 | N/A
GEN-2020-015 | DISIS-2020-01 | 03 CENTRAL | OGE | 104 | ER/NR | Solar | Johnston County 345 kV Substation | 764271 | 1 | 514809 | 6337.93 | 152.35 | 4788.8 | N/A | 5359.36 | 128.83 | 4788.85 | N/A | 5359.36 | 128.83 | 4780.05 | N/A | 5354.87 | 128.72 | 5882.76 | N/A | 6576.79 | 63.24 | 4794.85 | N/A | 5373.07 | 129.16
GEN-2020-022 | DISIS-2020-01 | 03 CENTRAL | SUNC | 125 | ER/NR | Solar | Holcomb Substation 115KV | 764996 | 1 | 531449 | 5601.95 | 112.04 | 4718.11 | N/A | 5284.75 | 105.7 | 4739.57 | N/A | 5299.57 | 105.99 | 4800.01 | N/A | 5417.84 | 43.34 | 4731.64 | N/A | 5295.23 | 105.9 | 4769.59 | N/A | 5326.34 | 106.53
GEN-2020-052 | DISIS-2020-01 | 03 CENTRAL | WERE | 126.91 | ER/NR | Wind | Neosho-Delaware 345 kV | 765101 | 1 | 765110 | 7502.16 | 295.57 | 6782.93 | 89.08 | 7368.25 | 290.29 | 6783.59 | 89.09 | 7368.31 | 290.3 | 6841.08 | 53.9 | 7456.19 | 58.75 | 6769.72 | 88.9 | 7373.65 | 290.51 | 6726.23 | 88.33 | 7336.89 | 289.06
GEN-2020-052 | DISIS-2020-01 | 03 CENTRAL | WERE | 126.91 | ER/NR | Wind | Neosho-Delaware 345 kV | 765104 | 1 | 765110 | 7502.16 | 302.29 | 6782.93 | 91.1 | 7368.25 | 296.89 | 6783.59 | 91.11 | 7368.31 | 296.89 | 6841.08 | 55.13 | 7456.19 | 60.09 | 6769.72 | 90.93 | 7373.65 | 297.11 | 6726.23 | 90.34 | 7336.89 | 295.63
GEN-2020-056 | DISIS-2020-01 | 03 CENTRAL | SUNC | 20 | ER/NR | Solar | Russell 115 kV Substation | 765011 | 1 | 539701 | 806.58 | 100.82 | 716.46 | N/A | 795.42 | 99.43 | 720.2 | N/A | 797.86 | 99.73 | 721.25 | N/A | 802.25 | 40.11 | 716.64 | N/A | 795.48 | 99.44 | 716.54 | N/A | 795.44 | 99.43
GEN-2020-057 | DISIS-2020-01 | 03 CENTRAL | WERE | 209.85 | ER/NR | Battery/Storage | Atlantic 345 kV Substation | 765116 | 1 | 765125 | 14382.58 | 68.49 | 8952.91 | N/A | 13514.04 | N/A | 8962.25 | N/A | 13516.02 | N/A | 9907.28 | N/A | 15131.46 | 72.05 | 8949.81 | N/A | 13511.02 | N/A | 8939.13 | N/A | 13509.1 | N/A
GEN-2020-057 | DISIS-2020-01 | 03 CENTRAL | WERE | 209.85 | ER/NR | Battery/Storage | Atlantic 345 kV Substation | 765119 | 1 | 765125 | 14382.58 | 67.05 | 8952.91 | N/A | 13514.04 | N/A | 8962.25 | N/A | 13516.02 | N/A | 9907.28 | N/A | 15131.46 | 70.54 | 8949.81 | N/A | 13511.02 | N/A | 8939.13 | N/A | 13509.1 | N/A
GEN-2020-058 | DISIS-2020-01 | 03 CENTRAL | KCPL | 209.3 | ER/NR | Solar | Craig-West Gardner 345 kV | 764376 | 1 | 765125 | 14382.58 | 171.79 | 8952.91 | N/A | 13514.04 | 161.42 | 8962.25 | N/A | 13516.02 | 161.44 | 9907.28 | N/A | 15131.46 | 72.3 | 8949.81 | N/A | 13511.02 | 161.38 | 8939.13 | N/A | 13509.1 | 161.36
GEN-2020-058 | DISIS-2020-01 | 03 CENTRAL | KCPL | 209.3 | ER/NR | Solar | Craig-West Gardner 345 kV | 764379 | 1 | 765125 | 14382.58 | 167.08 | 8952.91 | N/A | 13514.04 | 156.99 | 8962.25 | N/A | 13516.02 | 157.02 | 9907.28 | N/A | 15131.46 | 70.31 | 8949.81 | N/A | 13511.02 | 156.96 | 8939.13 | N/A | 13509.1 | 156.94
GEN-2020-064 | DISIS-2020-01 | 03 CENTRAL | EDE | 32 | ER/NR | Thermal | 4544 Stateline CC 161kV Substation | 547656 | X | 547498 | 7068.71 | 147.67 | 3747.88 | N/A | 6740.75 | 46.37 | 3747.96 | N/A | 6740.76 | 49.37 | 3898.18 | N/A | 6993.85 | 56.94 | 3754.47 | N/A | 6749.16 | 58.12 | 3737.35 | N/A | 6737.19 | 48.16
GEN-2020-064 | DISIS-2020-01 | 03 CENTRAL | EDE | 32 | ER/NR | Thermal | 4544 Stateline CC 161kV Substation | 547657 | X | 547498 | 7068.71 | 144.43 | 3747.88 | N/A | 6740.75 | 44.77 | 3747.96 | N/A | 6740.76 | 47.66 | 3898.18 | N/A | 6993.85 | 54.96 | 3754.47 | N/A | 6749.16 | 56.1 | 3737.35 | N/A | 6737.19 | 46.49
GEN-2020-070 | DISIS-2020-01 | 03 CENTRAL | SUNC | 255 | ER/NR | Wind | Postrock to Axtell 345 KV line | 765026 | 1 | 765035 | 4014.6 | 78.72 | 3539.71 | 23.14 | 3715.05 | 72.84 | 3909.43 | 15.33 | 4094.13 | 16.06 | 3580.63 | 23.4 | 3761.44 | 73.75 | 3542.21 | 23.15 | 3716.55 | 72.87 | 3541.69 | 23.15 | 3716.15 | 72.87
GEN-2020-071 | DISIS-2020-01 | 03 CENTRAL | WERE | 252 | ER/NR | Wind | Swissvale to Morris 230 KV line | 765131 | 1 | 765140 | 4235.74 | 84.04 | 3648.93 | 24.13 | 4174.07 | 82.82 | 3651.21 | 24.15 | 4174.57 | 82.83 | 3736.22 | 14.83 | 4219.85 | 16.75 | 3650.39 | 24.14 | 4174.36 | 82.82 | 3648.12 | 24.13 | 4173.94 | 82.82
GEN-2020-072 | DISIS-2020-01 | 03 CENTRAL | GMO | 150 | ER/NR | Solar | Windsor to AEC Sedalia 161 kV line | 764346 | 1 | 764355 | 2226.01 | 54.78 | 1878.14 | N/A | 2112.35 | 35.21 | 1878.32 | N/A | 2112.37 | 35.21 | 1888.83 | N/A | 2226.29 | 30.82 | 1878.21 | N/A | 2112.37 | 35.21 | 1877.87 | N/A | 2112.32 | 35.21
GEN-2020-072 | DISIS-2020-01 | 03 CENTRAL | GMO | 150 | ER/NR | Solar | Windsor to AEC Sedalia 161 kV line | 764349 | 1 | 764355 | 2226.01 | 20.35 | 1878.14 | N/A | 2112.35 | N/A | 1878.32 | N/A | 2112.37 | N/A | 1888.83 | N/A | 2226.29 | 28.63 | 1878.21 | N/A | 2112.37 | N/A | 1877.87 | N/A | 2112.32 | N/A
GEN-2020-073 | DISIS-2020-01 | 03 CENTRAL | KCPL | 80.75 | ER/NR | Solar | SE Ottawa to Pleasant Valley 161kV | 764391 | 1 | 764400 | 2329.89 | 101.21 | 1716.87 | N/A | 2115.65 | 65.5 | 1717.14 | N/A | 2115.67 | 65.5 | 2016.11 | N/A | 2674.59 | 63.37 | 1716.71 | N/A | 2115.59 | 65.5 | 1716.33 | N/A | 2115.56 | 65.5
GEN-2020-073 | DISIS-2020-01 | 03 CENTRAL | KCPL | 80.75 | ER/NR | Solar | SE Ottawa to Pleasant Valley 161kV | 764394 | 1 | 764400 | 2329.89 | 32.37 | 1716.87 | N/A | 2115.65 | N/A | 1717.14 | N/A | 2115.67 | N/A | 2016.11 | N/A | 2674.59 | 50.66 | 1716.71 | N/A | 2115.59 | N/A | 1716.33 | N/A | 2115.56 | N/A
GEN-2020-073 | DISIS-2020-01 | 03 CENTRAL | KCPL | 80.75 | ER/NR | Solar | SE Ottawa to Pleasant Valley 161kV | 764397 | 1 | 764400 | 2329.89 | 101.21 | 1716.87 | N/A | 2115.65 | 65.5 | 1717.14 | N/A | 2115.67 | 65.5 | 2016.11 | N/A | 2674.59 | 63.37 | 1716.71 | N/A | 2115.59 | 65.5 | 1716.33 | N/A | 2115.56 | 65.5
GEN-2020-073 | DISIS-2020-01 | 03 CENTRAL | KCPL | 80.75 | ER/NR | Solar | SE Ottawa to Pleasant Valley 161kV | 764398 | 1 | 764400 | 2329.89 | 32.37 | 1716.87 | N/A | 2115.65 | N/A | 1717.14 | N/A | 2115.67 | N/A | 2016.11 | N/A | 2674.59 | 50.66 | 1716.71 | N/A | 2115.59 | N/A | 1716.33 | N/A | 2115.56 | N/A
GEN-2020-076 | DISIS-2020-01 | 03 CENTRAL | WERE | 200 | ER/NR | Battery/Storage | Benton to Wolf Creek 345 kV Line | 765146 | 1 | 765155 | 6895.04 | 34.48 | 6069.93 | N/A | 6618.58 | N/A | 6072.66 | N/A | 6619.29 | N/A | 6337.8 | N/A | 6954.36 | 34.77 | 6092.48 | N/A | 6623.96 | N/A | 6051.11 | N/A | 6598.75 | N/A
GEN-2020-079 | DISIS-2020-01 | 03 CENTRAL | EDE | 101.16 | ER/NR | Solar | Riverton-Neosho 161kV line | 764301 | 1 | 764310 | 5182.7 | 128.08 | 3618.55 | N/A | 5004.72 | 123.68 | 3618.66 | N/A | 5004.73 | 123.68 | 3697.74 | N/A | 5163.33 | 51.04 | 3619.81 | N/A | 5007.23 | 123.74 | 3607.26 | N/A | 5001.1 | 123.59
GEN-2020-079 | DISIS-2020-01 | 03 CENTRAL | EDE | 101.16 | ER/NR | Solar | Riverton-Neosho 161kV line | 764304 | 1 | 764310 | 5182.7 | 41.85 | 3618.55 | N/A | 5004.72 | N/A | 3618.66 | N/A | 5004.73 | N/A | 3697.74 | N/A | 5163.33 | 41.69 | 3619.81 | N/A | 5007.23 | N/A | 3607.26 | N/A | 5001.1 | N/A
GEN-2020-082 | DISIS-2020-01 | 03 CENTRAL | SUNC | 20 | ER/NR | Solar | North Liberal 115 kV Substation | 765041 | 1 | 539737 | 1044.56 | 130.57 | 830.62 | N/A | 1001.49 | 125.19 | 830.9 | N/A | 1001.6 | 125.2 | 870.23 | N/A | 1037.52 | 51.88 | 831.36 | N/A | 1001.98 | 125.25 | 835.79 | N/A | 1006.91 | 125.86
GEN-2020-086 | DISIS-2020-01 | 03 CENTRAL | WERE | 250 | ER/NR | Solar | Benton to Wolf Creek 345 kV Line | 765161 | 1 | 765155 | 6895.04 | 68.95 | 6069.93 | N/A | 6618.58 | 66.19 | 6072.66 | N/A | 6619.29 | 66.19 | 6337.8 | N/A | 6954.36 | 27.82 | 6092.48 | N/A | 6623.96 | 66.24 | 6051.11 | N/A | 6598.75 | 65.99
GEN-2020-086 | DISIS-2020-01 | 03 CENTRAL | WERE | 250 | ER/NR | Solar | Benton to Wolf Creek 345 kV Line | 765164 | 1 | 765155 | 6895.04 | 68.95 | 6069.93 | N/A | 6618.58 | 66.19 | 6072.66 | N/A | 6619.29 | 66.19 | 6337.8 | N/A | 6954.36 | 27.82 | 6092.48 | N/A | 6623.96 | 66.24 | 6051.11 | N/A | 6598.75 | 65.99
GEN-2020-088 | DISIS-2020-01 | 03 CENTRAL | EDE | 150 | ER/NR | Solar | La Russell 161 kV Substation | 764316 | 1 | 547479 | 4179.31 | 69.66 | 3052.94 | N/A | 3368.48 | 56.14 | 3052.98 | N/A | 3368.49 | 56.14 | 3688.55 | N/A | 4265.6 | 28.44 | 3061.34 | N/A | 3373.28 | 56.22 | 3049.43 | N/A | 3367.8 | 56.13
GEN-2020-089 | DISIS-2020-01 | 03 CENTRAL | WERE | 104 | ER/NR | Solar | Dakota 161 kV Substation | 765176 | 1 | 543650 | 2470.14 | 59.38 | 2285.82 | N/A | 2459.66 | 59.13 | 2285.89 | N/A | 2459.66 | 59.13 | 2587.3 | N/A | 2783.43 | 26.76 | 2285.13 | N/A | 2459.3 | 59.12 | 2284.26 | N/A | 2459.06 | 59.11
GEN-2020-090 | DISIS-2020-01 | 03 CENTRAL | WERE | 204.3 | ER/NR | Battery/Storage | Wolf Creek- Blackberry 345 kV Substation | 765191 | 1 | 765200 | 6730.86 | 32.95 | 5792.74 | N/A | 6528.34 | N/A | 5793.82 | N/A | 6528.43 | N/A | 5876.97 | N/A | 6718.05 | 32.88 | 5788.46 | N/A | 6526.56 | N/A | 5771.69 | N/A | 6518.06 | 0
GEN-2020-009 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lawton East Side to Oklaunion 345kV | 764061 | 1 | 764070 | 5395.5 | 62.95 | 4105.24 | N/A | 4741.08 | 39.51 | 4105.32 | N/A | 4741.09 | 39.51 | 4092.36 | N/A | 4735.59 | 39.46 | 4565.83 | N/A | 5273.92 | 43.95 | 4261.55 | N/A | 5084.5 | 33.9
GEN-2020-009 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 300 | ER/NR | Solar | Lawton East Side to Oklaunion 345kV | 764064 | 1 | 764070 | 5395.5 | 25.18 | 4105.24 | N/A | 4741.08 | N/A | 4105.32 | N/A | 4741.09 | N/A | 4092.36 | N/A | 4735.59 | N/A | 4565.83 | N/A | 5273.92 | N/A | 4261.55 | N/A | 5084.5 | 33.9
GEN-2020-010 | DISIS-2020-01 | 04 SOUTHEAST | WFEC | 70 | ER/NR | Solar | Seiling-Taloga Substations 138kV | 765206 | 1 | 765215 | 1769.4 | 63.19 | 1548.66 | N/A | 1684.13 | 60.15 | 1548.71 | N/A | 1684.15 | 60.15 | 1548.49 | N/A | 1684.26 | 60.15 | 1555.98 | N/A | 1767 | 25.24 | 1549.11 | N/A | 1684.5 | 60.16
GEN-2020-010 | DISIS-2020-01 | 04 SOUTHEAST | WFEC | 70 | ER/NR | Solar | Seiling-Taloga Substations 138kV | 765209 | 1 | 765215 | 1769.4 | 25.28 | 1548.66 | N/A | 1684.13 | N/A | 1548.71 | N/A | 1684.15 | N/A | 1548.49 | N/A | 1684.26 | N/A | 1555.98 | N/A | 1767 | 25.24 | 1549.11 | N/A | 1684.5 | N/A
GEN-2020-012 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 56.5 | ER/NR | Solar | Snyder - Altus Jct. 138kV | 765221 | 1 | 765230 | 1543.15 | 68.28 | 1233.15 | N/A | 1356.41 | 60.02 | 1233.15 | N/A | 1356.41 | 60.02 | 1232.2 | N/A | 1356.15 | 60.01 | 1278.39 | N/A | 1574.04 | 27.86 | 1234.8 | N/A | 1358.3 | 60.1
GEN-2020-012 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 56.5 | ER/NR | Solar | Snyder - Altus Jct. 138kV | 765224 | 1 | 765230 | 1543.15 | 27.31 | 1233.15 | N/A | 1356.41 | N/A | 1233.15 | N/A | 1356.41 | N/A | 1232.2 | N/A | 1356.15 | N/A | 1278.39 | N/A | 1574.04 | 27.86 | 1234.8 | N/A | 1358.3 | N/A
GEN-2020-016 | DISIS-2020-01 | 04 SOUTHEAST | WFEC | 202 | ER/NR | Wind | Snyder SW-Cache 138 kV line | 764496 | 1 | 764505 | 1367.7 | 33.85 | 1215.02 | 10.02 | 1279.78 | 31.68 | 1215.02 | 10.02 | 1279.78 | 31.68 | 1214.1 | 10.02 | 1279.53 | 31.67 | 1363.39 | 6.75 | 1574.6 | 7.8 | 1216 | 10.03 | 1280.94 | 31.71
GEN-2020-020 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 201.6 | ER/NR | Solar | Tap the 345 kV Northwest Texarkana - Valliant line | 764511 | 1 | 764520 | 8040.2 | 99.7 | 5840.85 | N/A | 7667.35 | 95.08 | 5840.87 | N/A | 7667.35 | 95.08 | 5837.12 | N/A | 7665.42 | 95.06 | 6042.26 | N/A | 8063.33 | 59.84 | 5841.87 | N/A | 7670.39 | 95.12
GEN-2020-020 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 201.6 | ER/NR | Solar | Tap the 345 kV Northwest Texarkana - Valliant line | 764514 | 1 | 764520 | 8040.2 | 80.4 | 5840.85 | N/A | 7667.35 | N/A | 5840.87 | N/A | 7667.35 | N/A | 5837.12 | N/A | 7665.42 | N/A | 6042.26 | N/A | 8063.33 | 120.63 | 5841.87 | N/A | 7670.39 | N/A
GEN-2020-023 | DISIS-2020-01 | 04 SOUTHEAST | OGE | 202 | ER/NR | Battery/Storage | Woodring 345 KV Station | 764526 | 1 | 514714 | 4747.47 | 23.5 | 4310.23 | N/A | 4534.23 | N/A | 4310.48 | N/A | 4534.28 | N/A | 4322.1 | N/A | 4540.09 | N/A | 4429.9 | N/A | 4717.25 | 23.35 | 4306.32 | N/A | 4530.95 | N/A
GEN-2020-054 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 298 | ER/NR | Solar | Lydia 345 kV Station | 764076 | 1 | 508298 | 7885.94 | 66.16 | 5500.71 | N/A | 7525.62 | 63.13 | 5500.72 | N/A | 7525.63 | 63.13 | 5499.3 | N/A | 7525.06 | 63.13 | 5594.99 | N/A | 7911.29 | 26.55 | 5501.14 | N/A | 7526.54 | 63.14
GEN-2020-055 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 71 | ER/NR | Battery/Storage | Lydia 345 kV Station | 764091 | 1 | 508298 | 7885.94 | 111.07 | 5500.71 | N/A | 7525.62 | N/A | 5500.72 | N/A | 7525.63 | N/A | 5499.3 | N/A | 7525.06 | N/A | 5594.99 | N/A | 7911.29 | 111.43 | 5501.14 | N/A | 7526.54 | N/A
GEN-2020-074 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 200 | ER/NR | Battery/Storage | Lawton to Sunnyside 345 kV Substation | 764106 | 1 | 764115 | 6227.51 | 31.14 | 4716.61 | N/A | 5393.23 | N/A | 4716.67 | N/A | 5393.24 | N/A | 4705.37 | N/A | 5388.02 | N/A | 5819.45 | N/A | 6794.79 | 33.97 | 4741.47 | N/A | 5440.28 | N/A
GEN-2020-075 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 200 | ER/NR | Battery/Storage | Cimmarron to Lawton 345 kV Line | 764541 | 1 | 764550 | 8887.16 | 44.44 | 6282.26 | N/A | 7682.05 | N/A | 6282.46 | N/A | 7682.09 | N/A | 6245.45 | N/A | 7662.5 | N/A | 7706.05 | N/A | 9563.8 | 47.82 | 6398.53 | N/A | 7947.6 | N/A
GEN-2020-081 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 200 | ER/NR | Battery/Storage | Tenaska Switching Substation 345kV | 764121 | 1 | 508585 | 5005.64 | 25.03 | 3320.03 | N/A | 4885.49 | N/A | 3320.03 | N/A | 4885.49 | N/A | 3319.94 | N/A | 4885.48 | N/A | 3326.21 | N/A | 4993.41 | 24.97 | 3320.06 | N/A | 4885.5 | N/A
GEN-2020-085 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Lawton to Sunnyside 345 kV Line | 764136 | 1 | 764115 | 6227.51 | 62.28 | 4716.61 | N/A | 5393.23 | 53.93 | 4716.67 | N/A | 5393.24 | 53.93 | 4705.37 | N/A | 5388.02 | 53.88 | 5819.45 | N/A | 6794.79 | 27.18 | 4741.47 | N/A | 5440.28 | 54.4
GEN-2020-085 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Lawton to Sunnyside 345 kV Line | 764139 | 1 | 764115 | 6227.51 | 62.28 | 4716.61 | N/A | 5393.23 | 53.93 | 4716.67 | N/A | 5393.24 | 53.93 | 4705.37 | N/A | 5388.02 | 53.88 | 5819.45 | N/A | 6794.79 | 27.18 | 4741.47 | N/A | 5440.28 | 54.4
GEN-2020-087 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Cimmarron to Lawton 345 kV Line | 764556 | 1 | 764550 | 8887.16 | 88.87 | 6282.26 | N/A | 7682.05 | 76.82 | 6282.46 | N/A | 7682.09 | 76.82 | 6245.45 | N/A | 7662.5 | 76.63 | 7706.05 | N/A | 9563.8 | 38.26 | 6398.53 | N/A | 7947.6 | 79.48
GEN-2020-087 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 250 | ER/NR | Solar | Cimmarron to Lawton 345 kV Line | 764559 | 1 | 764550 | 8887.16 | 88.87 | 6282.26 | N/A | 7682.05 | 76.82 | 6282.46 | N/A | 7682.09 | 76.82 | 6245.45 | N/A | 7662.5 | 76.63 | 7706.05 | N/A | 9563.8 | 38.26 | 6398.53 | N/A | 7947.6 | 79.48
GEN-2020-092 | DISIS-2020-01 | 04 SOUTHEAST | AEP | 100 | ER/NR | Solar | Pryor Junction - Midwest Carbide 138kV line | 764151 | 1 | 764160 | 2036.18 | 50.9045 | 1773.05 | N/A | 1910.78 | 47.7695 | 1773.06 | N/A | 1910.78 | 47.7695 | 1762.89 | N/A | 1905.83 | 47.6457 | 1765.1 | N/A | 2034.36 | 20.3436 | 1761.33 | N/A | 1905.08 | 47.627
GEN-2020-005 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 150 | ER/NR | Wind | Conway 115 kV Line (524079) | 764811 | 1 | 524079 | 1056.82 | 35.23 | 1015.2 | N/A | 1052.51 | 35.08 | 1015.21 | 11.28 | 1052.51 | 35.08 | 1015.26 | 11.28 | 1052.56 | 35.09 | 1016.08 | 11.29 | 1053.6 | 35.12 | 1049.88 | 7 | 1085.86 | 7.24
GEN-2020-017 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 74.88 | ER/NR | Solar | 230kV Lamb County Interchange | 764826 | 1 | 525637 | 2195.4 | 73.3 | 2007.69 | N/A | 2141.74 | 71.51 | 2007.69 | N/A | 2141.74 | 71.51 | 2007.69 | N/A | 2141.75 | 71.51 | 2008.41 | N/A | 2141.95 | 71.51 | 2049.02 | N/A | 2192.67 | 29.28
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764841 | 1 | 764866 | 5550.12 | 190.37 | 4411.9 | N/A | 5139.95 | 122.38 | 4411.92 | N/A | 5139.95 | 122.38 | 4411.76 | N/A | 5139.95 | 122.38 | 4416.86 | N/A | 5141.67 | 122.42 | 4658.57 | N/A | 5428.35 | 106.4
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764843 | 1 | 764866 | 5550.12 | 76.15 | 4411.9 | N/A | 5139.95 | N/A | 4411.92 | N/A | 5139.95 | N/A | 4411.76 | N/A | 5139.95 | N/A | 4416.86 | N/A | 5141.67 | N/A | 4658.57 | N/A | 5428.35 | 106.4
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764846 | 1 | 764866 | 5550.12 | 190.37 | 4411.9 | N/A | 5139.95 | 122.38 | 4411.92 | N/A | 5139.95 | 122.38 | 4411.76 | N/A | 5139.95 | 122.38 | 4416.86 | N/A | 5141.67 | 122.42 | 4658.57 | N/A | 5428.35 | 106.4
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764848 | 1 | 764866 | 5550.12 | 76.15 | 4411.9 | N/A | 5139.95 | N/A | 4411.92 | N/A | 5139.95 | N/A | 4411.76 | N/A | 5139.95 | N/A | 4416.86 | N/A | 5141.67 | N/A | 4658.57 | N/A | 5428.35 | 106.4
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764851 | 1 | 764866 | 5550.12 | 196.93 | 4411.9 | N/A | 5139.95 | 126.6 | 4411.92 | N/A | 5139.95 | 126.6 | 4411.76 | N/A | 5139.95 | 126.6 | 4416.86 | N/A | 5141.67 | 126.64 | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764853 | 1 | 764866 | 5550.12 | 78.77 | 4411.9 | N/A | 5139.95 | N/A | 4411.92 | N/A | 5139.95 | N/A | 4411.76 | N/A | 5139.95 | N/A | 4416.86 | N/A | 5141.67 | N/A | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764856 | 1 | 764866 | 5550.12 | 196.93 | 4411.9 | N/A | 5139.95 | 126.6 | 4411.92 | N/A | 5139.95 | 126.6 | 4411.76 | N/A | 5139.95 | 126.6 | 4416.86 | N/A | 5141.67 | 126.64 | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764858 | 1 | 764866 | 5550.12 | 78.77 | 4411.9 | N/A | 5139.95 | N/A | 4411.92 | N/A | 5139.95 | N/A | 4411.76 | N/A | 5139.95 | N/A | 4416.86 | N/A | 5141.67 | N/A | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764861 | 1 | 764866 | 5550.12 | 196.93 | 4411.9 | N/A | 5139.95 | 126.6 | 4411.92 | N/A | 5139.95 | 126.6 | 4411.76 | N/A | 5139.95 | 126.6 | 4416.86 | N/A | 5141.67 | 126.64 | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-059 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 105 | ER/NR | Solar | Tuco-Yoakum-Hobbs 345 kV | 764863 | 1 | 764866 | 5550.12 | 78.77 | 4411.9 | N/A | 5139.95 | N/A | 4411.92 | N/A | 5139.95 | N/A | 4411.76 | N/A | 5139.95 | N/A | 4416.86 | N/A | 5141.67 | N/A | 4658.57 | N/A | 5428.35 | 110.06
GEN-2020-060 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 200 | ER | Battery/Storage | Lubbock East Substation 230 kV | 764876 | 1 | 526299 | 3845.59 | 19.23 | 2502.8 | N/A | 3705.13 | N/A | 2502.81 | N/A | 3705.13 | N/A | 2502.65 | N/A | 3705.13 | N/A | 2507.77 | N/A | 3707.04 | N/A | 2558.45 | N/A | 3840.94 | 19.2
GEN-2020-062 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 128 | ER | Solar | OASIS 230kV Substation | 764891 | 1 | 524875 | 3198.21 | 62.47 | 2709.33 | N/A | 3003.52 | 58.66 | 2709.33 | N/A | 3003.53 | 58.66 | 2709.33 | N/A | 3003.55 | 58.66 | 2710.37 | N/A | 3003.84 | 58.67 | 2865.54 | N/A | 3272.94 | 25.57
GEN-2020-062 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 128 | ER | Solar | OASIS 230kV Substation | 764894 | 1 | 524875 | 3198.21 | 62.47 | 2709.33 | N/A | 3003.52 | 58.66 | 2709.33 | N/A | 3003.53 | 58.66 | 2709.33 | N/A | 3003.55 | 58.66 | 2710.37 | N/A | 3003.84 | 58.67 | 2865.54 | N/A | 3272.94 | 25.57
GEN-2020-063 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 184 | ER | Solar | San Juan Mesa 230 kV Line | 764906 | 1 | 524885 | 1852.44 | 25.17 | 1664.04 | N/A | 1813.48 | 24.64 | 1664.04 | N/A | 1813.48 | 24.64 | 1664.03 | N/A | 1813.48 | 24.64 | 1664.33 | N/A | 1813.55 | 24.64 | 1913.89 | N/A | 2104.36 | 11.44
GEN-2020-065 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 334.33 | ER | Thermal | Hobbs-Andrews 345 kV Line | 764921 | 1 | 764930 | 4907.25 | 16.14 | 2620.46 | N/A | 2989.71 | N/A | 2620.46 | N/A | 2989.71 | N/A | 2620.44 | N/A | 2989.71 | N/A | 2621.22 | N/A | 2989.88 | N/A | 2684.75 | N/A | 3055.32 | N/A
GEN-2020-065 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 334.33 | ER | Thermal | Hobbs-Andrews 345 kV Line | 764924 | 1 | 764930 | 4907.25 | 16.14 | 2620.46 | N/A | 2989.71 | N/A | 2620.46 | N/A | 2989.71 | N/A | 2620.44 | N/A | 2989.71 | N/A | 2621.22 | N/A | 2989.88 | N/A | 2684.75 | N/A | 3055.32 | N/A
GEN-2020-065 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 334.33 | ER | Thermal | Hobbs-Andrews 345 kV Line | 764927 | 1 | 764930 | 4907.25 | 16.14 | 2620.46 | N/A | 2989.71 | N/A | 2620.46 | N/A | 2989.71 | N/A | 2620.44 | N/A | 2989.71 | N/A | 2621.22 | N/A | 2989.88 | N/A | 2684.75 | N/A | 3055.32 | N/A
GEN-2020-067 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 176.25 | ER/NR | Wind | Tuco to Yoakum 345kV line | 764936 | 1 | 764945 | 4552.17 | 129.14 | 3634.02 | 34.36 | 4376.96 | 124.17 | 3634.04 | 34.36 | 4376.96 | 124.17 | 3633.69 | 34.36 | 4376.92 | 124.17 | 3643.48 | 34.45 | 4381.46 | 124.3 | 3764.06 | 21.36 | 4508.9 | 25.58
GEN-2020-067 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 176.25 | ER/NR | Wind | Tuco to Yoakum 345kV line | 764939 | 1 | 764945 | 4552.17 | 129.14 | 3634.02 | 34.36 | 4376.96 | 124.17 | 3634.04 | 34.36 | 4376.96 | 124.17 | 3633.69 | 34.36 | 4376.92 | 124.17 | 3643.48 | 34.45 | 4381.46 | 124.3 | 3764.06 | 21.36 | 4508.9 | 25.58
GEN-2020-068 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 201.87 | ER/NR | Solar | Tuco to Yoakum 345kV line | 764951 | 1 | 764945 | 4552.17 | 56.38 | 3634.02 | N/A | 4376.96 | 54.21 | 3634.04 | N/A | 4376.96 | 54.21 | 3633.69 | N/A | 4376.92 | 54.2 | 3643.48 | N/A | 4381.46 | 54.26 | 3764.06 | N/A | 4508.9 | 22.34
GEN-2020-068 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 201.87 | ER/NR | Solar | Tuco to Yoakum 345kV line | 764954 | 1 | 764945 | 4552.17 | 57.44 | 3634.02 | N/A | 4376.96 | 55.23 | 3634.04 | N/A | 4376.96 | 55.23 | 3633.69 | N/A | 4376.92 | 55.23 | 3643.48 | N/A | 4381.46 | 55.29 | 3764.06 | N/A | 4508.9 | 22.76
GEN-2020-080 | DISIS-2020-01 | 05 SOUTHWEST | SPS | 200 | ER/NR | Battery/Storage | Tuco Interchange 345 kV Substation | 764966 | 1 | 525832 | 8407.78 | 42.04 | 5152.78 | N/A | 7717.56 | N/A | 5152.85 | N/A | 7717.57 | N/A | 5151.03 | N/A | 7717.11 | N/A | 5198.69 | N/A | 7758.56 | N/A | 5537.38 | N/A | 8356.76 | 41.78