03 - Central | 25S | Transfer | G03_P1_Regional_Fault_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_020 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_023 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_024 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_025 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_027 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_028 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_029 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_030 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_031 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_032 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_033 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2018-032 (762680) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_034 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_035 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_036 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_037 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_038 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_039 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_040 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_041 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2017-018 (588630) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_042 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_043 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_044 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_045 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_046 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_047 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_048 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_050 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_051 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_052 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_053 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_054 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_055 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_056 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_057 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_058 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_059 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P1_Regional_Fault_060 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.4. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply Fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to 5OSAGE CRK#! (338682) 161.0 kV Transmission Circuit #1 b.2. 5GRANDVIEW% (338099) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply Fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 b.2. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.2. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.2. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.3. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on CONCRD6 230.00 (539658) 230 kV Bus a. Apply Fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_099 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_100 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_101 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_102 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_103 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_104 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_105 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_106 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_107 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_108 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_109 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_110 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_111 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_112 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_113 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_114 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_115 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_116 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_119 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_120 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_125 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_126 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV to CHAMSPR1 (506919) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_127 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR7 (506945) 345.0 kV to TONTITN7 (506959) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_128 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_129 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_130 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_131 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_132 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_133 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_134 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_135 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_136 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_137 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_138 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_139 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_140 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_141 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_142 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_143 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_144 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_145 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_146 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_147 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_148 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_149 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_150 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_151 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_152 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_153 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_155 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_156 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_157 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_158 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_159 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_160 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_161 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_162 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_163 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_164 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_165 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_166 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_167 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_168 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_169 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_170 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_171 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_172 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_173 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_174 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_175 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_176 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_177 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_178 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_179 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_180 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_181 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_182 | Single Phase Fault with Stuck Breaker on 1THLG3 24.000 (300003) 24 kV Bus a. Apply Fault at the 1THLG3 24.000 (300003) 24 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 b.2. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.3. 7THOMHL (300049) 345.0 kV to 7THOMHLGSU3 (301503) 345.0 kV Transmission Circuit #1 b.4. 1THLG3 (300003) 24.0 kV to 7THOMHLGSU3 (301503) 345.0 kV Two Winding #3 b.5. 1THLG3 (300003) 24.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_183 | Single Phase Fault with Stuck Breaker on NES3-1 22.000 (511840) 22 kV Bus a. Apply Fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. NES3-1 (511840) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_184 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_185 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_186 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_188 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_189 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_190 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_191 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_192 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_193 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_194 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_195 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_196 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_197 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_198 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_199 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_200 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_201 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_202 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_203 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_204 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_205 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV to CHAMSPR1 (506919) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_206 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR7 (506945) 345.0 kV to TONTITN7 (506959) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_207 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_208 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_209 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_210 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_211 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_212 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_213 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_214 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_215 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_216 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_217 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_218 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_219 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_220 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_221 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_222 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_223 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_224 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_225 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_226 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_227 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_228 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_229 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_230 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_231 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_232 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_233 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_234 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_235 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_236 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_237 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_238 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_239 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_240 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_241 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_242 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_243 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_244 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_245 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_246 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_247 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_248 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_249 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_250 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_251 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_252 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_253 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_254 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_255 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_256 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_257 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_258 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_259 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_260 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_261 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_262 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_263 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_264 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_265 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #2 b.9. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.10. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_266 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_267 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_268 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_269 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_270 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_271 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_272 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_273 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_274 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_275 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_276 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_277 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_278 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_279 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_280 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_281 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_282 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_283 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_284 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_285 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 b.4. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_286 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_287 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_288 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_289 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_290 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_291 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_292 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_293 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_294 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_295 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_296 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_297 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_298 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_299 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_300 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_301 | Single Phase Fault with Stuck Breaker on NES3-1 22.000 (511840) 22 kV Bus a. Apply Fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. NES3-1 (511840) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_302 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. DOGWDCT1 (541163) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.3. DOGWDCT2 (541164) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.4. DOGWDSTG (541162) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_303 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_304 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_305 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.3. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.4. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.5. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.6. W.GRDNR7 (542965) 345.0 kV to GEN-2017-195 (762279) 345.0 kV Transmission Circuit #1 b.7. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_306 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.4. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 b.5. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_307 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.3. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_308 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.4. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.5. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_309 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.4. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.5. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_310 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.4. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.6. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_311 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_312 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_313 | Single Phase Fault with Stuck Breaker on OSBORN7 345.00 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 345.00 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 b.2. OSBORN7 (541501) 345.0 kV to OSBORN_B1_1 (541502) 34.5 kV to OSBORN_TER_1 (541505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P4_Local_Fault_314 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.3. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.4. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.5. HOLT 7 (541510) 345.0 kV to GEN-2017-115 (760746) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_315 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25S | Transfer | G03_P4_Local_Fault_316 | Single Phase Fault with Stuck Breaker on LACYGNE11_7 345.00 (543629) 345 kV Bus a. Apply Fault at the LACYGNE11_7 345.00 (543629) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 b.2. LACYGNE11_7 (543629) 345.0 kV to LAC11_AQC1 (543630) 13.8 kV to LAC11_TER1 (543631) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_317 | Single Phase Fault with Stuck Breaker on LACYGNE22_7 345.00 (543632) 345 kV Bus a. Apply Fault at the LACYGNE22_7 345.00 (543632) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 b.2. LACYGNE22_7 (543632) 345.0 kV to LAC22_AQC1 (543633) 13.8 kV to LAC22_TER1 (543634) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_318 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_319 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_320 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_321 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.9. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.10. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.13. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.14. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.15. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_322 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-T (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_323 | Single Phase Fault with Stuck Breaker on CONCORD3 115.00 (539657) 115 kV Bus a. Apply Fault at the CONCORD3 115.00 (539657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCRD6 (539658) 230.0 kV to CONCORD3 (539657) 115.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 b.3. CONCOD-T (539904) 13.8 kV to CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV Three Winding #1 b.4. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.5. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to CONCORD1 (539705) 34.5 kV to CONCOW-T (539905) 5.1 kV Three Winding #1 b.9. CONCORD3 (539657) 115.0 kV to CCORDIA1 (539745) 34.5 kV to CCORD-T (539945) 7.2 kV Three Winding #1 b.10. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_324 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 b.10. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.11. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.12. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.13. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.15. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.16. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.17. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.18. 24-FREY3 (539661) 115.0 kV to GEN-2018-116 (763329) 115.0 kV Transmission Circuit #1 b.19. 24-FREY3 (539661) 115.0 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 b.20. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.21. 2ND-KS 3 (539689) 115.0 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 b.22. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.23. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.24. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.25. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_325 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.8. SPERVLTT (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.11. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLDT (539936) 13.8 kV Three Winding #1 b.12. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.13. SVWF1 1 (539116) 0.6 kV to SVWF1-CLCT1 (539115) 34.5 kV Two Winding #1 b.14. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_326 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_327 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_328 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.3. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.4. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.5. STRANGR7 (532772) 345.0 kV to GEN-2016-149 (588240) 345.0 kV Transmission Circuit #1 b.6. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.7. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_329 | Single Phase Fault with Stuck Breaker on READWF 7 345.00 (532776) 345 kV Bus a. Apply Fault at the READWF 7 345.00 (532776) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to READWF 7 (532776) 345.0 kV Transmission Circuit #1 b.2. READWF 7 (532776) 345.0 kV to R1 WFTX1 (534040) 34.5 kV to R1 LV 1 (534043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_330 | Single Phase Fault with Stuck Breaker on GEN-2017-009345.00 (532778) 345 kV Bus a. Apply Fault at the GEN-2017-009345.00 (532778) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009XFMR1 (534056) 34.5 kV to GEN-2017-009 (532778) 345.0 kV Two Winding #1 b.3. G17-009XFMR2 (534057) 34.5 kV to GEN-2017-009 (532778) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_331 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_332 | Single Phase Fault with Stuck Breaker on CANEYWF7 345.00 (532781) 345 kV Bus a. Apply Fault at the CANEYWF7 345.00 (532781) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.2. CANEYWF7 (532781) 345.0 kV to CNYWFLV12 (533077) 34.5 kV to CNYWF1 2 (533100) 13.2 kV Three Winding #1 b.3. CANEYWF7 (532781) 345.0 kV to CNYWFLV11 (533079) 34.5 kV to CNYWF1 1 (533102) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_333 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_334 | Single Phase Fault with Stuck Breaker on KINGMAN7 345.00 (532783) 345 kV Bus a. Apply Fault at the KINGMAN7 345.00 (532783) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 b.3. KINGMAN7 (532783) 345.0 kV to K1 LV 1 (534001) 34.5 kV to K1 WFTX1 (534031) 13.8 kV Three Winding #1 b.4. KINGMAN7 (532783) 345.0 kV to K2 LV 1 (534002) 34.5 kV to K2 WFTX1 (534032) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_335 | Single Phase Fault with Stuck Breaker on NINN1WF7 345.00 (532784) 345 kV Bus a. Apply Fault at the NINN1WF7 345.00 (532784) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 b.2. NINN1WF7 (532784) 345.0 kV to PRATTWF7 (532785) 345.0 kV Transmission Circuit #1 b.3. NINN1WF7 (532784) 345.0 kV to N1 LV 1 (534000) 34.5 kV to N1 WFTX1 (534030) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_336 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_337 | Single Phase Fault with Stuck Breaker on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply Fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR2EAST7 (532792) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. FR2EAST7 (532792) 345.0 kV to FR2ELV11 (533131) 34.5 kV to F2EAST11 (533127) 13.8 kV Three Winding #1 b.4. FR2EAST7 (532792) 345.0 kV to FR2ELV21 (533132) 34.5 kV to F2EAST21 (533128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_338 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_339 | Single Phase Fault with Stuck Breaker on FR2WEST7 345.00 (532795) 345 kV Bus a. Apply Fault at the FR2WEST7 345.00 (532795) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR2WEST7 (532795) 345.0 kV to FR3HV (578530) 345.0 kV Transmission Circuit #1 b.3. FR2WEST7 (532795) 345.0 kV to FR2WLV11 (533133) 34.5 kV to F2WEST11 (533129) 13.8 kV Three Winding #1 b.4. FR2WEST7 (532795) 345.0 kV to FR2WLV21 (533134) 34.5 kV to F2WEST21 (533130) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_340 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_341 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_342 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_343 | Single Phase Fault with Stuck Breaker on ELKRVR17 345.00 (532801) 345 kV Bus a. Apply Fault at the ELKRVR17 345.00 (532801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 b.2. ELKRVR17 (532801) 345.0 kV to ER1 CLCT1 (534016) 34.5 kV to ER1 TERT1 (534036) 13.2 kV Three Winding #1 b.3. ELKRVR17 (532801) 345.0 kV to ER2 CLCT1 (534017) 34.5 kV to ER2 TERT1 (534037) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_344 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_345 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_346 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_347 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.3. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.4. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_348 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.3. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.4. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_349 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_350 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_351 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_352 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.3. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.4. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.5. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.6. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.7. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.8. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_353 | Single Phase Fault with Stuck Breaker on GEN-2020-001345.00 (764255) 345 kV Bus a. Apply Fault at the GEN-2020-001345.00 (764255) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-001 (764255) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-001 (764255) 345.0 kV to G20-001-XFM1 (764258) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_354 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_355 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_356 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S1214 5 (646214) 161.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_357 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S983 8 (647983) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_358 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_359 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_360 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_361 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_362 | Single Phase Fault with Stuck Breaker on GEN-2020-013115.00 (764435) 115 kV Bus a. Apply Fault at the GEN-2020-013115.00 (764435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-013 (764435) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. GEN-2020-013 (764435) 115.0 kV to G20-013-SS2 (764447) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_363 | Single Phase Fault with Stuck Breaker on GEN-2020-027161.00 (764615) 161 kV Bus a. Apply Fault at the GEN-2020-027161.00 (764615) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-027 (764615) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-027 (764615) 161.0 kV to G20-027-XFM1 (764618) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_364 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_365 | Single Phase Fault with Stuck Breaker on GEN-2020-031161.00 (764660) 161 kV Bus a. Apply Fault at the GEN-2020-031161.00 (764660) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-031 (764660) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-031 (764660) 161.0 kV to G20-031-GEN1 (764661) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_366 | Single Phase Fault with Stuck Breaker on GEN-2020-028161.00 (764630) 161 kV Bus a. Apply Fault at the GEN-2020-028161.00 (764630) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-028 (764630) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-028 (764630) 161.0 kV to G20-028-GEN1 (764631) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_367 | Single Phase Fault with Stuck Breaker on GEN-2020-025161.00 (764600) 161 kV Bus a. Apply Fault at the GEN-2020-025161.00 (764600) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-025 (764600) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-025 (764600) 161.0 kV to G20-025-GEN1 (764601) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_368 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_369 | Single Phase Fault with Stuck Breaker on GEN-2020-038345.00 (764705) 345 kV Bus a. Apply Fault at the GEN-2020-038345.00 (764705) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-038 (764705) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-038 (764705) 345.0 kV to G20-038-GEN1 (764706) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_370 | Single Phase Fault with Stuck Breaker on GEN-2018-033345.00 (762691) 345 kV Bus a. Apply Fault at the GEN-2018-033345.00 (762691) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-033 (762691) 345.0 kV to G18-033XFM1 (762692) 34.5 kV Two Winding #1 b.2. GEN-2018-033 (762691) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_371 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_372 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_373 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  | Protection relay instance was disabled and the study was performed again.
03 - Central | 25S | Transfer | G03_P4_Local_Fault_374 | Single Phase Fault with Stuck Breaker on GEN-2020-036345.00 (764690) 345 kV Bus a. Apply Fault at the GEN-2020-036345.00 (764690) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-036 (764690) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-036 (764690) 345.0 kV to G20-036-XFM1 (764693) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_375 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_376 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_377 | Single Phase Fault with Stuck Breaker on GEN-2020-045161.00 (764750) 161 kV Bus a. Apply Fault at the GEN-2020-045161.00 (764750) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-045 (764750) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-045 (764750) 161.0 kV to G20-045-GEN1 (764751) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_378 | Single Phase Fault with Stuck Breaker on GEN-2020-043161.00 (764720) 161 kV Bus a. Apply Fault at the GEN-2020-043161.00 (764720) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-043 (764720) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-043 (764720) 161.0 kV to G20-043-GEN1 (764721) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_379 | Single Phase Fault with Stuck Breaker on GEN-2020-044161.00 (764735) 161 kV Bus a. Apply Fault at the GEN-2020-044161.00 (764735) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-044 (764735) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-044 (764735) 161.0 kV to G20-044-GEN1 (764736) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_380 | Single Phase Fault with Stuck Breaker on GEN-2020-069115.00 (764465) 115 kV Bus a. Apply Fault at the GEN-2020-069115.00 (764465) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-069 (764465) 115.0 kV to G20-069-XFM1 (764468) 34.5 kV Two Winding #1 b.2. GEN-2020-069 (764465) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_381 | Single Phase Fault with Stuck Breaker on GEN-2020-070345.00 (765025) 345 kV Bus a. Apply Fault at the GEN-2020-070345.00 (765025) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-070 (765025) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-070 (765025) 345.0 kV to G20-070-XFM1 (765028) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_382 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_383 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_384 | Single Phase Fault with Stuck Breaker on GEN-2020-077115.00 (764480) 115 kV Bus a. Apply Fault at the GEN-2020-077115.00 (764480) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-077 (764480) 115.0 kV to G20-077-XFM1 (764483) 34.5 kV Two Winding #1 b.2. GEN-2020-077 (764480) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_385 | Single Phase Fault with Stuck Breaker on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_386 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to CARLJCT7 (640105) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_387 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_388 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_389 | Single Phase Fault with Stuck Breaker on GEN-2020-078161.00 (764765) 161 kV Bus a. Apply Fault at the GEN-2020-078161.00 (764765) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-078 (764765) 161.0 kV to G20-078-XFM1 (764768) 34.5 kV Two Winding #1 b.2. GEN-2020-078 (764765) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_390 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM2 (762784) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM2 (762784) 34.5 kV to G18-043-GSU2 (762785) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_391 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM3 (762787) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM3 (762787) 34.5 kV to G18-043-GSU3 (762788) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_392 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-084-XFM1 (764783) 34.5 kV to G20-084-GSU1 (764782) 34.5 kV Transmission Circuit #1 b.2. G20-084-XFM1 (764783) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_393 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-084-XFM2 (764786) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G20-084-XFM2 (764786) 34.5 kV to G20-084-GSU2 (764785) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_394 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_395 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM1 (762781) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM1 (762781) 34.5 kV to G18-043-GSU1 (762782) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_396 | Single Phase Fault with Stuck Breaker on GEN-2020-094345.00 (764795) 345 kV Bus a. Apply Fault at the GEN-2020-094345.00 (764795) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-094 (764795) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-094 (764795) 345.0 kV to G20-094-XFM1 (764798) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_397 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_398 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB4 (659210) 230 kV Bus a. Apply Fault at the SIDNEY__-MB4 (659210) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_399 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_400 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_401 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_402 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_403 | Single Phase Fault with Stuck Breaker on ORLEANS7 (640310) 115 kV Bus a. Apply Fault at the ORLEANS7 (640310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORLEANS7 (640310) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_404 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_405 | Single Phase Fault with Stuck Breaker on VALTN.W7 (640394) 115 kV Bus a. Apply Fault at the VALTN.W7 (640394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALTN.W7 (640394) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_406 | Single Phase Fault with Stuck Breaker on CODY 7 (640117) 115 kV Bus a. Apply Fault at the CODY 7 (640117) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CODY 7 (640117) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_407 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_408 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_409 | Single Phase Fault with Stuck Breaker on FAIRBRY7 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_410 | Single Phase Fault with Stuck Breaker on HEBRN N7 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_411 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_412 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_413 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Local_Fault_414 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_033 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_045 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_046 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_047 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_048 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_051 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_052 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_053 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_054 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_055 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_056 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_057 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_058 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_059 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_060 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_061 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_062 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25S | Transfer | G03_P4_Regional_Fault_063 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_001 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_002 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_003 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_004 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_005 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_006 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 b.2. 2MAURER (346048) 69.0 kV to 5MAURER 2 (344558) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_007 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_008 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_009 | 3 Phase fault on 5COMPTN 161.00 (300719) 161 kV Bus a. Apply fault at the 5COMPTN 161.00 (300719) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COMPTN (300719) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_010 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5HILLTOP% (338110) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 b.3. BUFORD 5 (504440) 161.0 kV to NORFORK5 (505448) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_011 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 b.4. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_012 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_013 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to RVS438 5 (547497) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_014 | 3 Phase fault on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_015 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_016 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_017 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_018 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X1 1 (505473) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_019 | 3 Phase fault on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_020 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_021 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_022 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_023 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_024 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_025 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_026 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_027 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_028 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_029 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_030 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_031 | 3 Phase fault on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.2. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.3. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.6. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_032 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_033 | 3 Phase fault on APCITY 2 69.000 (541306) 69 kV Bus a. Apply fault at the APCITY 2 69.000 (541306) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to URICH 2 (541305) 69.0 kV Transmission Circuit #1 b.3. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 b.4. APCITY 2 (541306) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 b.5. APCITY 2 (541306) 69.0 kV to ASGI-2018-00 (762361) 69.0 kV Transmission Circuit #1 b.6. APCITY 2 (541306) 69.0 kV to APCITY1 (541325) 34.5 kV to APCITY_TER1 (541326) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_034 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 b.2. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.3. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.4. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.5. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.6. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_035 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_036 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.2. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.4. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.5. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.6. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_037 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_038 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_039 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_040 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_041 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_042 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_043 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_044 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_045 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_046 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_047 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_048 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_049 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.2. 5BUTLER (301342) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_050 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_051 | 3 Phase fault on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_052 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_053 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_054 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.2. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_055 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_056 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 b.2. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_057 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_058 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_059 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 b.2. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 b.3. NORTON 5 (543064) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_060 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLA 5 (543069) 161.0 kV to OSAWAT 5 (543112) 161.0 kV Transmission Circuit #1 b.2. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_061 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_062 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_063 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_064 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_065 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_066 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_067 | 3 Phase fault on WINJT S5 161.00 (543010) 161 kV Bus a. Apply fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_068 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_069 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_070 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_071 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Fixed Shunt Device b.3. MC REAC2 (541412) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_072 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_073 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_074 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_075 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_076 | 3 Phase fault on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.2. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.3. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.4. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.5. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.6. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_077 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.3. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.4. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.5. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_078 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_079 | 3 Phase fault on APCITY 2 69.000 (541306) 69 kV Bus a. Apply fault at the APCITY 2 69.000 (541306) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. APCITY 2 (541306) 69.0 kV to NEVADA 2 (541308) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 b.3. APCITY 2 (541306) 69.0 kV to ASGI-2018-00 (762361) 69.0 kV Transmission Circuit #1 b.4. APCITY 2 (541306) 69.0 kV to APCITY1 (541325) 34.5 kV to APCITY_TER1 (541326) 2.4 kV Three Winding #11 b.5. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 b.6. URICHTP2 (541304) 69.0 kV to URICH 2 (541305) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_080 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.5. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 b.6. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_081 | 3 Phase fault on RAYTAP 69.000 (541348) 69 kV Bus a. Apply fault at the RAYTAP 69.000 (541348) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.2. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_082 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIEW2 (541385) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to CNTRVIEW2 (541385) 69.0 kV Transmission Circuit #1 b.3. HOLDEN 2 (541278) 69.0 kV to HLDENTP2 (541386) 69.0 kV Transmission Circuit #1 b.4. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 b.5. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 b.6. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_083 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. WBURGP 2 (541268) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 b.3. POSTOAK2 (541300) 69.0 kV to POSTOAK1 (541373) 34.5 kV to POSTOAK_TER1 (541374) 2.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_084 | 3 Phase fault on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. CORDER 2 (543097) 69.0 kV to CORDER1 (543150) 12.5 kV to CORDER_TER1 (543151) 7.2 kV Three Winding #1 b.3. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.4. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.5. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.6. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_085 | 3 Phase fault on WHGNSVL2 69.000 (543102) 69 kV Bus a. Apply fault at the WHGNSVL2 69.000 (543102) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 b.2. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.3. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 b.4. HIGNSVL2 (543099) 69.0 kV to HGNSVL1 (543152) 12.5 kV to HGNSVL_TER1 (543153) 2.4 kV Three Winding #1 b.5. LEXNTON2 (541265) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.6. 13&40 2 (541266) 69.0 kV to MAYVWTP2 (543096) 69.0 kV Transmission Circuit #1 b.7. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 b.8. WHGNSVL2 (543102) 69.0 kV to WHGNSVL1 (543154) 12.5 kV to WHGNSVL_TER1 (543155) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_086 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 b.2. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 b.3. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_087 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_088 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_089 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_090 | 3 Phase fault on OSAWTM_CAP5 161.00 (543135) 161 kV Bus a. Apply fault at the OSAWTM_CAP5 161.00 (543135) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWTM_CAP5 (543135) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_091 | 3 Phase fault on SWAVCAP5 161.00 (543013) 161 kV Bus a. Apply fault at the SWAVCAP5 161.00 (543013) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP5 (543013) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_092 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIB REA1 (541414) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_093 | 3 Phase fault on SWAVCAP2 69.000 (543012) 69 kV Bus a. Apply fault at the SWAVCAP2 69.000 (543012) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVCAP2 (543012) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_094 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_095 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_096 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.6. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_097 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_098 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_099 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_100 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_101 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_102 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_103 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_104 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_105 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_106 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_107 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_108 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_109 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_110 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_111 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_112 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_113 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_114 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_115 | 3 Phase fault on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_116 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_117 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_118 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.3. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_119 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_120 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_121 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_122 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_123 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_124 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to ULYSPLT3 (531490) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_125 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.2. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 b.3. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_126 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_127 | 3 Phase fault on HICKOCK3 115.00 (531378) 115 kV Bus a. Apply fault at the HICKOCK3 115.00 (531378) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HICKOCK3 (531378) 115.0 kV to PIONEER3 (531391) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_128 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_129 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_130 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_131 | 3 Phase fault on SAT-TAP3 115.00 (531442) 115 kV Bus a. Apply fault at the SAT-TAP3 115.00 (531442) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.2. PIONTAP3 (531392) 115.0 kV to SAT-TAP3 (531442) 115.0 kV Transmission Circuit #1 b.3. SAT-TAP3 (531442) 115.0 kV to SATMKEC3 (539691) 115.0 kV Transmission Circuit #1 b.4. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_132 | 3 Phase fault on N-CIMRN3 115.00 (539749) 115 kV Bus a. Apply fault at the N-CIMRN3 115.00 (539749) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.2. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 b.3. N-CIMRN3 (539749) 115.0 kV to N-CMRN 1 (539764) 34.5 kV to N-CMRN-T (539967) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_133 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 b.2. SELKIRK3 (531434) 115.0 kV to TRIB SW3 (531438) 115.0 kV Transmission Circuit #1 b.3. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_134 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.2. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.3. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_135 | 3 Phase fault on PILE 3 115.00 (531432) 115 kV Bus a. Apply fault at the PILE 3 115.00 (531432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_136 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_137 | 3 Phase fault on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_138 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 b.2. CUDAHY 3 (539659) 115.0 kV to CRKCK 3 (539783) 115.0 kV Transmission Circuit #1 b.3. CUDAHY 3 (539659) 115.0 kV to CUDAHY 1 (539706) 34.5 kV to CUDAHY-T (539906) 13.8 kV Three Winding #1 b.4. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 b.5. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 b.6. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_139 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_140 | 3 Phase fault on HAYNE3 115.00 (539640) 115 kV Bus a. Apply fault at the HAYNE3 115.00 (539640) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYNE3 (539640) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_141 | 3 Phase fault on NATBEEF3 115.00 (539751) 115 kV Bus a. Apply fault at the NATBEEF3 115.00 (539751) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 b.2. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_142 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_143 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_144 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_145 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.2. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.3. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.4. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_146 | 3 Phase fault on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 b.2. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 b.3. EHALLTP3 (539660) 115.0 kV to ESTHLL 1 (539757) 34.5 kV to ESTHLL-T (539966) 13.8 kV Three Winding #1 b.4. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_147 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_148 | 3 Phase fault on PHLBURG3 115.00 (539685) 115 kV Bus a. Apply fault at the PHLBURG3 115.00 (539685) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_149 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.2. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_150 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_151 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_152 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_153 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_154 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_155 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_156 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_157 | 3 Phase fault on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL3 (539701) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_158 | 3 Phase fault on 5CLEVCOV 161.00 (300718) 161 kV Bus a. Apply fault at the 5CLEVCOV 161.00 (300718) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLEVCOV (300718) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 b.2. 5CLEVCOV (300718) 161.0 kV to 5S.LEAD HILL (338120) 161.0 kV Transmission Circuit #1 b.3. 5S.LEAD HILL (338120) 161.0 kV to BULL SH W5 (505461) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_159 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 b.2. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_160 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.3. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_161 | 3 Phase fault on 27CROCO3 115.00 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 115.00 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_162 | 3 Phase fault on QUINTON3 115.00 (533172) 115 kV Bus a. Apply fault at the QUINTON3 115.00 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_163 | 3 Phase fault on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_164 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_165 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_166 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_167 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_168 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_169 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_170 | 3 Phase fault on SHERWOD3 115.00 (533194) 115 kV Bus a. Apply fault at the SHERWOD3 115.00 (533194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_171 | 3 Phase fault on KEENE 3 115.00 (533167) 115 kV Bus a. Apply fault at the KEENE 3 115.00 (533167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.2. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_172 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.2. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_173 | 3 Phase fault on GEARY 3 115.00 (533336) 115 kV Bus a. Apply fault at the GEARY 3 115.00 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_174 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_175 | 3 Phase fault on 54&MERI3 115.00 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 115.00 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_176 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_177 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_178 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_179 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_180 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_181 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_182 | 3 Phase fault on EMANHAT3 115.00 (533326) 115 kV Bus a. Apply fault at the EMANHAT3 115.00 (533326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_183 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_184 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_185 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_186 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_187 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_188 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_189 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_190 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_191 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_192 | 3 Phase fault on HALLMRK3 115.00 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 115.00 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.3. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_193 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_194 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_195 | 3 Phase fault on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_196 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_197 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.2. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_198 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_199 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_200 | 3 Phase fault on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_201 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_202 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_203 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_204 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_205 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_206 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_207 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_208 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_209 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_210 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_211 | 3 Phase fault on UNIONRG3 115.00 (533359) 115 kV Bus a. Apply fault at the UNIONRG3 115.00 (533359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG3 (533359) 115.0 kV to TCHOPE 3 (533360) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_212 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_213 | 3 Phase fault on 29TH 4 138.00 (533024) 138 kV Bus a. Apply fault at the 29TH 4 138.00 (533024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_214 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_215 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_216 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_217 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_218 | 3 Phase fault on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_219 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_220 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_221 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_222 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_223 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_224 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_225 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_226 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_227 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_228 | 3 Phase fault on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_229 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_230 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_231 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_232 | 3 Phase fault on COFFEYT4 138.00 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 138.00 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.6. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_233 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_234 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_235 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_236 | 3 Phase fault on FARBER 4 138.00 (533042) 138 kV Bus a. Apply fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_237 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_238 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_239 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.3. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_240 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_241 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.2. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_242 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_243 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_244 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_245 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_246 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_247 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_248 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_249 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_250 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_251 | 3 Phase fault on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_252 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_253 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_254 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_255 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_256 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_257 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_258 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_259 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_260 | 3 Phase fault on JEC 6 230.00 (532852) 230 kV Bus a. Apply fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_261 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_262 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_263 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_264 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_265 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_266 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_267 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_268 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_269 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_270 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_271 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_272 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_273 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_274 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_275 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_276 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_277 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_278 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_279 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_280 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_281 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_282 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_283 | 3 Phase fault on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_284 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_285 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_286 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_287 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_288 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_289 | 3 Phase fault on KINGMAN7 345.00 (532783) 345 kV Bus a. Apply fault at the KINGMAN7 345.00 (532783) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_290 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_291 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_292 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_293 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_294 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_295 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_296 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_297 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_298 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_299 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_300 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_301 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_302 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_303 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_304 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_305 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_306 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.2. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_307 | 3 Phase fault on WARE 2 69.000 (533652) 69 kV Bus a. Apply fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.3. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_308 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_309 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.2. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_310 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_311 | 3 Phase fault on LITCH S2 69.000 (533766) 69 kV Bus a. Apply fault at the LITCH S2 69.000 (533766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_312 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_313 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_314 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_315 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_316 | 3 Phase fault on HUDSON-2 69.000 (533763) 69 kV Bus a. Apply fault at the HUDSON-2 69.000 (533763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON-2 (533763) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_317 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_318 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_319 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_320 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_321 | 3 Phase fault on CC2SHAR2 69.000 (533629) 69 kV Bus a. Apply fault at the CC2SHAR2 69.000 (533629) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CC2SHAR2 (533629) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_322 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_323 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.3. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_324 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_325 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_326 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_327 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_328 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_329 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_330 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_331 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_332 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_333 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_334 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_335 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_336 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_337 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_338 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_339 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_340 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_341 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_342 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_343 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_344 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_345 | 3 Phase fault on SW DISP PLT5161.00 (549960) 161 kV Bus a. Apply fault at the SW DISP PLT5161.00 (549960) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 b.2. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_346 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 b.2. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_347 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to NICHOLS 2 (549925) 69.0 kV to NICHOL XF1 1 (549940) 13.2 kV Three Winding #1 b.4. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 b.5. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_348 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 b.2. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_349 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_350 | 3 Phase fault on SKIATOK4 138.00 (509884) 138 kV Bus a. Apply fault at the SKIATOK4 138.00 (509884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKIATOK4 (509884) 138.0 kV to BARNSAL4 (510388) 138.0 kV Transmission Circuit #1 b.2. T.NO.--4 (509817) 138.0 kV to SKIATOK4 (509884) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_351 | 3 Phase fault on MAYO--S4 138.00 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 138.00 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 (509780) 138.0 kV to BANNTAP4 (509785) 138.0 kV Transmission Circuit #1 b.2. BANNTAP4 (509785) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 b.3. MINGO-S4 (509761) 138.0 kV to T.S.E.-4 (509811) 138.0 kV Transmission Circuit #1 b.4. MINGO-S4 (509761) 138.0 kV to MAYO--S4 (509780) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_352 | 3 Phase fault on LLANETP4 138.00 (509804) 138 kV Bus a. Apply fault at the LLANETP4 138.00 (509804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.2. CATOOSA4 (509790) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.3. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 b.4. LLAN WT4 (509770) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 b.5. LLAN WT4 (509770) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.6. DAWSON-4 (509792) 138.0 kV to DAWSONT4 (509803) 138.0 kV Transmission Circuit #1 b.7. DAWSONT4 (509803) 138.0 kV to N21ST--4 (509866) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_353 | 3 Phase fault on ALWUETP4 138.00 (510429) 138 kV Bus a. Apply fault at the ALWUETP4 138.00 (510429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 b.2. N.E.S.-4 (510396) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.3. CHELSA4 (510410) 138.0 kV to HAWTHRN4 (510413) 138.0 kV Transmission Circuit #1 b.4. CHELSA4 (510410) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_354 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_355 | 3 Phase fault on GROVE 5 161.00 (510411) 161 kV Bus a. Apply fault at the GROVE 5 161.00 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 (510411) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_356 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_357 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_358 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_359 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_360 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_361 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_362 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_363 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_364 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_365 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_366 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_367 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_368 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_369 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_370 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_371 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_372 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_373 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_374 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_375 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_376 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_377 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_378 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_379 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_380 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_381 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC2 (510418) 69.0 kV to VINTAJC4 (510417) 138.0 kV to VINJT1-1 (510367) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_382 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_383 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_384 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_385 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_386 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_387 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_388 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_389 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.2. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_390 | 3 Phase fault on 5KETONVL 161.00 (300997) 161 kV Bus a. Apply fault at the 5KETONVL 161.00 (300997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. 5KETONVL (300997) 161.0 kV to COLINS 5 (512627) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_391 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_392 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_393 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_394 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_395 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_396 | 3 Phase fault on PENSA 5 161.00 (512654) 161 kV Bus a. Apply fault at the PENSA 5 161.00 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENSA 5 (512654) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_397 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_398 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_399 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_400 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_401 | 3 Phase fault on WMAIN ST5 161.00 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 161.00 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_402 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_403 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_404 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 b.2. 2MONKEY (301465) 69.0 kV to 2NEWPORT (301467) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_405 | 3 Phase fault on SAILBOA2 69.000 (510409) 69 kV Bus a. Apply fault at the SAILBOA2 69.000 (510409) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAILBOA2 (510409) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_406 | 3 Phase fault on CLEORTP2 69.000 (512692) 69 kV Bus a. Apply fault at the CLEORTP2 69.000 (512692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.2. PENSA 2 (512628) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 b.3. 2CLEORA (301460) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_407 | 3 Phase fault on MIAMI3 2 69.000 (513024) 69 kV Bus a. Apply fault at the MIAMI3 2 69.000 (513024) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.2. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.3. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_408 | 3 Phase fault on ESH TP 2 69.000 (512680) 69 kV Bus a. Apply fault at the ESH TP 2 69.000 (512680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP (301468) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.2. 2VINITAHQ (300983) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.3. VINITA-2 (510404) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.4. VINEOTP2 (512673) 69.0 kV to ESH TP 2 (512680) 69.0 kV Transmission Circuit #1 b.5. 2VIN NEO (301478) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.6. 2J6 (300829) 69.0 kV to VINEOTP2 (512673) 69.0 kV Transmission Circuit #1 b.7. 2J6 (300829) 69.0 kV to AFTP TP2 (512620) 69.0 kV Transmission Circuit #1 b.8. AFTP TP2 (512620) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.9. AFTONTP2 (510415) 69.0 kV to AFTN-EX2 (510428) 69.0 kV Transmission Circuit #1 b.10. AFTONTP2 (510415) 69.0 kV to A-CONT 2 (510427) 69.0 kV Transmission Circuit #1 b.11. AFTONTP2 (510415) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 b.12. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_409 | 3 Phase fault on FAIRTAP2 69.000 (512708) 69 kV Bus a. Apply fault at the FAIRTAP2 69.000 (512708) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 b.2. FAIRNEO2 (512691) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.3. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 b.4. FAIRTAP2 (512708) 69.0 kV to FRL363 2 (547583) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_410 | 3 Phase fault on MAIDTP2 69.000 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 69.000 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 (512625) 69.0 kV to GRDA1 2 (512727) 69.0 kV Transmission Circuit #1 b.2. MAIDTP2 (512625) 69.0 kV to HUNT 2 (512671) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_411 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 b.2. MIAMI3 2 (513024) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.3. MIAMI4 2 (513022) 69.0 kV to COMMTP 2 (513026) 69.0 kV Transmission Circuit #1 b.4. MIAMI1 2 (513020) 69.0 kV to MIAMI4 2 (513022) 69.0 kV Transmission Circuit #1 b.5. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_412 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_413 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_414 | 3 Phase fault on 2WLKRTP 69.000 (300760) 69 kV Bus a. Apply fault at the 2WLKRTP 69.000 (300760) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 b.2. 2SENECA (300830) 69.0 kV to 2MIAETP (300852) 69.0 kV Transmission Circuit #1 b.3. 2WLKRTP (300760) 69.0 kV to 2SENECA (300830) 69.0 kV Transmission Circuit #1 b.4. 2WLKRTP (300760) 69.0 kV to 2WLKRVL (300761) 69.0 kV Transmission Circuit #1 b.5. 2NEOSHO (300750) 69.0 kV to 2WLKRTP (300760) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_415 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_416 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_417 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_418 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_419 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_420 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_421 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_422 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_423 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_424 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 b.4. TOLK 7 (525549) 345.0 kV to CROSSROADS 7 (527656) 345.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_425 | 3 Phase fault on LAMB_CNTY 6230.00 (525637) 230 kV Bus a. Apply fault at the LAMB_CNTY 6230.00 (525637) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 b.2. LAMB_CNTY 6 (525637) 230.0 kV to LAMB_CNTY 3 (525636) 115.0 kV to LAMB_TR3 1 (525633) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_426 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 b.2. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_427 | 3 Phase fault on EAST_PLANT 6230.00 (524163) 230 kV Bus a. Apply fault at the EAST_PLANT 6230.00 (524163) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST_PLANT 6 (524163) 230.0 kV to EAST_PLANT 3 (524162) 115.0 kV to EPLANT_TR3 1 (524160) 13.2 kV Three Winding #1 b.4. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_428 | 3 Phase fault on OCHILTREE 6230.00 (523155) 230 kV Bus a. Apply fault at the OCHILTREE 6230.00 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OCHILTREE 6 (523155) 230.0 kV to OCHILTREE 3 (523154) 115.0 kV to OCHLTRE_TR11 (523151) 13.2 kV Three Winding #1 b.4. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_429 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 b.4. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_430 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_431 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to RIVERVIEW 3 (523377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_432 | 3 Phase fault on SPEARMAN 3115.00 (523186) 115 kV Bus a. Apply fault at the SPEARMAN 3115.00 (523186) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARMAN 3 (523186) 115.0 kV to PRINGLE 3 (523266) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_433 | 3 Phase fault on FAIN 3115.00 (523339) 115 kV Bus a. Apply fault at the FAIN 3115.00 (523339) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 b.2. FAIN 3 (523339) 115.0 kV to NICHOLS 3 (524043) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_434 | 3 Phase fault on EXELL_TP 3115.00 (523332) 115 kV Bus a. Apply fault at the EXELL_TP 3115.00 (523332) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUMAS_19ST 3 (523318) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 b.2. MCDWL_CREEK3 (523322) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 b.3. EXELL 3 (523325) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_435 | 3 Phase fault on Q_RYTON_TP 3115.00 (523478) 115 kV Bus a. Apply fault at the Q_RYTON_TP 3115.00 (523478) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 b.2. BLKHAWK_E 3 (523346) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_436 | 3 Phase fault on HALE_CNTY 3115.00 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3115.00 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 (525454) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_437 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to BAILEYCO 3 (525028) 115.0 kV Transmission Circuit #1 b.2. MULESHVALLY3 (525018) 115.0 kV to MULSHVLY_TP3 (525019) 115.0 kV Transmission Circuit #1 b.3. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_438 | 3 Phase fault on TXPHSF 3115.00 (523106) 115 kV Bus a. Apply fault at the TXPHSF 3115.00 (523106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPHSF 3 (523106) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_439 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-KELLEY +3 (525050) 115.0 kV to BC-EARTH 3 (525056) 115.0 kV Transmission Circuit #1 b.2. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_440 | 3 Phase fault on KRESS_INT 3115.00 (525192) 115 kV Bus a. Apply fault at the KRESS_INT 3115.00 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KRESS_INT 3 (525192) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_441 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to LAMTON 3 (525414) 115.0 kV Transmission Circuit #1 b.2. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_442 | 3 Phase fault on OUTPOST 3115.00 (524243) 115 kV Bus a. Apply fault at the OUTPOST 3115.00 (524243) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OUTPOST 3 (524243) 115.0 kV to BUSHLAND 3 (524266) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_443 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_444 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_445 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_446 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.7. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.8. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.9. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.10. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.11. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_447 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_448 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_449 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_450 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_451 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_452 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_453 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_454 | 3 Phase fault on WWDPST 4 138.00 (515425) 138 kV Bus a. Apply fault at the WWDPST 4 138.00 (515425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_455 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to KEENAN 4 (515394) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_456 | 3 Phase fault on SOONER 7 345.00 (514803) 345 kV Bus a. Apply fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_457 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_458 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_459 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_460 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_461 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_462 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_463 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_464 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_465 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_466 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. This issue is also present in the Base case. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_467 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_468 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_469 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_470 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_471 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_472 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_473 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_474 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_475 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_476 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 b.2. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_477 | 3 Phase fault on BOL431 5 161.00 (547493) 161 kV Bus a. Apply fault at the BOL431 5 161.00 (547493) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOL 73 5 (547464) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 b.2. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_478 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 b.2. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_479 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_480 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_481 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_482 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_483 | 3 Phase fault on 5MAURER 2 161.00 (344558) 161 kV Bus a. Apply fault at the 5MAURER 2 161.00 (344558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 2 (344558) 161.0 kV to CAROLTN5 (543060) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_484 | 3 Phase fault on 5OVERTON 2 161.00 (345411) 161 kV Bus a. Apply fault at the 5OVERTON 2 161.00 (345411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON 2 (345411) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_485 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.2. 1CALIF (346027) 34.5 kV to 5CALIF UE 1 (344233) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_486 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOYMART 2 (344041) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 b.2. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 b.3. 5MCBAINB2 (301489) 161.0 kV to 5MCBAIN T (345071) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_487 | 3 Phase fault on 5MOBTAP 161.00 (300126) 161 kV Bus a. Apply fault at the 5MOBTAP 161.00 (300126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHILB1 (300120) 161.0 kV to 5MOBTAP (300126) 161.0 kV Transmission Circuit #1 b.2. 5MOBTAP (300126) 161.0 kV to 5HIGBEEB2 (301494) 161.0 kV Transmission Circuit #1 b.3. 5MOBTAP (300126) 161.0 kV to 5MOBERLY (345221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_488 | 3 Phase fault on 5HUNTSDL 161.00 (300500) 161 kV Bus a. Apply fault at the 5HUNTSDL 161.00 (300500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUNTSDL (300500) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_489 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to 5MAURER 1 (344557) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_490 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_491 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MAURER 1 (344557) 161.0 kV to 5MAURER 2 (344558) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_492 | 3 Phase fault on 5OVERTON 161.00 (345409) 161 kV Bus a. Apply fault at the 5OVERTON 161.00 (345409) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OVERTON (345409) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_493 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 b.2. 5MPLTAP (300036) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 b.3. 5MPLTAP (300036) 161.0 kV to 5LATHROP (344923) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_494 | 3 Phase fault on 7KINGDM 345.00 (300043) 345 kV Bus a. Apply fault at the 7KINGDM 345.00 (300043) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KINGDM (300043) 345.0 kV to 7MCCRED (300044) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_495 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7THOMHL (300049) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_496 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to SOONER 7 (514803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_497 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_498 | 3 Phase fault on 5MPLTAP 161.00 (300036) 161 kV Bus a. Apply fault at the 5MPLTAP 161.00 (300036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MPLTAP (300036) 161.0 kV to 5LATHRP (300091) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_499 | 3 Phase fault on 7FRANKS 345.00 (300041) 345 kV Bus a. Apply fault at the 7FRANKS 345.00 (300041) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FRANKS (300041) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_500 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_501 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_502 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to VSC2_3 (992003) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_503 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_504 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_505 | 3 Phase fault on 5CAMDEN 161.00 (300064) 161 kV Bus a. Apply fault at the 5CAMDEN 161.00 (300064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAMDEN (300064) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_506 | 3 Phase fault on 5HIGBEEB1 161.00 (300066) 161 kV Bus a. Apply fault at the 5HIGBEEB1 161.00 (300066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HIGBEEB1 (300066) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_507 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5HYDERHL (300793) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_508 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_509 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLARK (300070) 161.0 kV to NEVADA 5 (541208) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_510 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_511 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_512 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_513 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_514 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_515 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5HUBEN (300088) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_516 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COFFMN (300072) 161.0 kV to 5LEBANN (300092) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_517 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_518 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_519 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5MRSHFL (300102) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_520 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5PHLIPS (300109) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_521 | 3 Phase fault on 5HUBEN 161.00 (300088) 161 kV Bus a. Apply fault at the 5HUBEN 161.00 (300088) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 5WHISPR (301077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_522 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5BTLFD (300348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_523 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5NIXA-1 (300678) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_524 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JAMESV (300089) 161.0 kV to 5RIVRDL (300726) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_525 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LATHRP (300091) 161.0 kV to 5MOCITYB1 (301563) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_526 | 3 Phase fault on 5MANSFDMN 161.00 (300095) 161 kV Bus a. Apply fault at the 5MANSFDMN 161.00 (300095) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MANSFDMN (300095) 161.0 kV to 5LOGAN (301161) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_527 | 3 Phase fault on 5MOCITYB2 161.00 (300098) 161 kV Bus a. Apply fault at the 5MOCITYB2 161.00 (300098) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB2 (300098) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_528 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to 5MORGANXF2 (301622) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_529 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_530 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to DAD368 5 (547478) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_531 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORGAN (300101) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_532 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MRSHFL (300102) 161.0 kV to 5HOLMAN (301159) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_533 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NORTON (300105) 161.0 kV to 5NORTONTP (301567) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_534 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_535 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_536 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_537 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_538 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_539 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_540 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_541 | 3 Phase fault on 5STKAEC 161.00 (300118) 161 kV Bus a. Apply fault at the 5STKAEC 161.00 (300118) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STKAEC (300118) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_542 | 3 Phase fault on 5THMHLB2 161.00 (300132) 161 kV Bus a. Apply fault at the 5THMHLB2 161.00 (300132) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB2 (300132) 161.0 kV to 5THMHLB4 (301443) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_543 | 3 Phase fault on 2KNOXVL 69.000 (300204) 69 kV Bus a. Apply fault at the 2KNOXVL 69.000 (300204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOXVL (300204) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_544 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2MOCITY (300304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_545 | 3 Phase fault on 2KEARNY 69.000 (300301) 69 kV Bus a. Apply fault at the 2KEARNY 69.000 (300301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KEARNY (300301) 69.0 kV to 2SMRSET (300311) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_546 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2ORRICK (300305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_547 | 3 Phase fault on 2MOCITY 69.000 (300304) 69 kV Bus a. Apply fault at the 2MOCITY 69.000 (300304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_548 | 3 Phase fault on 2SMITHV 69.000 (300310) 69 kV Bus a. Apply fault at the 2SMITHV 69.000 (300310) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SMITHV (300310) 69.0 kV to 2LMV (300526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_549 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2MAGNOL (300328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_550 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_551 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_552 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_553 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_554 | 3 Phase fault on 5BTLFD 161.00 (300348) 161 kV Bus a. Apply fault at the 5BTLFD 161.00 (300348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BTLFD (300348) 161.0 kV to JTEC 5 (549954) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_555 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_556 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_557 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_558 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_559 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_560 | 3 Phase fault on 2BELLAMY 69.000 (300646) 69 kV Bus a. Apply fault at the 2BELLAMY 69.000 (300646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BELLAMY (300646) 69.0 kV to 2BLLMYTP (300647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_561 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_562 | 3 Phase fault on 2BLLMYTP 69.000 (300647) 69 kV Bus a. Apply fault at the 2BLLMYTP 69.000 (300647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLLMYTP (300647) 69.0 kV to 2MILO (300654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_563 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2LAMR (300651) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_564 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to 2MEDOC (300653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_565 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_566 | 3 Phase fault on 2KENOMA 69.000 (300650) 69 kV Bus a. Apply fault at the 2KENOMA 69.000 (300650) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KENOMA (300650) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_567 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_568 | 3 Phase fault on 2LAMR 69.000 (300651) 69 kV Bus a. Apply fault at the 2LAMR 69.000 (300651) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_569 | 3 Phase fault on 2LAMRCTS 69.000 (300652) 69 kV Bus a. Apply fault at the 2LAMRCTS 69.000 (300652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTS (300652) 69.0 kV to 2LAMARPT (300685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_570 | 3 Phase fault on 2LAMRCTN 69.000 (300655) 69 kV Bus a. Apply fault at the 2LAMRCTN 69.000 (300655) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMRCTN (300655) 69.0 kV to 2JACK ST (300656) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_571 | 3 Phase fault on 2CRANE 69.000 (300667) 69 kV Bus a. Apply fault at the 2CRANE 69.000 (300667) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CRANE (300667) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_572 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2GRNFLD (300672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_573 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_574 | 3 Phase fault on 2DADEVL 69.000 (300668) 69 kV Bus a. Apply fault at the 2DADEVL 69.000 (300668) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DADEVL (300668) 69.0 kV to 2BONA (300800) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_575 | 3 Phase fault on 2ELWOOD 69.000 (300669) 69 kV Bus a. Apply fault at the 2ELWOOD 69.000 (300669) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELWOOD (300669) 69.0 kV to SPRGFLD2 (505494) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_576 | 3 Phase fault on 5NIXA-1 161.00 (300678) 161 kV Bus a. Apply fault at the 5NIXA-1 161.00 (300678) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NIXA-1 (300678) 161.0 kV to SPRGFLD5 (505492) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_577 | 3 Phase fault on 2PRDYTP 69.000 (300679) 69 kV Bus a. Apply fault at the 2PRDYTP 69.000 (300679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PRDYTP (300679) 69.0 kV to 2VERONA (300680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_578 | 3 Phase fault on 2VERONA 69.000 (300680) 69 kV Bus a. Apply fault at the 2VERONA 69.000 (300680) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VERONA (300680) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_579 | 3 Phase fault on 2AUSTIN 69.000 (300688) 69 kV Bus a. Apply fault at the 2AUSTIN 69.000 (300688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AUSTIN (300688) 69.0 kV to 2ELYNTP (300699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_580 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_581 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_582 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_583 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_584 | 3 Phase fault on 2ELYNNE 69.000 (300698) 69 kV Bus a. Apply fault at the 2ELYNNE 69.000 (300698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNNE (300698) 69.0 kV to 2SHARSNV (300709) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_585 | 3 Phase fault on 2ELYNTP 69.000 (300699) 69 kV Bus a. Apply fault at the 2ELYNTP 69.000 (300699) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNTP (300699) 69.0 kV to 2PECULR (300705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_586 | 3 Phase fault on 2ELYNTP 69.000 (300699) 69 kV Bus a. Apply fault at the 2ELYNTP 69.000 (300699) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELYNTP (300699) 69.0 kV to 2SHARSNV (300709) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_587 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_588 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_589 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_590 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_591 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_592 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2NEOSHO (300750) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_593 | 3 Phase fault on 2NEOSAC 69.000 (300748) 69 kV Bus a. Apply fault at the 2NEOSAC 69.000 (300748) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to 2SWTWT (300758) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_594 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_595 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_596 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2MORGAN (300782) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_597 | 3 Phase fault on 2EUDORA 69.000 (300774) 69 kV Bus a. Apply fault at the 2EUDORA 69.000 (300774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2EUDORA (300774) 69.0 kV to 2SLAGLE (300788) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_598 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_599 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_600 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_601 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_602 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_603 | 3 Phase fault on 2MIAETP 69.000 (300852) 69 kV Bus a. Apply fault at the 2MIAETP 69.000 (300852) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MIAETP (300852) 69.0 kV to MIAMI 2 (512630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_604 | 3 Phase fault on 5KETONVL 161.00 (300997) 161 kV Bus a. Apply fault at the 5KETONVL 161.00 (300997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_605 | 3 Phase fault on 5LOGAN 161.00 (301161) 161 kV Bus a. Apply fault at the 5LOGAN 161.00 (301161) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOGAN (301161) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_606 | 3 Phase fault on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BUTLER (301342) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_607 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_608 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_609 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_610 | 3 Phase fault on 5THMHLB4 161.00 (301443) 161 kV Bus a. Apply fault at the 5THMHLB4 161.00 (301443) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5THMHLB4 (301443) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_611 | 3 Phase fault on 2NEWPORT 69.000 (301467) 69 kV Bus a. Apply fault at the 2NEWPORT 69.000 (301467) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEWPORT (301467) 69.0 kV to AFTON 2 (512633) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_612 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_613 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_614 | 3 Phase fault on 5REEDSP 161.00 (301521) 161 kV Bus a. Apply fault at the 5REEDSP 161.00 (301521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5REEDSP (301521) 161.0 kV to RDS295 5 (547473) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_615 | 3 Phase fault on 5CALIF UE 1 161.00 (344233) 161 kV Bus a. Apply fault at the 5CALIF UE 1 161.00 (344233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CALIF UE 1 (344233) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_616 | 3 Phase fault on 5MCBAIN T 161.00 (345071) 161 kV Bus a. Apply fault at the 5MCBAIN T 161.00 (345071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MCBAIN T (345071) 161.0 kV to 5OVERTON 2 (345411) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_617 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_618 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOBERLY (345221) 161.0 kV to 5OVERTON (345409) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_619 | 3 Phase fault on BEAVER 5 161.00 (505480) 161 kV Bus a. Apply fault at the BEAVER 5 161.00 (505480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 5 (505480) 161.0 kV to WASHBURN5 (505485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_620 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_621 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_622 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_623 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_624 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_625 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_626 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_627 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to NIXA 5 (505496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_628 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_629 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_630 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_631 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_632 | 3 Phase fault on NIXA 2 69.000 (505501) 69 kV Bus a. Apply fault at the NIXA 2 69.000 (505501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_633 | 3 Phase fault on NIXA DT2 69.000 (505541) 69 kV Bus a. Apply fault at the NIXA DT2 69.000 (505541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA DT2 (505541) 69.0 kV to NX ESPY2 (505543) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_634 | 3 Phase fault on NX ESPY2 69.000 (505543) 69 kV Bus a. Apply fault at the NX ESPY2 69.000 (505543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NX ESPY2 (505543) 69.0 kV to NIX_SLR_U1_2 (505545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_635 | 3 Phase fault on BA.NO-S4 138.00 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 138.00 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 (509721) 138.0 kV to BA.N-ST4 (509786) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_636 | 3 Phase fault on BA101 S4 138.00 (509737) 138 kV Bus a. Apply fault at the BA101 S4 138.00 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 (509737) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_637 | 3 Phase fault on DENVTAP4 138.00 (509746) 138 kV Bus a. Apply fault at the DENVTAP4 138.00 (509746) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVTAP4 (509746) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_638 | 3 Phase fault on BA81---4 138.00 (509747) 138 kV Bus a. Apply fault at the BA81---4 138.00 (509747) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 (509747) 138.0 kV to BA101-N4 (509769) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_639 | 3 Phase fault on B111---4 138.00 (509767) 138 kV Bus a. Apply fault at the B111---4 138.00 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 (509767) 138.0 kV to BA101ST4 (509768) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_640 | 3 Phase fault on BA101ST4 138.00 (509768) 138 kV Bus a. Apply fault at the BA101ST4 138.00 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 (509768) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_641 | 3 Phase fault on BA101-N4 138.00 (509769) 138 kV Bus a. Apply fault at the BA101-N4 138.00 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 (509769) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_642 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to G16133G16146 (588039) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_643 | 3 Phase fault on BANNTAP4 138.00 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 138.00 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 (509785) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_644 | 3 Phase fault on BA.N-ST4 138.00 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 138.00 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to LLANETP4 (509804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_645 | 3 Phase fault on BA.N-ST4 138.00 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 138.00 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 (509786) 138.0 kV to ONETA--4 (509806) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_646 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to 121LYNN4 (509869) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_647 | 3 Phase fault on ONETA--4 138.00 (509806) 138 kV Bus a. Apply fault at the ONETA--4 138.00 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to BA_71ST4 (509891) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_648 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-ET 4 (509839) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_649 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to CDC-WT 4 (509842) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_650 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to OWASOTP4 (509844) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_651 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to P&P WTP4 (509851) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_652 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to SKIATOK4 (509884) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_653 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to T.NO.2-4 (509895) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_654 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to 46ST-TP-4 (509900) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_655 | 3 Phase fault on T.NO.--4 138.00 (509817) 138 kV Bus a. Apply fault at the T.NO.--4 138.00 (509817) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.--4 (509817) 138.0 kV to N.E.S.-4 (510396) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_656 | 3 Phase fault on 121LYNN4 138.00 (509869) 138 kV Bus a. Apply fault at the 121LYNN4 138.00 (509869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 121LYNN4 (509869) 138.0 kV to E_121ST4 (509889) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_657 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_658 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_659 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_660 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_661 | 3 Phase fault on NBVILLE4 138.00 (510386) 138 kV Bus a. Apply fault at the NBVILLE4 138.00 (510386) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_662 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to ALWUETP4 (510429) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_663 | 3 Phase fault on VINTAJC4 138.00 (510417) 138 kV Bus a. Apply fault at the VINTAJC4 138.00 (510417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_664 | 3 Phase fault on COFFEYT4 138.00 (510422) 138 kV Bus a. Apply fault at the COFFEYT4 138.00 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_665 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_666 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_667 | 3 Phase fault on MAIDTP2 69.000 (512625) 69 kV Bus a. Apply fault at the MAIDTP2 69.000 (512625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIDTP2 (512625) 69.0 kV to GRDA1 2 (512727) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_668 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to FAIRNEO2 (512691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_669 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI1 2 (513020) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_670 | 3 Phase fault on MIAMI 2 69.000 (512630) 69 kV Bus a. Apply fault at the MIAMI 2 69.000 (512630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 2 (512630) 69.0 kV to MIAMI3 2 (513024) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_671 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_672 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_673 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to EXPL TP2 (512672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_674 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to CLEORTP2 (512692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_675 | 3 Phase fault on AFTON 2 69.000 (512633) 69 kV Bus a. Apply fault at the AFTON 2 69.000 (512633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 2 (512633) 69.0 kV to FAIRTAP2 (512708) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_676 | 3 Phase fault on OKAYGR 5 161.00 (512640) 161 kV Bus a. Apply fault at the OKAYGR 5 161.00 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_677 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_678 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_679 | 3 Phase fault on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_680 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to G18-079-TAP (763113) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_681 | 3 Phase fault on IODINE-4 138.00 (514796) 138 kV Bus a. Apply fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_682 | 3 Phase fault on IODINE-4 138.00 (514796) 138 kV Bus a. Apply fault at the IODINE-4 138.00 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_683 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_684 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_685 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_686 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_687 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_688 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_689 | 3 Phase fault on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_690 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_691 | 3 Phase fault on BADGER 7 345.00 (515677) 345 kV Bus a. Apply fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_692 | 3 Phase fault on BOBCAT 7 345.00 (516106) 345 kV Bus a. Apply fault at the BOBCAT 7 345.00 (516106) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BOBCAT 7 (516106) 345.0 kV to 25MILE 7 (516146) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_693 | 3 Phase fault on 25MILE 7 345.00 (516146) 345 kV Bus a. Apply fault at the 25MILE 7 345.00 (516146) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 25MILE 7 (516146) 345.0 kV to 25MILZ 7 (516159) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_694 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to OCHILTREE 6 (523155) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_695 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to MOORE_CNTY 6 (523309) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_696 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOBLE_WND 7 (523101) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_697 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to NOVUS1 7 (523112) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_698 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_699 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_700 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to G10014G11022 (576397) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_701 | 3 Phase fault on NOBLE_WND 3115.00 (523103) 115 kV Bus a. Apply fault at the NOBLE_WND 3115.00 (523103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_702 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_703 | 3 Phase fault on GRPLNS-HV4-3115.00 (523130) 115 kV Bus a. Apply fault at the GRPLNS-HV4-3115.00 (523130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_704 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to CHAN+TASCOS6 (523869) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_705 | 3 Phase fault on PRINGLE 3115.00 (523266) 115 kV Bus a. Apply fault at the PRINGLE 3115.00 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 3 (523266) 115.0 kV to Q_RYTON_TP 3 (523478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_706 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_707 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MCDWL_CREEK6 (523323) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_708 | 3 Phase fault on MCDWL_CREEK3115.00 (523322) 115 kV Bus a. Apply fault at the MCDWL_CREEK3115.00 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to EXELL_TP 3 (523332) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_709 | 3 Phase fault on MCDWL_CREEK3115.00 (523322) 115 kV Bus a. Apply fault at the MCDWL_CREEK3115.00 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK3 (523322) 115.0 kV to FAIN 3 (523339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_710 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_711 | 3 Phase fault on HUTCHISON 6230.00 (523551) 230 kV Bus a. Apply fault at the HUTCHISON 6230.00 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUTCHISON 6 (523551) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_712 | 3 Phase fault on GRAPEVINE 6230.00 (523771) 230 kV Bus a. Apply fault at the GRAPEVINE 6230.00 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPEVINE 6 (523771) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_713 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_714 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_715 | 3 Phase fault on CHAN+TASCOS6230.00 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6230.00 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 (523869) 230.0 kV to POTTER_CO 6 (523959) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_716 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to HARRNG_EST 6 (523979) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_717 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_718 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to BUSHLAND 6 (524267) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_719 | 3 Phase fault on POTTER_CO 6230.00 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6230.00 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 (523959) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_720 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_721 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_722 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_723 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to ROLLHILLS 6 (524010) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_724 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_725 | 3 Phase fault on HARRNG_WST 6230.00 (523977) 230 kV Bus a. Apply fault at the HARRNG_WST 6230.00 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_WST 6 (523977) 230.0 kV to EAST_PLANT 6 (524163) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_726 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to NICHOLS 6 (524044) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_727 | 3 Phase fault on HARRNG_MID 6230.00 (523978) 230 kV Bus a. Apply fault at the HARRNG_MID 6230.00 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARRNG_MID 6 (523978) 230.0 kV to RANDALL 6 (524365) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_728 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_729 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to DEAFSMITH 6 (524623) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_730 | 3 Phase fault on SPNSPUR_WND7345.00 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7345.00 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_731 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to AMA_SOUTH 6 (524415) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_732 | 3 Phase fault on AMA_SOUTH 6230.00 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6230.00 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 (524415) 230.0 kV to SWISHER 6 (525213) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_733 | 3 Phase fault on DEAFSMITH 6230.00 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6230.00 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 (524623) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_734 | 3 Phase fault on CASTRO_CNTY3115.00 (524746) 115 kV Bus a. Apply fault at the CASTRO_CNTY3115.00 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASTRO_CNTY3 (524746) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_735 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_736 | 3 Phase fault on ROOSEVELT 6230.00 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6230.00 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 (524909) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_737 | 3 Phase fault on MULSHVLY_TP3115.00 (525019) 115 kV Bus a. Apply fault at the MULSHVLY_TP3115.00 (525019) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULSHVLY_TP3 (525019) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_738 | 3 Phase fault on BC-EARTH 3115.00 (525056) 115 kV Bus a. Apply fault at the BC-EARTH 3115.00 (525056) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC-EARTH 3 (525056) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_739 | 3 Phase fault on HART_INDUST3115.00 (525124) 115 kV Bus a. Apply fault at the HART_INDUST3115.00 (525124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HART_INDUST3 (525124) 115.0 kV to NEWHART 3 (525460) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_740 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to NEWHART 6 (525461) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_741 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_742 | 3 Phase fault on RKYFORD_TP 3115.00 (525446) 115 kV Bus a. Apply fault at the RKYFORD_TP 3115.00 (525446) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RKYFORD_TP 3 (525446) 115.0 kV to PLANT_X 3 (525480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_743 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to PLANT_X 6 (525481) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_744 | 3 Phase fault on PLANT_X 3115.00 (525480) 115 kV Bus a. Apply fault at the PLANT_X 3115.00 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 3 (525480) 115.0 kV to LAMB_CNTY 3 (525636) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_745 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_746 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to TOLK 6 (525531) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_747 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to SUNDOWN 6 (526435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_748 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to G17-146-TAP (760498) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_749 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to NEEDMORE 6 (525586) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_750 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to LAMB_CNTY 6 (525637) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_751 | 3 Phase fault on TOLK 6230.00 (525531) 230 kV Bus a. Apply fault at the TOLK 6230.00 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 (525531) 230.0 kV to TUCO_INT 6 (525830) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_752 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to AMOCO_SS 6 (526460) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_753 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to WOLFFORTH 6 (526525) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_754 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SMKYP1 6 (530593) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_755 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_756 | 3 Phase fault on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_757 | 3 Phase fault on MANNGT 3 115.00 (531362) 115 kV Bus a. Apply fault at the MANNGT 3 115.00 (531362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_758 | 3 Phase fault on HASKELL3 115.00 (531374) 115 kV Bus a. Apply fault at the HASKELL3 115.00 (531374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASKELL3 (531374) 115.0 kV to SEWARD-3 (531467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_759 | 3 Phase fault on JONES3 115.00 (531379) 115 kV Bus a. Apply fault at the JONES3 115.00 (531379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_760 | 3 Phase fault on HUGOTON2 69.000 (531380) 69 kV Bus a. Apply fault at the HUGOTON2 69.000 (531380) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to CHUGTON2 (531479) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_761 | 3 Phase fault on MOSCOW 2 69.000 (531384) 69 kV Bus a. Apply fault at the MOSCOW 2 69.000 (531384) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOW 2 (531384) 69.0 kV to MOSCOWT2 (531385) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_762 | 3 Phase fault on MOSCOWT2 69.000 (531385) 69 kV Bus a. Apply fault at the MOSCOWT2 69.000 (531385) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOSCOWT2 (531385) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_763 | 3 Phase fault on NORTH6 2 69.000 (531388) 69 kV Bus a. Apply fault at the NORTH6 2 69.000 (531388) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6 2 (531388) 69.0 kV to NORTH6T2 (531389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_764 | 3 Phase fault on NORTH6T2 69.000 (531389) 69 kV Bus a. Apply fault at the NORTH6T2 69.000 (531389) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH6T2 (531389) 69.0 kV to WALKMYR2 (531404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_765 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_766 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER3 (531391) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_767 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_768 | 3 Phase fault on ROLLA 2 115.00 (531395) 115 kV Bus a. Apply fault at the ROLLA 2 115.00 (531395) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLA 2 (531395) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_769 | 3 Phase fault on WALKMYR2 69.000 (531404) 69 kV Bus a. Apply fault at the WALKMYR2 69.000 (531404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WOODS 2 (531406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_770 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to SELKIRK3 (531434) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_771 | 3 Phase fault on LEOTI 3 115.00 (531428) 115 kV Bus a. Apply fault at the LEOTI 3 115.00 (531428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEOTI 3 (531428) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_772 | 3 Phase fault on PILE 3 115.00 (531432) 115 kV Bus a. Apply fault at the PILE 3 115.00 (531432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_773 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_774 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD-3 (531467) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_775 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_776 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to G19-030-TAP (763677) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_777 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to GRANTTP3 (531483) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_778 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON3 (531481) 115.0 kV to ABBK 2 (531494) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_779 | 3 Phase fault on GRANTTP3 115.00 (531483) 115 kV Bus a. Apply fault at the GRANTTP3 115.00 (531483) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTTP3 (531483) 115.0 kV to GRANT 3 (531484) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_780 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_781 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to READWF 7 (532776) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_782 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_783 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_784 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_785 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_786 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_787 | 3 Phase fault on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 (532792) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_788 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_789 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_790 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_791 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_792 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_793 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_794 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to G20-090-TAP (765200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_795 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_796 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_797 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_798 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_799 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_800 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_801 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to G20-071-TAP (765140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_802 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to G20-071-TAP (765140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_803 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_804 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_805 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_806 | 3 Phase fault on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_807 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_808 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_809 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_810 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_811 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_812 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_813 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_814 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_815 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_816 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to TCBURNS4 (532994) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_817 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_818 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_819 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_820 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_821 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_822 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_823 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_824 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_825 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_826 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_827 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_828 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_829 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_830 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_831 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_832 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_833 | 3 Phase fault on EVANS S4 138.00 (533041) 138 kV Bus a. Apply fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_834 | 3 Phase fault on EVANS S4 138.00 (533041) 138 kV Bus a. Apply fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_835 | 3 Phase fault on FARBER 4 138.00 (533042) 138 kV Bus a. Apply fault at the FARBER 4 138.00 (533042) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_836 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_837 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_838 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_839 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_840 | 3 Phase fault on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_841 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_842 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_843 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_844 | 3 Phase fault on TECHILE3 115.00 (533182) 115 kV Bus a. Apply fault at the TECHILE3 115.00 (533182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_845 | 3 Phase fault on TECHILE3 115.00 (533182) 115 kV Bus a. Apply fault at the TECHILE3 115.00 (533182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_846 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_847 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_848 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_849 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_850 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_851 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_852 | 3 Phase fault on FAIRGDS3 115.00 (533236) 115 kV Bus a. Apply fault at the FAIRGDS3 115.00 (533236) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_853 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_854 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_855 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_856 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_857 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_858 | 3 Phase fault on MOCKBRD3 115.00 (533253) 115 kV Bus a. Apply fault at the MOCKBRD3 115.00 (533253) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_859 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_860 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_861 | 3 Phase fault on PENTAGN3 115.00 (533261) 115 kV Bus a. Apply fault at the PENTAGN3 115.00 (533261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_862 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_863 | 3 Phase fault on STULL 3 115.00 (533269) 115 kV Bus a. Apply fault at the STULL 3 115.00 (533269) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_864 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_865 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_866 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_867 | 3 Phase fault on LANG 3 115.00 (533304) 115 kV Bus a. Apply fault at the LANG 3 115.00 (533304) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_868 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_869 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_870 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_871 | 3 Phase fault on WMBROS 3 115.00 (533310) 115 kV Bus a. Apply fault at the WMBROS 3 115.00 (533310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_872 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_873 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_874 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_875 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_876 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_877 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_878 | 3 Phase fault on ARKCTYE2 69.000 (533542) 69 kV Bus a. Apply fault at the ARKCTYE2 69.000 (533542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_879 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_880 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_881 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_882 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_883 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_884 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_885 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_886 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_887 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_888 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_889 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_890 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_891 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_892 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_893 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_894 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_895 | 3 Phase fault on PRAIRIE2 69.000 (533562) 69 kV Bus a. Apply fault at the PRAIRIE2 69.000 (533562) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRAIRIE2 (533562) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_896 | 3 Phase fault on WEAVER 2 69.000 (533604) 69 kV Bus a. Apply fault at the WEAVER 2 69.000 (533604) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_897 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLIND2 (533625) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_898 | 3 Phase fault on BURLING2 69.000 (533624) 69 kV Bus a. Apply fault at the BURLING2 69.000 (533624) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLING2 (533624) 69.0 kV to BURLJCT2 (533626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_899 | 3 Phase fault on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_900 | 3 Phase fault on BURLJCT2 69.000 (533626) 69 kV Bus a. Apply fault at the BURLJCT2 69.000 (533626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_901 | 3 Phase fault on CC3WEST2 69.000 (533630) 69 kV Bus a. Apply fault at the CC3WEST2 69.000 (533630) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_902 | 3 Phase fault on MARMATN2 69.000 (533639) 69 kV Bus a. Apply fault at the MARMATN2 69.000 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_903 | 3 Phase fault on MARMATN2 69.000 (533639) 69 kV Bus a. Apply fault at the MARMATN2 69.000 (533639) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_904 | 3 Phase fault on MCKEE 2 69.000 (533640) 69 kV Bus a. Apply fault at the MCKEE 2 69.000 (533640) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_905 | 3 Phase fault on UN1ELSM2 69.000 (533647) 69 kV Bus a. Apply fault at the UN1ELSM2 69.000 (533647) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_906 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_907 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_908 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_909 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_910 | 3 Phase fault on LABETTS2 69.000 (533696) 69 kV Bus a. Apply fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_911 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_912 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_913 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_914 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_915 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_916 | 3 Phase fault on GIR JCT2 69.000 (533762) 69 kV Bus a. Apply fault at the GIR JCT2 69.000 (533762) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_917 | 3 Phase fault on GIR JCT2 69.000 (533762) 69 kV Bus a. Apply fault at the GIR JCT2 69.000 (533762) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_918 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_919 | 3 Phase fault on SHEFFLD2 69.000 (533774) 69 kV Bus a. Apply fault at the SHEFFLD2 69.000 (533774) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_920 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_921 | 3 Phase fault on ROSEHIL2 69.000 (533836) 69 kV Bus a. Apply fault at the ROSEHIL2 69.000 (533836) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL2 (533836) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_922 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_923 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_924 | 3 Phase fault on ELLSWTP3 115.00 (539642) 115 kV Bus a. Apply fault at the ELLSWTP3 115.00 (539642) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLSWTP3 (539642) 115.0 kV to ROLLHLS3 (539643) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_925 | 3 Phase fault on ROLLHLS3 115.00 (539643) 115 kV Bus a. Apply fault at the ROLLHLS3 115.00 (539643) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHLS3 (539643) 115.0 kV to EHALLTP3 (539660) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_926 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_927 | 3 Phase fault on COVERT 3 115.00 (539644) 115 kV Bus a. Apply fault at the COVERT 3 115.00 (539644) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_928 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CMRIVTP3 (539652) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_929 | 3 Phase fault on KISMET 3 115.00 (539646) 115 kV Bus a. Apply fault at the KISMET 3 115.00 (539646) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KISMET 3 (539646) 115.0 kV to CUDAHY 3 (539659) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_930 | 3 Phase fault on IONIA 3 115.00 (539647) 115 kV Bus a. Apply fault at the IONIA 3 115.00 (539647) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_931 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_932 | 3 Phase fault on CMRIVTP3 115.00 (539652) 115 kV Bus a. Apply fault at the CMRIVTP3 115.00 (539652) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMRIVTP3 (539652) 115.0 kV to E-LIBER3 (539672) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_933 | 3 Phase fault on CIM-PLT3 115.00 (539654) 115 kV Bus a. Apply fault at the CIM-PLT3 115.00 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIM-PLT3 (539654) 115.0 kV to N-CIMRN3 (539749) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_934 | 3 Phase fault on EHALLTP3 115.00 (539660) 115 kV Bus a. Apply fault at the EHALLTP3 115.00 (539660) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EHALLTP3 (539660) 115.0 kV to ELLSWTH3 (539662) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_935 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_936 | 3 Phase fault on 24-FREY3 115.00 (539661) 115 kV Bus a. Apply fault at the 24-FREY3 115.00 (539661) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_937 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_938 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_939 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_940 | 3 Phase fault on GBENDTP3 115.00 (539666) 115 kV Bus a. Apply fault at the GBENDTP3 115.00 (539666) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_941 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to E-PINE 3 (539690) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_942 | 3 Phase fault on E-LIBER3 115.00 (539672) 115 kV Bus a. Apply fault at the E-LIBER3 115.00 (539672) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E-LIBER3 (539672) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_943 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_944 | 3 Phase fault on GRTBEND3 115.00 (539678) 115 kV Bus a. Apply fault at the GRTBEND3 115.00 (539678) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_945 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_946 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_947 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_948 | 3 Phase fault on WALDO 3 115.00 (539698) 115 kV Bus a. Apply fault at the WALDO 3 115.00 (539698) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_949 | 3 Phase fault on W-LIBER3 115.00 (539700) 115 kV Bus a. Apply fault at the W-LIBER3 115.00 (539700) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W-LIBER3 (539700) 115.0 kV to NLIB 3 (539737) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_950 | 3 Phase fault on NLIB 3 115.00 (539737) 115 kV Bus a. Apply fault at the NLIB 3 115.00 (539737) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NLIB 3 (539737) 115.0 kV to NATBEEF3 (539751) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_951 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-19-063 (763926). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_952 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-19-063 (763926). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_953 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_954 | 3 Phase fault on CLNTPLT_CAP269.000 (541138) 69 kV Bus a. Apply fault at the CLNTPLT_CAP269.000 (541138) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT_CAP2 (541138) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_955 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_956 | 3 Phase fault on WBURGE_CAP5 161.00 (541148) 161 kV Bus a. Apply fault at the WBURGE_CAP5 161.00 (541148) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE_CAP5 (541148) 161.0 kV to WBURGE 5 (541228) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_957 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_958 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_959 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_960 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_961 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_962 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_963 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_964 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_965 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_966 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_967 | 3 Phase fault on PRALEE 5 161.00 (541206) 161 kV Bus a. Apply fault at the PRALEE 5 161.00 (541206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_968 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_969 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_970 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_971 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_972 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_973 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_974 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_975 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDSR 5 (541217) 161.0 kV to G20-072-TAP (764355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_976 | 3 Phase fault on GRNWD 5 161.00 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 161.00 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_977 | 3 Phase fault on GRNWD 5 161.00 (541218) 161 kV Bus a. Apply fault at the GRNWD 5 161.00 (541218) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_978 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_979 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_980 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_981 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_982 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_983 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_984 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_985 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to ODESSA 5 (541229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_986 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 5 (541228) 161.0 kV to WAFBW_SW5 (541335) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_987 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_988 | 3 Phase fault on SEDEAST5 161.00 (541241) 161 kV Bus a. Apply fault at the SEDEAST5 161.00 (541241) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDEAST5 (541241) 161.0 kV to NUCOR5 (541395) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_989 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_990 | 3 Phase fault on ORRICK 5 161.00 (541244) 161 kV Bus a. Apply fault at the ORRICK 5 161.00 (541244) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_991 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_992 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_993 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_994 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to LAMONTETP (541535) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_995 | 3 Phase fault on SEDN 2 69.000 (541271) 69 kV Bus a. Apply fault at the SEDN 2 69.000 (541271) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to G18-063-TAP (762992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_996 | 3 Phase fault on SEDS 2 69.000 (541272) 69 kV Bus a. Apply fault at the SEDS 2 69.000 (541272) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to PITTCRN2 (541274) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_997 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_998 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_999 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1000 | 3 Phase fault on PHILL 2 69.000 (541280) 69 kV Bus a. Apply fault at the PHILL 2 69.000 (541280) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1001 | 3 Phase fault on BELTON 2 69.000 (541289) 69 kV Bus a. Apply fault at the BELTON 2 69.000 (541289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1002 | 3 Phase fault on BELTON 2 69.000 (541289) 69 kV Bus a. Apply fault at the BELTON 2 69.000 (541289) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1003 | 3 Phase fault on BELTONS2 69.000 (541290) 69 kV Bus a. Apply fault at the BELTONS2 69.000 (541290) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1004 | 3 Phase fault on HSNVLS 2 69.000 (541294) 69 kV Bus a. Apply fault at the HSNVLS 2 69.000 (541294) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1005 | 3 Phase fault on HSNVL 2 69.000 (541295) 69 kV Bus a. Apply fault at the HSNVL 2 69.000 (541295) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVLSW2 (541296) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1006 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to HSNVLN 2 (541297) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1007 | 3 Phase fault on HSNVLSW2 69.000 (541296) 69 kV Bus a. Apply fault at the HSNVLSW2 69.000 (541296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVLSW2 (541296) 69.0 kV to GRDNCTY2 (541298) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1008 | 3 Phase fault on GRDNCTY2 69.000 (541298) 69 kV Bus a. Apply fault at the GRDNCTY2 69.000 (541298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY2 (541298) 69.0 kV to GUNNPS2 (541299) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1009 | 3 Phase fault on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1010 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1011 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to URICHTP2 (541304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1012 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1013 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1014 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBW5 (541336) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1015 | 3 Phase fault on WAFBW_SW5 161.00 (541335) 161 kV Bus a. Apply fault at the WAFBW_SW5 161.00 (541335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBW_SW5 (541335) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1016 | 3 Phase fault on WAFBE_SW5 161.00 (541337) 161 kV Bus a. Apply fault at the WAFBE_SW5 161.00 (541337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAFBE_SW5 (541337) 161.0 kV to WAFBE5 (541338) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1017 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1018 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1019 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1020 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1021 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1022 | 3 Phase fault on HLDENTP2 69.000 (541386) 69 kV Bus a. Apply fault at the HLDENTP2 69.000 (541386) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLDENTP2 (541386) 69.0 kV to KNGSVIL 2 (541387) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1023 | 3 Phase fault on KNGSVIL 2 69.000 (541387) 69 kV Bus a. Apply fault at the KNGSVIL 2 69.000 (541387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNGSVIL 2 (541387) 69.0 kV to KNGSVRL2 (541388) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1024 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1025 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1026 | 3 Phase fault on ATLNTIC7 345.00 (542940) 345 kV Bus a. Apply fault at the ATLNTIC7 345.00 (542940) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1027 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1028 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1029 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1030 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1031 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1032 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1033 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BULLCRK5 (543105) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1034 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1035 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1036 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1037 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1038 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1039 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1040 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1041 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1042 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1043 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1044 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1045 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1046 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1047 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1048 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1049 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1050 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1051 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1052 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1053 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1054 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1055 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1056 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1057 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1058 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1059 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1060 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1061 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1062 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1063 | 3 Phase fault on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1064 | 3 Phase fault on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1065 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1066 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1067 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1068 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1069 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1070 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1071 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1072 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1073 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1074 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1075 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1076 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1077 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1078 | 3 Phase fault on BRKRIDG5 161.00 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 161.00 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1079 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1080 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1081 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1082 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1083 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1084 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1085 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1086 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1087 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to GARDNER5 (543056) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1088 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1089 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1090 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1091 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1092 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1093 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1094 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1095 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to SWAVRLY5 (543063) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1096 | 3 Phase fault on MALTABN5 161.00 (543059) 161 kV Bus a. Apply fault at the MALTABN5 161.00 (543059) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALTABN5 (543059) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1097 | 3 Phase fault on CAROLTN5 161.00 (543060) 161 kV Bus a. Apply fault at the CAROLTN5 161.00 (543060) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAROLTN5 (543060) 161.0 kV to BRUNSWK5 (543061) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1098 | 3 Phase fault on BRUNSWK5 161.00 (543061) 161 kV Bus a. Apply fault at the BRUNSWK5 161.00 (543061) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRUNSWK5 (543061) 161.0 kV to SALSBRY5 (543062) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1099 | 3 Phase fault on SALSBRY5 161.00 (543062) 161 kV Bus a. Apply fault at the SALSBRY5 161.00 (543062) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALSBRY5 (543062) 161.0 kV to NORTON 5 (543064) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1100 | 3 Phase fault on NORTON 5 161.00 (543064) 161 kV Bus a. Apply fault at the NORTON 5 161.00 (543064) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 5 (543064) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1101 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1102 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1103 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1104 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1105 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1106 | 3 Phase fault on PAOLA 5 161.00 (543069) 161 kV Bus a. Apply fault at the PAOLA 5 161.00 (543069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLA 5 (543069) 161.0 kV to OSAWAT 5 (543112) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1107 | 3 Phase fault on S EAST 5 161.00 (543071) 161 kV Bus a. Apply fault at the S EAST 5 161.00 (543071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S EAST 5 (543071) 161.0 kV to MRSHLJT5 (543072) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1108 | 3 Phase fault on MRSHLJT5 161.00 (543072) 161 kV Bus a. Apply fault at the MRSHLJT5 161.00 (543072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRSHLJT5 (543072) 161.0 kV to MIAMI_ 5 (543073) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1109 | 3 Phase fault on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSTVAL5 (543077) 161.0 kV to G20-073-TAP (764400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1110 | 3 Phase fault on SWAVRLY2 69.000 (543094) 69 kV Bus a. Apply fault at the SWAVRLY2 69.000 (543094) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1111 | 3 Phase fault on MAYVWTP2 69.000 (543096) 69 kV Bus a. Apply fault at the MAYVWTP2 69.000 (543096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYVWTP2 (543096) 69.0 kV to AMOCOPL2 (543100) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1112 | 3 Phase fault on CORDER 2 69.000 (543097) 69 kV Bus a. Apply fault at the CORDER 2 69.000 (543097) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDER 2 (543097) 69.0 kV to CORDERTP2 (543657) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1113 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HIGNSVL2 (543099) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1114 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HGNSCTYW2 (543144) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1115 | 3 Phase fault on CTY HIG2 69.000 (543098) 69 kV Bus a. Apply fault at the CTY HIG2 69.000 (543098) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTY HIG2 (543098) 69.0 kV to HGNSCTYPLNT2 (543146) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1117 | 3 Phase fault on HIGNSVL2 69.000 (543099) 69 kV Bus a. Apply fault at the HIGNSVL2 69.000 (543099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGNSVL2 (543099) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1118 | 3 Phase fault on AMOCOPL2 69.000 (543100) 69 kV Bus a. Apply fault at the AMOCOPL2 69.000 (543100) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCOPL2 (543100) 69.0 kV to WHGNSVL2 (543102) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1119 | 3 Phase fault on DOVER2 69.000 (543101) 69 kV Bus a. Apply fault at the DOVER2 69.000 (543101) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER2 (543101) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1120 | 3 Phase fault on OSAWAT 5 161.00 (543112) 161 kV Bus a. Apply fault at the OSAWAT 5 161.00 (543112) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OSAWAT 5 (543112) 161.0 kV to OSAWTM_CAP5 (543135) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1121 | 3 Phase fault on DAKOTA_5 161.00 (543650) 161 kV Bus a. Apply fault at the DAKOTA_5 161.00 (543650) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAKOTA_5 (543650) 161.0 kV to PRQN_WIND5 (543651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1122 | 3 Phase fault on CORDERTP2 69.000 (543657) 69 kV Bus a. Apply fault at the CORDERTP2 69.000 (543657) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORDERTP2 (543657) 69.0 kV to DOVER_TAP2 (543658) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1123 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON416J2 (547402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1124 | 3 Phase fault on MON376J2 69.000 (547400) 69 kV Bus a. Apply fault at the MON376J2 69.000 (547400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376J2 (547400) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1125 | 3 Phase fault on MON376 2 69.000 (547401) 69 kV Bus a. Apply fault at the MON376 2 69.000 (547401) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON376 2 (547401) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1126 | 3 Phase fault on MON416J2 69.000 (547402) 69 kV Bus a. Apply fault at the MON416J2 69.000 (547402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON416J2 (547402) 69.0 kV to MON416 2 (547403) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1127 | 3 Phase fault on MON416J2 69.000 (547402) 69 kV Bus a. Apply fault at the MON416J2 69.000 (547402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON416J2 (547402) 69.0 kV to PUR390 2 (547404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1128 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON352 2 (547406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1129 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON311J2 (547407) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1130 | 3 Phase fault on MON352J2 69.000 (547405) 69 kV Bus a. Apply fault at the MON352J2 69.000 (547405) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON352J2 (547405) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1131 | 3 Phase fault on MON311J2 69.000 (547407) 69 kV Bus a. Apply fault at the MON311J2 69.000 (547407) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON311J2 (547407) 69.0 kV to MON311 2 (547408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1132 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1133 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1134 | 3 Phase fault on SEN375 2 69.000 (547426) 69 kV Bus a. Apply fault at the SEN375 2 69.000 (547426) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEN375 2 (547426) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1135 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1136 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to EXP4492 (547439) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1137 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1138 | 3 Phase fault on EXP449T2 69.000 (547438) 69 kV Bus a. Apply fault at the EXP449T2 69.000 (547438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXP449T2 (547438) 69.0 kV to JOP389 2 (547592) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1139 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to WEN205 2 (547544) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1140 | 3 Phase fault on PRC460 2 69.000 (547449) 69 kV Bus a. Apply fault at the PRC460 2 69.000 (547449) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRC460 2 (547449) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1141 | 3 Phase fault on JAS344T2 69.000 (547450) 69 kV Bus a. Apply fault at the JAS344T2 69.000 (547450) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAS344T2 (547450) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1142 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1143 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1144 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1145 | 3 Phase fault on SVRCK469 5 161.00 (547462) 161 kV Bus a. Apply fault at the SVRCK469 5 161.00 (547462) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1146 | 3 Phase fault on KOD471 2 69.000 (547463) 69 kV Bus a. Apply fault at the KOD471 2 69.000 (547463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KOD471 2 (547463) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1147 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1148 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1149 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1150 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1151 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1152 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1153 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1154 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1155 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1156 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1157 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1158 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to G20-079-TAP (764310) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1159 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1160 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1161 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1162 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1163 | 3 Phase fault on TIP292 5 161.00 (547472) 161 kV Bus a. Apply fault at the TIP292 5 161.00 (547472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 5 (547472) 161.0 kV to RNM393 5 (547500) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1164 | 3 Phase fault on RDS295 5 161.00 (547473) 161 kV Bus a. Apply fault at the RDS295 5 161.00 (547473) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDS295 5 (547473) 161.0 kV to G19-035-TAP (763696) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1165 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-181 (760245 and 760248). This trip does not occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1166 | 3 Phase fault on ASB349 5 161.00 (547476) 161 kV Bus a. Apply fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-181 (760245 and 760248). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1167 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1168 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to BOL431 5 (547493) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1169 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to CPK446 5 (547499) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1170 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1171 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1172 | 3 Phase fault on DEC392 5 161.00 (547484) 161 kV Bus a. Apply fault at the DEC392 5 161.00 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 (547484) 161.0 kV to NOL435 5 (547496) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1173 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1174 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1175 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to JOP391 5 (547593) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1176 | 3 Phase fault on RIV453 5 161.00 (547501) 161 kV Bus a. Apply fault at the RIV453 5 161.00 (547501) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1177 | 3 Phase fault on RIV167 5 161.00 (547502) 161 kV Bus a. Apply fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1178 | 3 Phase fault on NEO 56 2 69.000 (547524) 69 kV Bus a. Apply fault at the NEO 56 2 69.000 (547524) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO 56 2 (547524) 69.0 kV to RAC375 2 (547589) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1179 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1180 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1181 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1182 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1183 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP145 2 (547539) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1184 | 3 Phase fault on JOP 64 2 69.000 (547526) 69 kV Bus a. Apply fault at the JOP 64 2 69.000 (547526) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 64 2 (547526) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1185 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1186 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1187 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1188 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1189 | 3 Phase fault on JOP100 2 69.000 (547531) 69 kV Bus a. Apply fault at the JOP100 2 69.000 (547531) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP100 2 (547531) 69.0 kV to JOP284 2 (547557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1190 | 3 Phase fault on CAR108 2 69.000 (547532) 69 kV Bus a. Apply fault at the CAR108 2 69.000 (547532) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAR108 2 (547532) 69.0 kV to ATL109 2 (547533) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1191 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1192 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to JOP360 2 (547581) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1193 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1194 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1195 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1196 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MON152 2 (547540) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1197 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to AUR355 2 (547578) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1198 | 3 Phase fault on AUR124 2 69.000 (547537) 69 kV Bus a. Apply fault at the AUR124 2 69.000 (547537) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 2 (547537) 69.0 kV to MAR437 2 (547611) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1199 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1200 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1201 | 3 Phase fault on MON152 2 69.000 (547540) 69 kV Bus a. Apply fault at the MON152 2 69.000 (547540) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON152 2 (547540) 69.0 kV to MON383 2 (547591) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1202 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1203 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1204 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to ROC296 2 (547560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1205 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to LIN314 2 (547563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1206 | 3 Phase fault on NEO184 2 69.000 (547543) 69 kV Bus a. Apply fault at the NEO184 2 69.000 (547543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 2 (547543) 69.0 kV to AND322 2 (547566) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1207 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1208 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1209 | 3 Phase fault on GAL278 2 69.000 (547555) 69 kV Bus a. Apply fault at the GAL278 2 69.000 (547555) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAL278 2 (547555) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1210 | 3 Phase fault on TIP292 2 69.000 (547559) 69 kV Bus a. Apply fault at the TIP292 2 69.000 (547559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIP292 2 (547559) 69.0 kV to RNM393 2 (547595) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1211 | 3 Phase fault on JOP360 2 69.000 (547581) 69 kV Bus a. Apply fault at the JOP360 2 69.000 (547581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP360 2 (547581) 69.0 kV to JOP372 2 (547588) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1212 | 3 Phase fault on QUA377 2 69.000 (547590) 69 kV Bus a. Apply fault at the QUA377 2 69.000 (547590) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1213 | 3 Phase fault on JOP389 2 69.000 (547592) 69 kV Bus a. Apply fault at the JOP389 2 69.000 (547592) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 2 (547592) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1214 | 3 Phase fault on JOP391 5 161.00 (547593) 161 kV Bus a. Apply fault at the JOP391 5 161.00 (547593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP391 5 (547593) 161.0 kV to JOP422 5 (547607) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1215 | 3 Phase fault on RNM393 2 69.000 (547595) 69 kV Bus a. Apply fault at the RNM393 2 69.000 (547595) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 2 (547595) 69.0 kV to PLB447 2 (547685) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1216 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1217 | 3 Phase fault on COX 269.000 (549910) 69 kV Bus a. Apply fault at the COX 269.000 (549910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COX 2 (549910) 69.0 kV to GOLDEN 2 (549911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1218 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to LAUREL 2 (549924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1219 | 3 Phase fault on GOLDEN 269.000 (549911) 69 kV Bus a. Apply fault at the GOLDEN 269.000 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDEN 2 (549911) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1220 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to FORT 2 (549914) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1221 | 3 Phase fault on DAYTON 269.000 (549913) 69 kV Bus a. Apply fault at the DAYTON 269.000 (549913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 2 (549913) 69.0 kV to BATTLEFIELD2 (549979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1222 | 3 Phase fault on CHAD 269.000 (549919) 69 kV Bus a. Apply fault at the CHAD 269.000 (549919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAD 2 (549919) 69.0 kV to HARGISS 2 (549920) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1223 | 3 Phase fault on HARGISS 269.000 (549920) 69 kV Bus a. Apply fault at the HARGISS 269.000 (549920) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARGISS 2 (549920) 69.0 kV to MAIN STREET2 (549921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1224 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to GRAND 2 (549922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1225 | 3 Phase fault on MAIN STREET269.000 (549921) 69 kV Bus a. Apply fault at the MAIN STREET269.000 (549921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET2 (549921) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1226 | 3 Phase fault on GRAND 269.000 (549922) 69 kV Bus a. Apply fault at the GRAND 269.000 (549922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 2 (549922) 69.0 kV to MONROE 2 (549923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1227 | 3 Phase fault on NORTON 269.000 (549928) 69 kV Bus a. Apply fault at the NORTON 269.000 (549928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTON 2 (549928) 69.0 kV to WASHINGTON 2 (549929) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1228 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1229 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to JAMES RIVER5 (549961) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1230 | 3 Phase fault on JTEC 5161.00 (549954) 161 kV Bus a. Apply fault at the JTEC 5161.00 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JTEC 5 (549954) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1231 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to NICHOLS 5 (549956) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1232 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to BROOKLINE 5 (549969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1233 | 3 Phase fault on JUNCTION 5161.00 (549955) 161 kV Bus a. Apply fault at the JUNCTION 5161.00 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JUNCTION 5 (549955) 161.0 kV to PIC WEST 5 (549971) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1234 | 3 Phase fault on NICHOLS 5161.00 (549956) 161 kV Bus a. Apply fault at the NICHOLS 5161.00 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 5 (549956) 161.0 kV to WEST BELT 5 (549957) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1235 | 3 Phase fault on WEST BELT 5161.00 (549957) 161 kV Bus a. Apply fault at the WEST BELT 5161.00 (549957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST BELT 5 (549957) 161.0 kV to MAIN STREET5 (549958) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1236 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to BATTLEFIELD5 (549959) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1237 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to SW DISP PLT5 (549960) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1238 | 3 Phase fault on JAMES RIVER5161.00 (549961) 161 kV Bus a. Apply fault at the JAMES RIVER5161.00 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMES RIVER5 (549961) 161.0 kV to MENTOR 5 (549963) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1239 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MC CARTNEY 5 (549968) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1240 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1241 | 3 Phase fault on MENTOR 5161.00 (549963) 161 kV Bus a. Apply fault at the MENTOR 5161.00 (549963) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 5 (549963) 161.0 kV to CLAY 5 (549970) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1242 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1243 | 3 Phase fault on LAMAR 6 345.00 (599951) 345 kV Bus a. Apply fault at the LAMAR 6 345.00 (599951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR 6 (599951) 345.0 kV to PNM-DC7 (599956) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1244 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5HUBEN (300088) 161.0 kV to 7HUBEN (300042) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1245 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1246 | 3 Phase fault on 5CLARK 161.00 (300070) 161 kV Bus a. Apply fault at the 5CLARK 161.00 (300070) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLARK (300802) 69.0 kV to 5CLARK (300070) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1247 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1248 | 3 Phase fault on 5COFFMN 161.00 (300072) 161 kV Bus a. Apply fault at the 5COFFMN 161.00 (300072) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2COFFMN (301048) 69.0 kV to 5COFFMN (300072) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1249 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEORGE (300531) 69.0 kV to 5GEORGE (300082) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1250 | 3 Phase fault on 5JAMESV 161.00 (300089) 161 kV Bus a. Apply fault at the 5JAMESV 161.00 (300089) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JAMESV (300673) 69.0 kV to 5JAMESV (300089) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1251 | 3 Phase fault on 5LATHRP 161.00 (300091) 161 kV Bus a. Apply fault at the 5LATHRP 161.00 (300091) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LATHRP (300302) 69.0 kV to 5LATHRP (300091) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1252 | 3 Phase fault on 5MORGAN 161.00 (300101) 161 kV Bus a. Apply fault at the 5MORGAN 161.00 (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MORGAN (300782) 69.0 kV to 5MORGAN (300101) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1253 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MRSHFL (301163) 69.0 kV to 5MRSHFL (300102) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1254 | 3 Phase fault on 5MRSHFL 161.00 (300102) 161 kV Bus a. Apply fault at the 5MRSHFL 161.00 (300102) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MRSHFL (301163) 69.0 kV to 5MRSHFL (300102) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1255 | 3 Phase fault on 5NORTON 161.00 (300105) 161 kV Bus a. Apply fault at the 5NORTON 161.00 (300105) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NORTON (300540) 69.0 kV to 5NORTON (300105) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1256 | 3 Phase fault on 5PHLIPS 161.00 (300109) 161 kV Bus a. Apply fault at the 5PHLIPS 161.00 (300109) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PBURG (301071) 69.0 kV to 5PHLIPS (300109) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1257 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1258 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1259 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1260 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOCITY (300304) 69.0 kV to 5MOCITYB1 (301563) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1261 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LAMR (300651) 69.0 kV to 5LAMAR (300794) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1262 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SHARSNV (300709) 69.0 kV to 5SHARSNV (301515) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1263 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1264 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2NEOSAC (300748) 69.0 kV to NEO184 5 (547471) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1265 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WASHBRN (300763) 69.0 kV to WASHBURN5 (505485) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1266 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1267 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1268 | 3 Phase fault on 5MAURER 1 161.00 (344557) 161 kV Bus a. Apply fault at the 5MAURER 1 161.00 (344557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MAURER (346048) 69.0 kV to 5MAURER 1 (344557) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1269 | 3 Phase fault on 5MOBERLY 161.00 (345221) 161 kV Bus a. Apply fault at the 5MOBERLY 161.00 (345221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOBERLY (345222) 69.0 kV to 5MOBERLY (345221) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1270 | 3 Phase fault on TABLE R5 161.00 (505472) 161 kV Bus a. Apply fault at the TABLE R5 161.00 (505472) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TABLE R5 (505472) 161.0 kV to TABLE R2 (505474) 69.0 kV to TBR X2 1 (505475) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1271 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1272 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD2 (505494) 69.0 kV to SPRGFLD5 (505492) 161.0 kV to SPF X1 1 (505491) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1273 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X1 1 (505497) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1274 | 3 Phase fault on NIXA 5 161.00 (505496) 161 kV Bus a. Apply fault at the NIXA 5 161.00 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NIXA 2 (505501) 69.0 kV to NIXA 5 (505496) 161.0 kV to NXA X2 1 (505499) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1275 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1276 | 3 Phase fault on AFTON 5 161.00 (512632) 161 kV Bus a. Apply fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1277 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1278 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1279 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1280 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1281 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1282 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WODWRD 2 (514782) 69.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1283 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1284 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1285 | 3 Phase fault on HITCHLAND 6230.00 (523095) 230 kV Bus a. Apply fault at the HITCHLAND 6230.00 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 3 (523093) 115.0 kV to HITCHLD_TR11 (523092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1286 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1287 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1288 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1289 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1290 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1291 | 3 Phase fault on XIT_INTG 6230.00 (523221) 230 kV Bus a. Apply fault at the XIT_INTG 6230.00 (523221) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XIT_INTG 6 (523221) 230.0 kV to XIT_INTG 3 (523220) 115.0 kV to XIT_INTG TR1 (523219) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1292 | 3 Phase fault on PRINGLE 6230.00 (523267) 230 kV Bus a. Apply fault at the PRINGLE 6230.00 (523267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRINGLE 6 (523267) 230.0 kV to PRINGLE 3 (523266) 115.0 kV to PRINGLE_TR 1 (523265) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1293 | 3 Phase fault on MOORE_CNTY 6230.00 (523309) 230 kV Bus a. Apply fault at the MOORE_CNTY 6230.00 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE_CNTY 6 (523309) 230.0 kV to MOORE_E 3 (523308) 115.0 kV to MOORE_TR1 1 (523302) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1294 | 3 Phase fault on MCDWL_CREEK6230.00 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6230.00 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 (523323) 230.0 kV to MCDWL_CREEK3 (523322) 115.0 kV to MCDWL_CRKTR1 (523321) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1295 | 3 Phase fault on POTTER_CO 7345.00 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7345.00 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV to POTTER_TR 1 (523957) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1296 | 3 Phase fault on ROLLHILLS 6230.00 (524010) 230 kV Bus a. Apply fault at the ROLLHILLS 6230.00 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROLLHILLS 6 (524010) 230.0 kV to ROLLHILLS 3 (524007) 115.0 kV to ROLHILLS_TR1 (524008) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1297 | 3 Phase fault on NICHOLS 6230.00 (524044) 230 kV Bus a. Apply fault at the NICHOLS 6230.00 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NICHOLS 6 (524044) 230.0 kV to NICHOLS 3 (524043) 115.0 kV to NICHOLS_TR11 (524041) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1298 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV to BUSHLAND 3 (524266) 115.0 kV to BSHLND_TR1 1 (524263) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1299 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV to RANDALL 3 (524364) 115.0 kV to RANDAL_TR1 1 (524361) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1300 | 3 Phase fault on DEAFSMITH 6230.00 (524623) 230 kV Bus a. Apply fault at the DEAFSMITH 6230.00 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEAFSMITH 6 (524623) 230.0 kV to DFSMTH_WST 3 (524622) 115.0 kV to DEFSMTH_TR11 (524620) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1301 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV to SWISHER 3 (525212) 115.0 kV to SWISHER_TR11 (525211) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1302 | 3 Phase fault on NEWHART 6230.00 (525461) 230 kV Bus a. Apply fault at the NEWHART 6230.00 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWHART 6 (525461) 230.0 kV to NEWHART 3 (525460) 115.0 kV to NEWHART_TR11 (525459) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1303 | 3 Phase fault on PLANT_X 6230.00 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6230.00 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 (525481) 230.0 kV to PLANT_X 3 (525480) 115.0 kV to PLANTX_TR1 1 (525479) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1304 | 3 Phase fault on TOLK 7345.00 (525549) 345 kV Bus a. Apply fault at the TOLK 7345.00 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 (525549) 345.0 kV to TOLK 6 (525531) 230.0 kV to TOLK_TR 1 (525537) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1305 | 3 Phase fault on SUNDOWN 6230.00 (526435) 230 kV Bus a. Apply fault at the SUNDOWN 6230.00 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNDOWN 6 (526435) 230.0 kV to SUNDOWN 3 (526434) 115.0 kV to SUNDOWN_TR11 (526432) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1306 | 3 Phase fault on HUGOTON3 115.00 (531481) 115 kV Bus a. Apply fault at the HUGOTON3 115.00 (531481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOTON2 (531380) 69.0 kV to HUGOTON3 (531481) 115.0 kV to HUGOTON1 (531261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1307 | 3 Phase fault on PIONEER3 115.00 (531391) 115 kV Bus a. Apply fault at the PIONEER3 115.00 (531391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONEER2 (531390) 69.0 kV to PIONEER3 (531391) 115.0 kV to PIONEER1 (531251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1308 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1309 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1310 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1311 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1312 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1313 | 3 Phase fault on SEWARD-3 115.00 (531467) 115 kV Bus a. Apply fault at the SEWARD-3 115.00 (531467) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMSSWRD2 (531466) 69.0 kV to SEWARD-3 (531467) 115.0 kV to SEWARD 1 (531260) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1314 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1315 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1316 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1317 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1318 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1319 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1320 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1321 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1322 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1323 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1324 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1325 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1326 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1327 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1328 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1329 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1330 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1331 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1332 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1333 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1334 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1335 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1336 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1337 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1338 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1339 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1340 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1341 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1342 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1343 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1344 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1345 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1346 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1347 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1348 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1349 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1350 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1351 | 3 Phase fault on TECHILL5 161.00 (532920) 161 kV Bus a. Apply fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1352 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1353 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1354 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1355 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1356 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1357 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1358 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1359 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1360 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1361 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1362 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1363 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1364 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1365 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1366 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1367 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1368 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1369 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1370 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1371 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1372 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1373 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1374 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-018 (588633 and 588637). The trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1375 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1376 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1377 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1378 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1379 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1380 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1381 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1382 | 3 Phase fault on WBURGE 5 161.00 (541228) 161 kV Bus a. Apply fault at the WBURGE 5 161.00 (541228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WBURGE 2 (541269) 69.0 kV to WBURGE 5 (541228) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1383 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1384 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1385 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBRTYS2 (543095) 69.0 kV to LBRTYST5 (541248) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1386 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1387 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1388 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1389 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1390 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1391 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1392 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1393 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1394 | 3 Phase fault on SWAVRLY5 161.00 (543063) 161 kV Bus a. Apply fault at the SWAVRLY5 161.00 (543063) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWAVRLY2 (543094) 69.0 kV to SWAVRLY5 (543063) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1395 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1396 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1397 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1398 | 3 Phase fault on AUR124 5 161.00 (547468) 161 kV Bus a. Apply fault at the AUR124 5 161.00 (547468) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUR124 5 (547468) 161.0 kV to AUR124 2 (547537) 69.0 kV to AUR1241 (547704) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1399 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1400 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1401 | 3 Phase fault on NEO184 5 161.00 (547471) 161 kV Bus a. Apply fault at the NEO184 5 161.00 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 (547471) 161.0 kV to NEO184 2 (547543) 69.0 kV to NEO184B1 (547709) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1402 | 3 Phase fault on DAD368 5 161.00 (547478) 161 kV Bus a. Apply fault at the DAD368 5 161.00 (547478) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAD368 5 (547478) 161.0 kV to DAD368 2 (547585) 69.0 kV to DAD368 1 (547711) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1403 | 3 Phase fault on MON383 5 161.00 (547480) 161 kV Bus a. Apply fault at the MON383 5 161.00 (547480) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MON383 5 (547480) 161.0 kV to MON383 2 (547591) 69.0 kV to MON383 1 (547712) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1404 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1405 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1406 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1407 | 3 Phase fault on NOL435 5 161.00 (547496) 161 kV Bus a. Apply fault at the NOL435 5 161.00 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 5 (547496) 161.0 kV to NOL435 2 (547610) 69.0 kV to NOL435 1 (547720) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1408 | 3 Phase fault on CPK446 5 161.00 (547499) 161 kV Bus a. Apply fault at the CPK446 5 161.00 (547499) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CPK446 5 (547499) 161.0 kV to CPK446 2 (547618) 69.0 kV to CPK446 1 (547721) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1409 | 3 Phase fault on RNM393 5 161.00 (547500) 161 kV Bus a. Apply fault at the RNM393 5 161.00 (547500) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNM393 5 (547500) 161.0 kV to RNM393 2 (547595) 69.0 kV to RNM393 1 (547722) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1410 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1411 | 3 Phase fault on MAIN STREET5161.00 (549958) 161 kV Bus a. Apply fault at the MAIN STREET5161.00 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAIN STREET5 (549958) 161.0 kV to MAIN STREET2 (549921) 69.0 kV to MAINST XF1 1 (549936) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1412 | 3 Phase fault on BATTLEFIELD5161.00 (549959) 161 kV Bus a. Apply fault at the BATTLEFIELD5161.00 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLEFIELD5 (549959) 161.0 kV to BATTLEFIELD2 (549979) 69.0 kV to BATLEFLDXF11 (549980) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1413 | 3 Phase fault on MILL 5161.00 (549962) 161 kV Bus a. Apply fault at the MILL 5161.00 (549962) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILL 5 (549962) 161.0 kV to MILL 2 (549918) 69.0 kV to MILL XF1 1 (549946) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1414 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1415 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1416 | 3 Phase fault on BUSHLAND 6230.00 (524267) 230 kV Bus a. Apply fault at the BUSHLAND 6230.00 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUSHLAND 6 (524267) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1417 | 3 Phase fault on RANDALL 6230.00 (524365) 230 kV Bus a. Apply fault at the RANDALL 6230.00 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDALL 6 (524365) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1418 | 3 Phase fault on SWISHER 6230.00 (525213) 230 kV Bus a. Apply fault at the SWISHER 6230.00 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 (525213) 230.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1419 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 7 (531465) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1420 | 3 Phase fault on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BROOKLINE 7 (549984) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Local_Fault_1421 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_001 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_002 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_003 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_004 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.4. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_005 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_006 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_007 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_008 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_009 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_010 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_011 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_012 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_013 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_014 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_015 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_016 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_017 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_018 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_019 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_020 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_021 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_022 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_023 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_024 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_025 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_026 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_027 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Non-dampening oscillations observed in the active power output of GEN-17-060 (588984) following the event. | GEN-17-060 drive train model was disabled and the issue was resolved.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_028 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_029 | 3 Phase fault on BUFF_DUNES 7345.00 (523118) 345 kV Bus a. Apply fault at the BUFF_DUNES 7345.00 (523118) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_030 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_031 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_032 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_033 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to GEN-2018-032 (762680) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_034 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_035 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_036 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_037 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_038 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_039 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-19-063 (763926). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_040 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-19-063 (763926). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_041 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2017-018 (588630) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-018 (588633 and 588637). The trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_042 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to GEN-2018-049 (762834) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-018 (588633 and 588637). The trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_043 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_044 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_045 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_046 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_047 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_048 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_049 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_050 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_051 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_052 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_053 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_054 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_055 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_056 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_057 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-17-121 (761841 and 761744). The trips also occur in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_058 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-17-018 (588633 and 588637). The trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_059 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to (659608) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P1_Regional_Fault_060 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO3 (640325) 345.0 kV Fixed Shunt Device c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_001 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.4. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_002 | Single Phase Fault with Stuck Breaker on 5GRANDVIEW% 161.00 (338099) 161 kV Bus a. Apply Fault at the 5GRANDVIEW% 161.00 (338099) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GRANDVIEW% (338099) 161.0 kV to 5OSAGE CRK#! (338682) 161.0 kV Transmission Circuit #1 b.2. 5GRANDVIEW% (338099) 161.0 kV to EUREKA 5 (506932) 161.0 kV Transmission Circuit #1 b.3. 5GRANDVIEW% (338099) 161.0 kV to TABLE R5 (505472) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_003 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_004 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_005 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_006 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_007 | Single Phase Fault with Stuck Breaker on BLSPS 5 161.00 (541211) 161 kV Bus a. Apply Fault at the BLSPS 5 161.00 (541211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRALEE 5 (541206) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.2. BLSPE 5 (541205) 161.0 kV to BLSPS 5 (541211) 161.0 kV Transmission Circuit #1 b.3. BLSPE 5 (541205) 161.0 kV to GRAINVL5 (541226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_008 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_009 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_010 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_011 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_012 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_013 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_014 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_015 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_016 | Single Phase Fault with Stuck Breaker on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply Fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_017 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_018 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_019 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_020 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_021 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_022 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_023 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_024 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_025 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_026 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_027 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_028 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_029 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_030 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_031 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_032 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_033 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_034 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_035 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_036 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_037 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_038 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 b.2. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_039 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_040 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_041 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_042 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_043 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_044 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_045 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_046 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_047 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_048 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_049 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_050 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_051 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_052 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_053 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_054 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_055 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_056 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_057 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVWF1-TERT1 (539743) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV Three Winding #1 b.2. SVWF3-TERT1 (539744) 13.8 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV Three Winding #1 b.3. SVWF1-CLCT1 (539115) 34.5 kV to SVWF1-TX1 (539752) 34.5 kV Transmission Circuit #1 b.4. SVWF1-TX1 (539752) 34.5 kV to SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_058 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.4. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_059 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.2. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.3. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_060 | Single Phase Fault with Stuck Breaker on CIMWD2 7 345.00 (531504) 345 kV Bus a. Apply Fault at the CIMWD2 7 345.00 (531504) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMWD2 7 (531504) 345.0 kV Transmission Circuit #1 b.3. CIMWD2 7 (531504) 345.0 kV to CIMWD2 1 (531505) 34.5 kV to CIMWD2-T 1 (531506) 13.8 kV Three Winding #1 b.4. CIMWD2 1 (531505) 34.5 kV to CIMARON_CB (531604) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_061 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_062 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_063 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.3. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.4. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_064 | Single Phase Fault with Stuck Breaker on BUCKNER7 345.00 (531501) 345 kV Bus a. Apply Fault at the BUCKNER7 345.00 (531501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCKNER7 (531501) 345.0 kV to CIMRRN 7 (531502) 345.0 kV Transmission Circuit #1 b.2. CIMRRN 7 (531502) 345.0 kV to CIMRRN 1 (531503) 34.5 kV Two Winding #1 b.3. CIMRRN 1 (531503) 34.5 kV to CIMARON-GSU1 (531602) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_065 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_066 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_067 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_068 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_069 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_070 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_071 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.5. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_072 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.3. SETAB 7 (531465) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_073 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_074 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_075 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_076 | Single Phase Fault with Stuck Breaker on CONCRD6 230.00 (539658) 230 kV Bus a. Apply Fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_077 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.3. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.4. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.5. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_078 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.4. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_079 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_080 | Single Phase Fault with Stuck Breaker on N-GBEND3 115.00 (539681) 115 kV Bus a. Apply Fault at the N-GBEND3 115.00 (539681) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBNDTT (539920) 13.8 kV to GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV Three Winding #1 b.2. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.3. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.4. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_081 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_082 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_083 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_084 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_085 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_086 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_087 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_088 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_089 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_090 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_091 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_092 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_093 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_094 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_095 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_096 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_097 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_098 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_099 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_100 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_101 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_102 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_103 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_104 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_105 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_106 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_107 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_108 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_109 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_110 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_111 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_112 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_113 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_114 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_115 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_116 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_117 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_118 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 b.2. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_119 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_120 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_121 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_122 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_123 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_124 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_125 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_126 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV to CHAMSPR1 (506919) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_127 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR7 (506945) 345.0 kV to TONTITN7 (506959) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_128 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_129 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_130 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_131 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_132 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_133 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_134 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_135 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_136 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_137 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_138 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_139 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_140 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_141 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_142 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_143 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_144 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_145 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_146 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_147 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_148 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_149 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_150 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_151 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_152 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_153 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_154 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_155 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_156 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_157 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_158 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_159 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_160 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_161 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_162 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_163 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_164 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_165 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_166 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_167 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_168 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_169 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_170 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_171 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_172 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_173 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_174 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_175 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_176 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_177 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_178 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_179 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_180 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_181 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_182 | Single Phase Fault with Stuck Breaker on 1THLG3 24.000 (300003) 24 kV Bus a. Apply Fault at the 1THLG3 24.000 (300003) 24 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5THOMHLXF4 (301510) 161.0 kV to 7THOMHL (300049) 345.0 kV Two Winding #4 b.2. 5THMHLB4 (301443) 161.0 kV to 5THOMHLXF4 (301510) 161.0 kV Transmission Circuit #1 b.3. 7THOMHL (300049) 345.0 kV to 7THOMHLGSU3 (301503) 345.0 kV Transmission Circuit #1 b.4. 1THLG3 (300003) 24.0 kV to 7THOMHLGSU3 (301503) 345.0 kV Two Winding #3 b.5. 1THLG3 (300003) 24.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_183 | Single Phase Fault with Stuck Breaker on NES3-1 22.000 (511840) 22 kV Bus a. Apply Fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. NES3-1 (511840) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_184 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_185 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_186 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_188 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.2. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.4. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.5. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.6. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.7. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_189 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_190 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_191 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_192 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_193 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_194 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 3 (530601) 115.0 kV to HZRNGPL3 (530609) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_195 | Single Phase Fault with Stuck Breaker on ALBERT 2 69.000 (530586) 69 kV Bus a. Apply Fault at the ALBERT 2 69.000 (530586) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.5. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_196 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT3 1 (530628) 12.5 kV Three Winding #3 b.4. HEIZER 2 (530563) 69.0 kV to GB NTH 2 (530568) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_197 | Single Phase Fault with Stuck Breaker on PRWNDCL1 34.500 (530701) 34.5 kV Bus a. Apply Fault at the PRWNDCL1 34.500 (530701) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to RICE 3 (530623) 115.0 kV to RICET1 (530687) 12.5 kV Three Winding #1 b.4. RICE 6 (530686) 230.0 kV to BUFLOCRK6 (530688) 230.0 kV Transmission Circuit #1 b.5. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.6. BUFLOCRK6 (530688) 230.0 kV to BUFLOCRK1 (530689) 34.5 kV to BUFCRKT11 (530691) 12.5 kV Three Winding #1 b.8. BUFLOCRK1 (530689) 34.5 kV to PRWNDCL1 (530701) 34.5 kV Transmission Circuit #1 b.10. PRWINDG1 (530690) 0.7 kV to PRWNDCL1 (530701) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_198 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_199 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_200 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_201 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_202 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_203 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_204 | Single Phase Fault with Stuck Breaker on FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus a. Apply Fault at the FLTWTR1W 0.6900 (645061) 0.689999998 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.3. S1399 5 (646399) 161.0 kV to FLTWTRX9 (648500) 34.5 kV to FLTWTRY9 (648501) 13.8 kV Three Winding #1 b.6. FLTWTR1W (645061) 0.7 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_205 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR5 (506944) 161.0 kV to CHAMSPR7 (506945) 345.0 kV to CHAMSPR1 (506919) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_206 | Single Phase Fault with Stuck Breaker on CHAMSPR7 345.00 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 345.00 (506945) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAMSPR7 (506945) 345.0 kV to CLARKSV7 (509745) 345.0 kV Transmission Circuit #1 b.2. CHAMSPR7 (506945) 345.0 kV to TONTITN7 (506959) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_207 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_208 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_209 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_210 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_211 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_212 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_213 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_214 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_215 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_216 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_217 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_218 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_219 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_220 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 b.2. RSS T2 4 (509875) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST2 T1 (509876) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_221 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_222 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_223 | Single Phase Fault with Stuck Breaker on SAPLPRD7 345.00 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 345.00 (509870) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. SAPLPRD4 (509871) 138.0 kV to SAPLPRD7 (509870) 345.0 kV to SAPLPRD1 (509872) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_224 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_225 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_226 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_227 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_228 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_229 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_230 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_231 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_232 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_233 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_234 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_235 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_236 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_237 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_238 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_239 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_240 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_241 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_242 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_243 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_244 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_245 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_246 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_247 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_248 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_249 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_250 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_251 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 b.2. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_252 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_253 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_254 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_255 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_256 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_257 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_258 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_259 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_260 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_261 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_262 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_263 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Fixed Shunt Device | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_264 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_265 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.4. CHISHOLM7 (511553) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #2 b.5. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.6. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.7. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #2 b.9. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.10. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_266 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_267 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_268 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BADGER 7 (515677) 345.0 kV to BLUWND 7 (515686) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_269 | Single Phase Fault with Stuck Breaker on BADGER 7 345.00 (515677) 345 kV Bus a. Apply Fault at the BADGER 7 345.00 (515677) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #1 b.2. BADGER 7 (515677) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_270 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_271 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to BADGER 7 (515677) 345.0 kV Transmission Circuit #2 b.2. BVRCNTY7 (515554) 345.0 kV to BALKOW 7 (515618) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_272 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 b.2. BORDER 7 (515458) 345.0 kV to CRAWFISH_DR (560022) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_273 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_274 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_275 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_276 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_277 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_278 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_279 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_280 | Single Phase Fault with Stuck Breaker on MUSKOGE7 345.00 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 345.00 (515224) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. CLARKSV7 (509745) 345.0 kV to MUSKOGE7 (515224) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_281 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_282 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. OPENSKY7 (515621) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_283 | Single Phase Fault with Stuck Breaker on OPENSKY7 345.00 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 345.00 (515621) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAYWIND7 (514825) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_284 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUSKOGE7 (515224) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_285 | Single Phase Fault with Stuck Breaker on PECANCK7 345.00 (515235) 345 kV Bus a. Apply Fault at the PECANCK7 345.00 (515235) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECANCK5 (515234) 161.0 kV to PECANCK7 (515235) 345.0 kV to PECANC21 (515759) 13.8 kV Three Winding #2 b.4. R.S.S.-7 (509782) 345.0 kV to PECANCK7 (515235) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_286 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_287 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to FRNTWND7 (515688) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_288 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_289 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to OMCDLEC7 (529200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_290 | Single Phase Fault with Stuck Breaker on RANCHRD7 345.00 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 345.00 (515576) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANCHRD7 (515576) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 b.2. RANCHRD7 (515576) 345.0 kV to G18-071_TAP (763069) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_291 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #2 b.2. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_292 | Single Phase Fault with Stuck Breaker on REDBUD 7 345.00 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 345.00 (514909) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #1 b.2. ARCADIA7 (514908) 345.0 kV to REDBUD 7 (514909) 345.0 kV Transmission Circuit #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_293 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_294 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_295 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_296 | Single Phase Fault with Stuck Breaker on SOONER 7 345.00 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 345.00 (514803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOONER 7 (514803) 345.0 kV to RANCHRD7 (515576) 345.0 kV Transmission Circuit #1 b.2. SOONER 7 (514803) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_297 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_298 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_299 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_300 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_301 | Single Phase Fault with Stuck Breaker on NES3-1 22.000 (511840) 22 kV Bus a. Apply Fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. NES3-1 (511840) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_302 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 b.2. DOGWDCT1 (541163) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.3. DOGWDCT2 (541164) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 b.4. DOGWDSTG (541162) 18.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_303 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_304 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-18-022 (765284, 765287, and 765288). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_305 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.3. ATLNTIC7 (542940) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.4. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.5. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.6. W.GRDNR7 (542965) 345.0 kV to GEN-2017-195 (762279) 345.0 kV Transmission Circuit #1 b.7. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_306 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.4. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 b.5. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_307 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.3. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.4. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_308 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. ATLNTIC7 (542940) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.4. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.5. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_309 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.3. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.4. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.5. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_310 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.4. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.6. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relay trips GEN-18-031 (762672). This trip also occurs in the Base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_311 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-18-022 (765284, 765287, and 765288). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_312 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 b.3. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 b.4. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.5. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.6. MULLNCR7 (541197) 345.0 kV to GEN-2018-022 (762581) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Frequency relay trips GEN-18-022 (765284, 765287, and 765288). This trip also occurs in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_313 | Single Phase Fault with Stuck Breaker on OSBORN7 345.00 (541501) 345 kV Bus a. Apply Fault at the OSBORN7 345.00 (541501) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 b.2. OSBORN7 (541501) 345.0 kV to OSBORN_B1_1 (541502) 34.5 kV to OSBORN_TER_1 (541505) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_314 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.3. HOLT 7 (541510) 345.0 kV to ROCKCK7 (541511) 345.0 kV Transmission Circuit #1 b.4. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.5. HOLT 7 (541510) 345.0 kV to GEN-2017-115 (760746) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_315 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.3. KETCHEM7 (541500) 345.0 kV to OSBORN7 (541501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_316 | Single Phase Fault with Stuck Breaker on LACYGNE11_7 345.00 (543629) 345 kV Bus a. Apply Fault at the LACYGNE11_7 345.00 (543629) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 b.2. LACYGNE11_7 (543629) 345.0 kV to LAC11_AQC1 (543630) 13.8 kV to LAC11_TER1 (543631) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_317 | Single Phase Fault with Stuck Breaker on LACYGNE22_7 345.00 (543632) 345 kV Bus a. Apply Fault at the LACYGNE22_7 345.00 (543632) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 b.2. LACYGNE22_7 (543632) 345.0 kV to LAC22_AQC1 (543633) 13.8 kV to LAC22_TER1 (543634) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_318 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_319 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_320 | Single Phase Fault with Stuck Breaker on SEWARD 3 115.00 (539692) 115 kV Bus a. Apply Fault at the SEWARD 3 115.00 (539692) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.2. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.3. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.4. SWRD1 1 (530631) 12.5 kV to SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV Three Winding #1 b.6. SEWARD 2 (530565) 69.0 kV to GB STH 2 (530569) 69.0 kV Transmission Circuit #1 b.7. SEWARD 2 (530565) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.8. SEWARD 2 (530565) 69.0 kV to ZOOK 2 (530577) 69.0 kV Transmission Circuit #1 b.10. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.11. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.12. S ELWD 2 (530567) 69.0 kV to HUDSON 2 (530576) 69.0 kV Transmission Circuit #1 b.13. S ELWD 2 (530567) 69.0 kV to N ELWD 2 (530575) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_321 | Single Phase Fault with Stuck Breaker on LAXTAP 3 115.00 (530602) 115 kV Bus a. Apply Fault at the LAXTAP 3 115.00 (530602) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.9. NEKOMA 2 (530564) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.10. NEKOMA 2 (530564) 69.0 kV to WALNTCRK3 (530700) 69.0 kV Transmission Circuit #1 b.13. HEIZER 2 (530563) 69.0 kV to ALBERT 2 (530586) 69.0 kV Transmission Circuit #1 b.14. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.15. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_322 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 b.3. HARBNGR-T (531511) 13.8 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV Three Winding #1 b.4. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_323 | Single Phase Fault with Stuck Breaker on CONCORD3 115.00 (539657) 115 kV Bus a. Apply Fault at the CONCORD3 115.00 (539657) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCRD6 (539658) 230.0 kV to CONCORD3 (539657) 115.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 b.3. CONCOD-T (539904) 13.8 kV to CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV Three Winding #1 b.4. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.5. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.6. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to CONCORD1 (539705) 34.5 kV to CONCOW-T (539905) 5.1 kV Three Winding #1 b.9. CONCORD3 (539657) 115.0 kV to CCORDIA1 (539745) 34.5 kV to CCORD-T (539945) 7.2 kV Three Winding #1 b.10. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.11. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.12. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_324 | Single Phase Fault with Stuck Breaker on SEWRDMW3 115.00 (530679) 115 kV Bus a. Apply Fault at the SEWRDMW3 115.00 (530679) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.2. ELLSWTP3 (539642) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.3. GBENDTP3 (539666) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 b.4. GRTBEND3 (539678) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.5. GRTBEND3 (539678) 115.0 kV to OTISSUB3 (539684) 115.0 kV Transmission Circuit #1 b.6. GRTBEND1 (539677) 13.8 kV to GRTBEND3 (539678) 115.0 kV Two Winding #1 b.7. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.8. GRTBEND3 (539678) 115.0 kV to GRTBEND1 (539719) 34.5 kV to GRTBENDT (539921) 7.2 kV Three Winding #1 b.10. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.11. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.12. GRTBEND6 (539679) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.13. GRTBEND6 (539679) 230.0 kV to G19-054-TAP (763862) 230.0 kV Transmission Circuit #1 b.15. 24-FREY3 (539661) 115.0 kV to N-GBEND3 (539681) 115.0 kV Transmission Circuit #1 b.16. N-GBEND3 (539681) 115.0 kV to N-GBEND1 (539721) 34.5 kV to NGBEND-T (539923) 13.8 kV Three Winding #1 b.17. 24-FREY3 (539661) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.18. 24-FREY3 (539661) 115.0 kV to GEN-2018-116 (763329) 115.0 kV Transmission Circuit #1 b.19. 24-FREY3 (539661) 115.0 kV to 24-FREY1 (539707) 34.5 kV to 24-FREYT (539907) 13.8 kV Three Winding #1 b.20. GBENDTP3 (539666) 115.0 kV to 2ND-KS 3 (539689) 115.0 kV Transmission Circuit #1 b.21. 2ND-KS 3 (539689) 115.0 kV to 2ND-KS 1 (539728) 34.5 kV to 2ND-KS T (539931) 13.8 kV Three Winding #1 b.22. GBENDTP3 (539666) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.23. SEWRDMW3 (530679) 115.0 kV to SEWARD 3 (539692) 115.0 kV Transmission Circuit #1 b.24. SEWARD 3 (539692) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #1 b.25. SEWRDMW3 (530679) 115.0 kV to SEWARD 2 (530565) 69.0 kV to SWRD1 1 (530631) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_325 | Single Phase Fault with Stuck Breaker on SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus a. Apply Fault at the SVWF3-CLCT1 34.500 (539119) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRVILL-EHVB (539117) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #z1 b.2. SPEARVL6 (539695) 230.0 kV to G19-055-TAP (763850) 230.0 kV Transmission Circuit #1 b.3. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 b.4. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 b.5. SPRVILL-EHVB (539117) 230.0 kV to SVWF1-TX1 (539752) 34.5 kV to SVWF1-TERT1 (539743) 13.8 kV Three Winding #1 b.6. SPRVILL-EHVB (539117) 230.0 kV to SVWF2-TX1 (539133) 34.5 kV to SVWF2-TERT1 (539134) 13.8 kV Three Winding #1 b.7. SPRVILL-EHVB (539117) 230.0 kV to SVWF3-TX1 (539118) 34.5 kV to SVWF3-TERT1 (539744) 13.8 kV Three Winding #1 b.8. SPERVLTT (539935) 13.8 kV to SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV Three Winding #1 b.9. SPEARVL3 (539694) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 b.11. SPEARVL3 (539694) 115.0 kV to SPEARVL1 (539732) 34.5 kV to SPERVLDT (539936) 13.8 kV Three Winding #1 b.12. SVWF2 1 (539136) 0.6 kV to SVWF2-CLCT1 (539135) 34.5 kV Two Winding #1 b.13. SVWF1 1 (539116) 0.6 kV to SVWF1-CLCT1 (539115) 34.5 kV Two Winding #1 b.14. SVWF3-CLCT1 (539119) 34.5 kV to SVWF3 1 (539120) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_326 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_327 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_328 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.3. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.4. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.5. STRANGR7 (532772) 345.0 kV to GEN-2016-149 (588240) 345.0 kV Transmission Circuit #1 b.6. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 b.7. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_329 | Single Phase Fault with Stuck Breaker on READWF 7 345.00 (532776) 345 kV Bus a. Apply Fault at the READWF 7 345.00 (532776) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to READWF 7 (532776) 345.0 kV Transmission Circuit #1 b.2. READWF 7 (532776) 345.0 kV to R1 WFTX1 (534040) 34.5 kV to R1 LV 1 (534043) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_330 | Single Phase Fault with Stuck Breaker on GEN-2017-009345.00 (532778) 345 kV Bus a. Apply Fault at the GEN-2017-009345.00 (532778) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009XFMR1 (534056) 34.5 kV to GEN-2017-009 (532778) 345.0 kV Two Winding #1 b.3. G17-009XFMR2 (534057) 34.5 kV to GEN-2017-009 (532778) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_331 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_332 | Single Phase Fault with Stuck Breaker on CANEYWF7 345.00 (532781) 345 kV Bus a. Apply Fault at the CANEYWF7 345.00 (532781) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.2. CANEYWF7 (532781) 345.0 kV to CNYWFLV12 (533077) 34.5 kV to CNYWF1 2 (533100) 13.2 kV Three Winding #1 b.3. CANEYWF7 (532781) 345.0 kV to CNYWFLV11 (533079) 34.5 kV to CNYWF1 1 (533102) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_333 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_334 | Single Phase Fault with Stuck Breaker on KINGMAN7 345.00 (532783) 345 kV Bus a. Apply Fault at the KINGMAN7 345.00 (532783) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 b.3. KINGMAN7 (532783) 345.0 kV to K1 LV 1 (534001) 34.5 kV to K1 WFTX1 (534031) 13.8 kV Three Winding #1 b.4. KINGMAN7 (532783) 345.0 kV to K2 LV 1 (534002) 34.5 kV to K2 WFTX1 (534032) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_335 | Single Phase Fault with Stuck Breaker on NINN1WF7 345.00 (532784) 345 kV Bus a. Apply Fault at the NINN1WF7 345.00 (532784) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KINGMAN7 (532783) 345.0 kV to NINN1WF7 (532784) 345.0 kV Transmission Circuit #1 b.2. NINN1WF7 (532784) 345.0 kV to PRATTWF7 (532785) 345.0 kV Transmission Circuit #1 b.3. NINN1WF7 (532784) 345.0 kV to N1 LV 1 (534000) 34.5 kV to N1 WFTX1 (534030) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_336 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_337 | Single Phase Fault with Stuck Breaker on FR2EAST7 345.00 (532792) 345 kV Bus a. Apply Fault at the FR2EAST7 345.00 (532792) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR2EAST7 (532792) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. FR2EAST7 (532792) 345.0 kV to FR2ELV11 (533131) 34.5 kV to F2EAST11 (533127) 13.8 kV Three Winding #1 b.4. FR2EAST7 (532792) 345.0 kV to FR2ELV21 (533132) 34.5 kV to F2EAST21 (533128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_338 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_339 | Single Phase Fault with Stuck Breaker on FR2WEST7 345.00 (532795) 345 kV Bus a. Apply Fault at the FR2WEST7 345.00 (532795) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FR2EAST7 (532792) 345.0 kV to FR2WEST7 (532795) 345.0 kV Transmission Circuit #1 b.2. FR2WEST7 (532795) 345.0 kV to FR3HV (578530) 345.0 kV Transmission Circuit #1 b.3. FR2WEST7 (532795) 345.0 kV to FR2WLV11 (533133) 34.5 kV to F2WEST11 (533129) 13.8 kV Three Winding #1 b.4. FR2WEST7 (532795) 345.0 kV to FR2WLV21 (533134) 34.5 kV to F2WEST21 (533130) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_340 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_341 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_342 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_343 | Single Phase Fault with Stuck Breaker on ELKRVR17 345.00 (532801) 345 kV Bus a. Apply Fault at the ELKRVR17 345.00 (532801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 b.2. ELKRVR17 (532801) 345.0 kV to ER1 CLCT1 (534016) 34.5 kV to ER1 TERT1 (534036) 13.2 kV Three Winding #1 b.3. ELKRVR17 (532801) 345.0 kV to ER2 CLCT1 (534017) 34.5 kV to ER2 TERT1 (534037) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_344 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_345 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_346 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_347 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.3. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 b.4. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_348 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.3. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.4. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_349 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_350 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_351 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_352 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.3. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.4. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.5. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.6. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.7. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 b.8. ONETA--7 (509807) 345.0 kV to ONETA--4 (509806) 138.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_353 | Single Phase Fault with Stuck Breaker on GEN-2020-001345.00 (764255) 345 kV Bus a. Apply Fault at the GEN-2020-001345.00 (764255) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-001 (764255) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-001 (764255) 345.0 kV to G20-001-XFM1 (764258) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_354 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB3345.00 (659133) 345 kV Bus a. Apply Fault at the SIDNEY__-MB3345.00 (659133) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB4 (659210) 230.0 kV to SIDNEY__-MB3 (659133) 345.0 kV to SIDNEY__-MB9 (659168) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_355 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3345.00 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3345.00 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to LARAMIE_-MB3 (659131) 345.0 kV Transmission Circuit #1 b.2. STEGALL_-MB3 (659135) 345.0 kV to SIDNEY__-MB3 (659133) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_356 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S914A 8 (647014) 69.0 kV to S1214 5 (646214) 161.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 b.2. S914A 8 (647014) 69.0 kV to S914 8 (647914) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_357 | Single Phase Fault with Stuck Breaker on S983 8 69.000 (647983) 69 kV Bus a. Apply Fault at the S983 8 69.000 (647983) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S983 8 (647983) 69.0 kV to S6846 8 (647846) 69.0 kV Transmission Circuit #1 b.2. S983 8 (647983) 69.0 kV to S902 8 (647902) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_358 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_359 | Single Phase Fault with Stuck Breaker on GEN-2020-011345.00 (764420) 345 kV Bus a. Apply Fault at the GEN-2020-011345.00 (764420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-011 (764420) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-011 (764420) 345.0 kV to G20-011-SS3 (764433) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_360 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_361 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_362 | Single Phase Fault with Stuck Breaker on GEN-2020-013115.00 (764435) 115 kV Bus a. Apply Fault at the GEN-2020-013115.00 (764435) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-013 (764435) 115.0 kV to G20-013-TAP (764445) 115.0 kV Transmission Circuit #1 b.2. GEN-2020-013 (764435) 115.0 kV to G20-013-SS2 (764447) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_363 | Single Phase Fault with Stuck Breaker on GEN-2020-027161.00 (764615) 161 kV Bus a. Apply Fault at the GEN-2020-027161.00 (764615) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-027 (764615) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-027 (764615) 161.0 kV to G20-027-XFM1 (764618) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_364 | Single Phase Fault with Stuck Breaker on S1281 5 161.00 (646281) 161 kV Bus a. Apply Fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_365 | Single Phase Fault with Stuck Breaker on GEN-2020-031161.00 (764660) 161 kV Bus a. Apply Fault at the GEN-2020-031161.00 (764660) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-031 (764660) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-031 (764660) 161.0 kV to G20-031-GEN1 (764661) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_366 | Single Phase Fault with Stuck Breaker on GEN-2020-028161.00 (764630) 161 kV Bus a. Apply Fault at the GEN-2020-028161.00 (764630) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-028 (764630) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-028 (764630) 161.0 kV to G20-028-GEN1 (764631) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_367 | Single Phase Fault with Stuck Breaker on GEN-2020-025161.00 (764600) 161 kV Bus a. Apply Fault at the GEN-2020-025161.00 (764600) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-025 (764600) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-025 (764600) 161.0 kV to G20-025-GEN1 (764601) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_368 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_369 | Single Phase Fault with Stuck Breaker on GEN-2020-038345.00 (764705) 345 kV Bus a. Apply Fault at the GEN-2020-038345.00 (764705) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-038 (764705) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-038 (764705) 345.0 kV to G20-038-GEN1 (764706) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_370 | Single Phase Fault with Stuck Breaker on GEN-2018-033345.00 (762691) 345 kV Bus a. Apply Fault at the GEN-2018-033345.00 (762691) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2018-033 (762691) 345.0 kV to G18-033XFM1 (762692) 34.5 kV Two Winding #1 b.2. GEN-2018-033 (762691) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_371 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_372 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_373 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Voltage relays trip Outlaw units (541546, 541549, and 541550). These relay trip also occur in the base case. | Protection relay instance was disabled and no issues were observed during the simulations without that protection.
03 - Central | 25W | Transfer | G03_P4_Local_Fault_374 | Single Phase Fault with Stuck Breaker on GEN-2020-036345.00 (764690) 345 kV Bus a. Apply Fault at the GEN-2020-036345.00 (764690) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-036 (764690) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-036 (764690) 345.0 kV to G20-036-XFM1 (764693) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_375 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_376 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_377 | Single Phase Fault with Stuck Breaker on GEN-2020-045161.00 (764750) 161 kV Bus a. Apply Fault at the GEN-2020-045161.00 (764750) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-045 (764750) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-045 (764750) 161.0 kV to G20-045-GEN1 (764751) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_378 | Single Phase Fault with Stuck Breaker on GEN-2020-043161.00 (764720) 161 kV Bus a. Apply Fault at the GEN-2020-043161.00 (764720) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-043 (764720) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-043 (764720) 161.0 kV to G20-043-GEN1 (764721) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_379 | Single Phase Fault with Stuck Breaker on GEN-2020-044161.00 (764735) 161 kV Bus a. Apply Fault at the GEN-2020-044161.00 (764735) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-044 (764735) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. GEN-2020-044 (764735) 161.0 kV to G20-044-GEN1 (764736) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_380 | Single Phase Fault with Stuck Breaker on GEN-2020-069115.00 (764465) 115 kV Bus a. Apply Fault at the GEN-2020-069115.00 (764465) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-069 (764465) 115.0 kV to G20-069-XFM1 (764468) 34.5 kV Two Winding #1 b.2. GEN-2020-069 (764465) 115.0 kV to G20-069-TAP (764475) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_381 | Single Phase Fault with Stuck Breaker on GEN-2020-070345.00 (765025) 345 kV Bus a. Apply Fault at the GEN-2020-070345.00 (765025) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-070 (765025) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-070 (765025) 345.0 kV to G20-070-XFM1 (765028) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_382 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to G20-070-TAP (765035) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_383 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_384 | Single Phase Fault with Stuck Breaker on GEN-2020-077115.00 (764480) 115 kV Bus a. Apply Fault at the GEN-2020-077115.00 (764480) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-077 (764480) 115.0 kV to G20-077-XFM1 (764483) 34.5 kV Two Winding #1 b.2. GEN-2020-077 (764480) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_385 | Single Phase Fault with Stuck Breaker on FAIRBRY7 115.00 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 115.00 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to G20-077-TAP (764490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_386 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to CARLJCT7 (640105) 115.0 kV Transmission Circuit #1 b.2. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_387 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_388 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_389 | Single Phase Fault with Stuck Breaker on GEN-2020-078161.00 (764765) 161 kV Bus a. Apply Fault at the GEN-2020-078161.00 (764765) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-078 (764765) 161.0 kV to G20-078-XFM1 (764768) 34.5 kV Two Winding #1 b.2. GEN-2020-078 (764765) 161.0 kV to G20-078-TAP (764775) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_390 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM2 (762784) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM2 (762784) 34.5 kV to G18-043-GSU2 (762785) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_391 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM3 (762787) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM3 (762787) 34.5 kV to G18-043-GSU3 (762788) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_392 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-084-XFM1 (764783) 34.5 kV to G20-084-GSU1 (764782) 34.5 kV Transmission Circuit #1 b.2. G20-084-XFM1 (764783) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_393 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G20-084-XFM2 (764786) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G20-084-XFM2 (764786) 34.5 kV to G20-084-GSU2 (764785) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_394 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_395 | Single Phase Fault with Stuck Breaker on GEN-2018-043345.00 (762780) 345 kV Bus a. Apply Fault at the GEN-2018-043345.00 (762780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-XFM1 (762781) 34.5 kV to GEN-2018-043 (762780) 345.0 kV Two Winding #1 b.2. G18-043-XFM1 (762781) 34.5 kV to G18-043-GSU1 (762782) 34.5 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_396 | Single Phase Fault with Stuck Breaker on GEN-2020-094345.00 (764795) 345 kV Bus a. Apply Fault at the GEN-2020-094345.00 (764795) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2020-094 (764795) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. GEN-2020-094 (764795) 345.0 kV to G20-094-XFM1 (764798) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_397 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.2. 103&ROKEBY3 (650189) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_398 | Single Phase Fault with Stuck Breaker on SIDNEY__-MB4 (659210) 230 kV Bus a. Apply Fault at the SIDNEY__-MB4 (659210) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIDNEY__-MB4 (659210) 230.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_399 | Single Phase Fault with Stuck Breaker on STEGALL_-MB3 (659135) 345 kV Bus a. Apply Fault at the STEGALL_-MB3 (659135) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STEGALL_-MB3 (659135) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_400 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_401 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_402 | Single Phase Fault with Stuck Breaker on HOLDREG7 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_403 | Single Phase Fault with Stuck Breaker on ORLEANS7 (640310) 115 kV Bus a. Apply Fault at the ORLEANS7 (640310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORLEANS7 (640310) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_404 | Single Phase Fault with Stuck Breaker on S1281 5 (646281) 161 kV Bus a. Apply Fault at the S1281 5 (646281) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1281 5 (646281) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_405 | Single Phase Fault with Stuck Breaker on VALTN.W7 (640394) 115 kV Bus a. Apply Fault at the VALTN.W7 (640394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALTN.W7 (640394) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_406 | Single Phase Fault with Stuck Breaker on CODY 7 (640117) 115 kV Bus a. Apply Fault at the CODY 7 (640117) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CODY 7 (640117) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_407 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_408 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_409 | Single Phase Fault with Stuck Breaker on FAIRBRY7 (640169) 115 kV Bus a. Apply Fault at the FAIRBRY7 (640169) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FAIRBRY7 (640169) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_410 | Single Phase Fault with Stuck Breaker on HEBRN N7 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEBRN N7 (640218) 115.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_411 | Single Phase Fault with Stuck Breaker on S1226 5 (646226) 161 kV Bus a. Apply Fault at the S1226 5 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_412 | Single Phase Fault with Stuck Breaker on S1237 5 (646237) 161 kV Bus a. Apply Fault at the S1237 5 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_413 | Single Phase Fault with Stuck Breaker on G18-043-TAP (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Local_Fault_414 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 103&ROKEBY3 (650189) 345.0 kV to remove bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_001 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_002 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_003 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_004 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_005 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_006 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_007 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_008 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_009 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_010 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_011 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_012 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_013 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_014 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_015 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_016 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_017 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_018 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_019 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_020 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_021 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_022 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_023 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to G20-052-TAP (765110) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_024 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_025 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_026 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_027 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_028 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_029 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_030 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_031 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_032 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_033 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_034 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_035 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_036 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_037 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_038 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_039 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G20-011-TAP (764430) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_040 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_041 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_042 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_043 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_044 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_045 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_046 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_047 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_048 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 b.4. CARPENTER 7 (523823) 345.0 kV to GEN-2020-008 (764980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_049 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_050 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_051 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_052 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_053 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to KINGMAN7 (532783) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.4. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.5. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.6. BUFFALO7 (532782) 345.0 kV to GEN-2016-073 (587500) 345.0 kV Transmission Circuit #1 b.7. BUFFALO7 (532782) 345.0 kV to GEN-2017-220 (760284) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_054 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.3. BENTON 7 (532791) 345.0 kV to G20-076-TAP (765155) 345.0 kV Transmission Circuit #1 b.4. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.5. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_055 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.3. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.4. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.5. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 b.6. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 b.7. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_056 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.3. VIOLA 7 (532798) 345.0 kV to G18-128-TAP (763421) 345.0 kV Transmission Circuit #1 b.4. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.5. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_057 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to G20-007-TAP (766261) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_058 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_059 | Single Phase Fault with Stuck Breaker on WAVERTX7 345.00 (532802) 345 kV Bus a. Apply Fault at the WAVERTX7 345.00 (532802) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.2. WAVERTX7 (532802) 345.0 kV to WAVERTX1 (532954) 34.5 kV to WAVETV 1 (532961) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_060 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to GEN-2017-009 (532778) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.3. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_061 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_062 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 b.8. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.9. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.10. S1258 5 (646258) 161.0 kV to NC1HS 5 (648600) 161.0 kV Transmission Circuit #1 b.11. S1258 5 (646258) 161.0 kV to NC2HS 5 (648610) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25W | Transfer | G03_P4_Regional_Fault_063 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.4. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.5. S3458 3 (645458) 345.0 kV to G20-094-TAP (764805) 345.0 kV Transmission Circuit #1 b.6. S3458 3 (645458) 345.0 kV to NEBCTY1G (645011) 18.0 kV Two Winding #1 b.7. S3458 3 (645458) 345.0 kV to NEBCTY2G (645012) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes due to large reactive power oscillations observed in the output of Outlaw units (541549, 541550, 541546). This issue is also observed in the Base case. | Disabling the dynamic response of Outlaw units allows the simulation to complete and no violations are observed.
03 - Central | 25S | Base | G03_P1_Local_Fault_450 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_451 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_452 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_453 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_455 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to KEENAN 4 (515394) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_466 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_472 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_683 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BVRCNTY7 (515554) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_685 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25S | Base | G03_P1_Local_Fault_686 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Base | G03_P1_Local_Fault_452 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Base | G03_P1_Local_Fault_453 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Base | G03_P1_Local_Fault_455 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to KEENAN 4 (515394) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
03 - Central | 25W | Base | G03_P1_Local_Fault_466 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BECKHAM7 (516059) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulation crashes following the fault. | 1- Acceleration factor was reduced to 0.1. 2- Reclosing was removed.
04 - Southeast | 25S | Transfer | Group4_Fault_0001_P4 | a. Apply SLG fault at SW SHV 7 (507760) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from SW SHV 7 (507760) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip SW SHV 7 (507760) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0002_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB #10610Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO NWTXARK7 (508072) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0003_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0004_P4 | a. Apply single-phase fault at WILKES 7 (508841) 345 kV Bus CB #1W10 Stuck b. 1. Run for 5 cycles, Trip branch from WILKES 7 (508841) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WILKES 7 (508841) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0005_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO PIRKEY 7 (508563) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0006_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 1N60 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0007_P4 | a. Apply single-phase fault on ONETA--7 (509807) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from ONETA--7 (509807) 345 kV Bus TO R.S.S.-7 (509782) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip ONETA--7 (509807) 345 kV Bus TO CLARKSV7 (509745) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0008_P4 | a. Apply single-phase fault at R.S.S.-7 (509782) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip R.S.S.-7 (509782) 345 kV Bus TO SAPLPRD7 (509870) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0009_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10280 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0010_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO 7SAREPTA% (337376) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0011_P4 | a. Apply single-phase fault at NEO SPA5 (505486) 161 kV Bus 16119 Stuck b. 1. Run for 5 cycles, Trip branch NEO SPA5 (505486) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 2. Run for 60 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 3. Run for 20 cycles, Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 4. Run for 3 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 5. Run for 37 cycles, Trip branch JOP389 5 (547483) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear Fault and run for 13 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 7. Drop Load 1 TIP292 5 (547472) 161 kV b. 8. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0012_P4 | a. Apply single-phase fault at ASB349 5 (547476) 161 kV Bus CB 16118 Stuck b. 1. Run for 5 cycles, Trip branch CAR395 5 (547485) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO PUR421 5 (547491) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 4. Clear fault and run for 15 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 6. Drop Load 1 Bus CAR395 5 (547485) 161 kV b. 7. Drop Load 1 Bus PUR421 5 (547491) 161 kV b. 8. Disconnect Bus CAR395 5 (547485) 161 kV b. 9. Disconnect Bus PUR421 5 (547491) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0013_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO NEOSHO 5 (532937) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch NEOSHO 5 (532937) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch HOC404 5 (547487) 161 kV Bus TO BAX488 5 (547729) 161 kV Bus CKT 1 b. 4. Clear fault after 86 cycles and Trip BAX488 5 (547729) 161 kV Bus TO HOC404 5 (547487) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0014_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 161120 Stuck b. 1. Run for 5 cycles, Trip branch ORO110 5 (547467) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 2. Run for 12 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 b. 3. Clear fault after 98 cycles and Trip branch STL439 5 (547498) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0015_P4 | a. Apply single-phase fault on TIP292 5 (547472) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch TIP292 5 (547472) 161 kV Bus TO JOP389 5 (547483) 161 kV Bus CKT 1 b. 2. Run for 60 cycles: b. 3. Trip branch TIP292 5 (547472) 161 kV Bus TO NEO SPA5 (505486) 161 kV Bus CKT 1 b. 4. Trip branch NEO SPA5 (505486) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 5. Run for 5 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear fault and run for 15 cycles: b. 7. Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 8. Drop Load 1 Bus TIP292 5 (547472) 161 kV b. 9. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0016_P4 | a. Apply single-phase fault on L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 1. Run for 5 cycles, Trip branch L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 2. Run for 12 cycles, Trip LAR382 5 ( 547479 ) 161 kV Bus TO MON383 5 ( 547480 ) 345 kV Bus CKT 1 b. 3. Clear fault and run for 95 cycles: b. 4. Trip branch MON383 5 ( 547480 ) 161 kV Bus TO LAR382 5 ( 547479 ) 345 kV Bus CKT 1 b. 5. Drop GENERATOR 1 BUS 547651 b. 6. Drop LOAD S1 BUS 547651 b. 7. Disconnect BUS 547651 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0018_P4 | a. Apply single-phase fault on LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 1. Run for 15 cycles, Trip branch LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 2. Clear fault after 15 cycles and Trip LEBROCK7 ( 508572 ) 161 kV Bus TO TENRUSK7 ( 508585 ) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0019_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Disconnect BUS 532791 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0020_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0021_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0022_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 13 cycles, Disconnect BUS 532831 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0023_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0024_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0025_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles: d. 2. Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 d. 3. Disconnect BUS 532962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0026_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543641 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0027_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543643 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0028_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0029_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0030_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0031_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542956 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0032_P4 | a. Apply single-phase fault on PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0033_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 3. Trip branch SWISVAL7 (532774) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0034_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 3. Trip branch STILWEL7 (542968) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0035_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Disconnect BUS 532831 c. Reclose the fault d. 1. Clear fault after 13 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0036_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69 kV Bus to TONECESTR2 (512756) 69 kV Bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69 kV Bus to ARKLIN2 (512728) 69 kV Bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69 kV Bus to SSNEWN2 (512747) 69 kV Bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69 kV Bus to SSNORT2 (512746) 69 kV Bus CKT 1 b. 5. Trip branch from SSNORT2 (512746) 69 kV Bus to SSLINC2 (512745) 69 kV Bus CKT 1 b. 6. Drop Load 1 at SSNORT2 (512746) 69 kV Bus b. 7. Drop Load 1 at SSLINC2 (512745) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0037_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT2-1 (506920) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0038_P1 | 3 phase fault on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD2 (505494) 69 kV Bus to 2ELWOOD (300669) 69 kV Bus CKT 1 b. 2. Trip branch from 2ELWOOD (300669) 69 kV Bus to 2ASHGRV (300657) 69 kV Bus CKT 1 b. 3. Drop Load 1 at 2ELWOOD (300669) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0039_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 5 (549956) 161 kV Bus to NICHOLS 2 (549925) 69 kV Bus to NICHOL XF1 1 (549940) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0040_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 5 (549956) 161 kV Bus to WEST BELT 5 (549957) 161 kV Bus CKT 1 b. 2. Trip branch from WEST BELT 5 (549957) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 b. 3. Drop Load W at WEST BELT 5 (549957) 161 kV Bus b. 4. Drop Load E at WEST BELT 5 (549957) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0041_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 1 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0042_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 2 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0043_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to GOLDEN 2 (549911) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0044_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to DAYTON 2 (549913) 69 kV Bus CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV Bus to FORT 2 (549914) 69 kV Bus CKT 1 b. 3. Trip branch from FORT 2 (549914) 69 kV Bus to SUNSET 2 (549907) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DAYTON 2 (549913) 69 kV Bus b. 5. Drop Load N at FORT 2 (549914) 69 kV Bus b. 6. Drop Load S at FORT 2 (549914) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0045_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to LAUREL 2 (549924) 69 kV Bus CKT 1 b. 2. Trip branch from LAUREL 2 (549924) 69 kV Bus to NICHOLS 2 (549925) 69 kV Bus CKT 1 b. 3. Drop Load N at LAUREL 2 (549924) 69 kV Bus b. 4. Drop Load S at LAUREL 2 (549924) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0046_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to COX 2 (549910) 69 kV Bus CKT 1 b. 2. Trip branch from COX 2 (549910) 69 kV Bus to PLAINVIEW 2 (549905) 69 kV Bus CKT 1 b. 3. Trip branch from PLAINVIEW 2 (549905) 69 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus CKT 1 b. 4. Drop Load N at COX 2 (549910) 69 kV Bus b. 5. Drop Load S at COX 2 (549910) 69 kV Bus b. 6. Drop Load E at PLAINVIEW 2 (549905) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0047_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to NIC170 2 (547542) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0048_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0049_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to FRISCO 2 (549926) 69 kV Bus CKT 1 b. 2. Trip branch from FRISCO 2 (549926) 69 kV Bus to N HWY13 2 (549927) 69 kV Bus CKT 1 b. 3. Trip branch from N HWY13 2 (549927) 69 kV Bus to NORTON 2 (549928) 69 kV Bus CKT 1 b. 4. Drop Load N at FRISCO 2 (549926) 69 kV Bus b. 5. Drop Load S at FRISCO 2 (549926) 69 kV Bus b. 6. Drop Load E at N HWY13 2 (549927) 69 kV Bus b. 7. Drop Load W at N HWY13 2 (549927) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0050_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to SED 80 2 (547529) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0051_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to NIX114 2 (547535) 69 kV Bus CKT 1 b. 2. Trip branch from NIX114 2 (547535) 69 kV Bus to BHJ415 2 (547604) 69 kV Bus CKT 1 b. 3. Drop Load 1 at NIX114 2 (547535) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0052_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to REP345 2 (547576) 69 kV Bus CKT 1 b. 2. Trip branch from REP345 2 (547576) 69 kV Bus to REP451 2 (547443) 69 kV Bus CKT 1 b. 3. Trip branch from REP451 2 (547443) 69 kV Bus to REP359 2 (547580) 69 kV Bus CKT 1 b. 4. Trip branch from REP359 2 (547580) 69 kV Bus to BIL221 2 (547546) 69 kV Bus CKT 1 b. 5. Drop Load 1 at REP345 2 (547576) 69 kV Bus b. 6. Drop Load 1 at REP451 2 (547443) 69 kV Bus b. 7. Drop Load 1 at REP359 2 (547580) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0053_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to SILSPWW5 (512642) 161 kV Bus CKT 1 b. 2. Trip branch from SILSPWW5 (512642) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 b. 3. Drop Load 1 at SILSPWW5 (512642) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0054_P1 | 3 phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161 kV Bus to WEDINGTON (506992) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0055_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to WEDINGTON5 (504275) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0056_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to FARMNGTN 5 (504020) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0058_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 7HUBEN (300042) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25S | Transfer | Group4_Fault_0059_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to GENTRY 5 (504201) 161 kV Bus CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV Bus to BEN279_5 (506960) 161 kV Bus CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV Bus to GREENHOUSE 5 (506990) 161 kV Bus CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 5. Drop Load A1 at GENTRY 5 (504201) 161 kV Bus b. 6. Drop Load 1 at BEN279_5 (506960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0061_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 5MORGANXF2 (301622) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25S | Transfer | Group4_Fault_0062_P1 | 3 phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGANXF2 (301622) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0063_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0064_P1 | 3 phase fault on EROGERS5 (506931) 161 kV Bus a. Apply Fault at the EROGERS5 (506931) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EROGERS5 (506931) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0065_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYESS1-1 (506914) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0066_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES2-1 (506915) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0067_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES3-1 (506916) 13.2 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0068_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to CARLEYRD 5 (504274) 161 kV Bus CKT 1 b. 2. Trip branch from CARLEYRD 5 (504274) 161 kV Bus to VANASCH5 (506939) 161 kV Bus CKT 1 b. 3. Trip branch from VANASCH5 (506939) 161 kV Bus to GREGGST5 (506983) 161 kV Bus CKT 1 b. 4. Trip branch from GREGGST5 (506983) 161 kV Bus to FAYETVL5 (506933) 161 kV Bus CKT 1 b. 5. Trip branch from FAYETVL5 (506933) 161 kV Bus to SFAYTVL5 (506947) 161 kV Bus CKT 1 b. 6. Drop Load A1 at CARLEYRD 5 (504274) 161 kV Bus b. 7. Drop Load 1 at VANASCH5 (506939) 161 kV Bus b. 8. Drop Load 1 at GREGGST5 (506983) 161 kV Bus b. 9. Drop Load 1 at FAYETVL5 (506933) 161 kV Bus b. 10. Drop Shunt 1 at VANASCH5 (506939) 161 kV Bus1 b. 11. Drop Shunt 1 at FAYETVL5 (506933) 161 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0069_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to SOSPRDL5 (506949) 161 kV Bus CKT 1 b. 2. Trip branch from SOSPRDL5 (506949) 161 kV Bus to OSBURN (506985) 161 kV Bus CKT 1 b. 3. Trip branch from OSBURN (506985) 161 kV Bus to EFAYETVL 5 (504015) 161 kV Bus CKT 1 b. 4. Drop Load 1 at SOSPRDL5 (506949) 161 kV Bus b. 5. Drop Load 1 at OSBURN (506985) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0070_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to DEC392 5 (547484) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0071_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to GROVE 5 (510411) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0072_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to NEO184 5 (547471) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0073_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NOL435 5 (547496) 161 kV Bus to NOL435 2 (547610) 69 kV Bus to NOL435 1 (547720) 12.5 kV Bus CKT 1 b. 2. Drop Shunt 1 at NOL435 1 (547720) 12.5 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0074_P1 | 3 phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply Fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161 kV Bus to 5CHOTEAU2 (301348) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0075_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR1 (512814) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0076_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR2 (512815) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0077_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLARMR 5 (512651) 161 kV Bus to 5KETONVL (300997) 161 kV Bus CKT 1 b. 2. Trip branch from 5KETONVL (300997) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5KETONVL (300997) 161 kV Bus b. 4. Drop Load 1 at 5KETONVL (300997) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0078_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR 5 (512700) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0079_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WAGNOR 5 (512700) 161 kV Bus to WAGNOR 2 (512697) 69 kV Bus to WAGNOR1 (512818) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0080_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to STOCKTN5 (505498) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0081_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to TONTITN5 (506957) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0082_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to DAD368 5 (547478) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0083_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to 2MORGAN (300782) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0084_P1 | 3 phase fault on SSSWTP2 (512737) 69 kV Bus a. Apply Fault at the SSSWTP2 (512737) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SSMOSS2 (512744) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0085_P1 | 3 phase fault on 5CHOTEAU2 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 (301348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU2 (301348) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0086_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 b. 2. Drop Load 1 at DRYGULCH5 (512629) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0087_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0088_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to 412SUB 5 (512637) 161 kV Bus CKT 1 b. 2. Trip branch from 412SUB 5 (512637) 161 kV Bus to KANSATP5 (512714) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 412SUB 5 (512637) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0089_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK1 5 (512770) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0090_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK4 5 (512771) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0091_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0092_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAMSP 5 (504202) 161 kV Bus CKT 1 b. 2. Trip branch from SILOAMSP 5 (504202) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 b. 3. Drop Load A1 at SILOAMSP 5 (504202) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0093_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0094_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER1 1 (512833) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0095_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER2 1 (512834) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0096_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161 kV Bus to 5ELMCRK (300993) 161 kV Bus CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5ELMCRK (300993) 161 kV Bus b. 4. Drop Load 2 at 5ELMCRK (300993) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0097_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIXA 5 (505496) 161 kV Bus to TABLE R5 (505472) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0098_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X2 1 (505499) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0099_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X1 1 (505497) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0100_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to CARTHAG5 (505488) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0101_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to MON383 5 (547480) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0102_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MILL 5 (549962) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0103_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0104_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MENTOR 5 (549963) 161 kV Bus CKT 1 b. 2. Trip branch from MENTOR 5 (549963) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 b. 3. Drop Load S at MENTOR 5 (549963) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0105_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to 5LOGAN (301161) 161 kV Bus CKT 1 b. 2. Trip branch from 5LOGAN (301161) 161 kV Bus to 5MANSFDMN (300095) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5LOGAN (301161) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0106_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus to JRPS XF2 1 (549945) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0107_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JAMES RIVER2 (549904) 69 kV Bus to JRPS XF1 1 (549944) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0108_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF1 1 (549936) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0109_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF2 1 (549938) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0110_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to MC CARTNEY 5 (549968) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0111_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to NORTON 5 (549967) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0112_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to KANSAS 5 (512716) 161 kV Bus CKT 1 b. 2. Trip three winding transformer from KANSAS 5 (512716) 161 kV Bus to KANSAS 2 (512715) 69 kV Bus to KANSAS1 (512736) 13.8 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0113_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2KANSASTP (301637) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0114_P1 | 3 phase fault on SHIPERD5 (506980) 161 kV Bus a. Apply Fault at the SHIPERD5 (506980) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHIPERD5 (506980) 161 kV Bus to CENTRTN5 (506952) 161 kV Bus CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 3. Drop Load 1 at CENTRTN5 (506952) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0115_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2WATTS (300987) 69 kV Bus CKT 1 b. 2. Trip branch from 2WATTS (300987) 69 kV Bus to 2WESTVIL (300988) 69 kV Bus CKT 1 b. 3. Trip branch from 2WESTVIL (300988) 69 kV Bus to 2BALDOR (300980) 69 kV Bus CKT 1 b. 4. Trip branch from 2BALDOR (300980) 69 kV Bus to STLWLGR2 (512721) 69 kV Bus CKT 1 b. 5. Drop Load 1 at 2WATTS (300987) 69 kV Bus b. 6. Drop Load 1 at 2WESTVIL (300988) 69 kV Bus b. 7. Drop Load 2 at 2WESTVIL (300988) 69 kV Bus b. 8. Drop Load 1 at 2BALDOR (300980) 69 kV Bus b. 9. Drop Shunt 1 at 2WESTVIL (300988) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0116_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2KANSASKM (301638) 69 kV Bus CKT 1 b. 2. Drop Load 2 at 2KANSASKM (301638) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0117_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2COLCOTP (301458) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0118_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0119_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY1 1 (512849) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0120_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE5 (512751) 161 kV Bus to TONNEC2 (512753) 69 kV Bus to TONNEC1 (512754) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0121_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY2 1 (512850) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0122_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA1 (512821) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRDA1 (512821) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0123_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA2 1 (512826) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRDA2 1 (512826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0124_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0125_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to GREC TAP5 (512865) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0126_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF1 1 (549988) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0127_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF2 1 (549989) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0128_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 7 (549984) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0129_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 5 (506948) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0130_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILOAM 5 (506948) 161 kV Bus to SILOAM 2 (506973) 69 kV Bus to SILOAM-1 (506917) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0131_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0132_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONTITN7 (506959) 345 kV Bus to TONTITN5 (506957) 161 kV Bus to TONTITN1 (506958) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0133_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0134_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEC392 5 (547484) 161 kV Bus to DEC392 2 (547594) 69 kV Bus to DEC392 1 (547714) 12.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0135_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 5 (547484) 161 kV Bus to NOL435 5 (547496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0136_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWES2 (512730) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0137_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWTP2 (512737) 69 kV Bus CKT 1 b. 2. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0138_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0139_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0140_P1 | 3 phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC TAP5 (512865) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0141_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE7 (512750) 345 kV Bus to TONECE5 (512751) 161 kV Bus to TONECE1 (512752) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_0142_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0143_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to CLARMR 5 (512651) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0144_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WAGNOR 5 (512700) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0145_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WMAIN ST5 (512742) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0146_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 5 (512656) 161 kV Bus to GRDA1 2 (512727) 69 kV Bus to GRDA1 1 (512816) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0147_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0148_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to SPRGFLD5 (505492) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0149_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JTEC 5 (549954) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0150_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JUNCTION 5 (549955) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0151_P1 | 3 phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply Fault at the SILOAM 2 (506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 2 (506973) 69 kV Bus to LINCOLN2 (506972) 69 kV Bus CKT 1 b. 2. Trip branch from LINCOLN2 (506972) 69 kV Bus to PRGROVE2 (506941) 69 kV Bus CKT 1 b. 3. Trip branch from PRGROVE2 (506941) 69 kV Bus to GREENLD2 (506936) 69 kV Bus CKT 1 b. 4. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 b. 5. Drop Load A1 at LINCOLN2 (506972) 69 kV Bus b. 6. Drop Load 1 at PRGROVE2 (506941) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0152_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to GRDA1 7 (512650) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0153_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to ELMSPRGS 5 (504010) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0154_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to BRUSHCRK_5 (506991) 161 kV Bus CKT 1 b. 2. Trip branch from BRUSHCRK_5 (506991) 161 kV Bus to LOWELL 5 (506938) 161 kV Bus CKT 1 b. 3. Trip branch from LOWELL 5 (506938) 161 kV Bus to ROGERS 5 (506942) 161 kV Bus CKT 1 b. 4. Trip branch from ROGERS 5 (506942) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 5. Drop Load 1 at BRUSHCRK_5 (506991) 161 kV Bus b. 6. Drop Load 1 at LOWELL 5 (506938) 161 kV Bus b. 7. Drop Load 1 at ROGERS 5 (506942) 161 kV Bus b. 8. Drop Shunt 1 at ROGERS 5 (506942) 161 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0155_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELMSPRGS 5 (504010) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0156_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_1 2 (504011) 69 kV Bus to ELMSP_T1 1 (504012) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ELMSPG_1 2 (504011) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0157_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_2 2 (504013) 69 kV Bus to ELMSP_T2 1 (504014) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0158_P1 | 3 phase fault on TONTITN7 (506959) 345 kV Bus a. Apply Fault at the TONTITN7 (506959) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN7 (506959) 345 kV Bus to CHAMSPR7 (506945) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0159_P1 | 3 phase fault on DEC392 2 (547594) 69 kV Bus a. Apply Fault at the DEC392 2 (547594) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 2 (547594) 69 kV Bus to DEC467 2 (547569) 69 kV Bus CKT 1 b. 2. Trip branch from DEC467 2 (547569) 69 kV Bus to GRA700 2 (547617) 69 kV Bus CKT 1 b. 3. Trip branch from GRA700 2 (547617) 69 kV Bus to NOL435 2 (547610) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DEC467 2 (547569) 69 kV Bus b. 5. Drop Load 1 at GRA700 2 (547617) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0160_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_1 2 (504006) 69 kV Bus to ECENT_T1 1 (504007) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ECENT_1 2 (504006) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0161_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_2 2 (504008) 69 kV Bus to ECENT_T2 1 (504009) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0162_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR2-1 (506924) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0163_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to FLINTCR7 (506935) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0164_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR1-1 (506923) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0165_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV Bus to BENT_SL5 (506963) 161 kV Bus CKT 1 b. 2. Trip branch from BENT_SL5 (506963) 161 kV Bus to BENTVJ_5 (506962) 161 kV Bus CKT 1 b. 3. Trip branch from BENTVJ_5 (506962) 161 kV Bus to BENT ML5 (506955) 161 kV Bus CKT 1 b. 4. Trip branch from BENT ML5 (506955) 161 kV Bus to WROGERS 5 (504200) 161 kV Bus CKT 1 b. 5. Trip branch from WROGERS 5 (504200) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 6. Drop Load 1 at BENT_SL5 (506963) 161 kV Bus b. 7. Drop Load 1 at BENTVJ_5 (506962) 161 kV Bus b. 8. Drop Load 1 at BENT ML5 (506955) 161 kV Bus b. 9. Drop Load A1 at WROGERS 5 (504200) 161 kV Bus b. 10. Drop Load A2 at WROGERS 5 (504200) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0166_P1 | 3 phase fault on ECNTRTN2 (506928) 69 kV Bus a. Apply Fault at the ECNTRTN2 (506928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN2 (506928) 69 kV Bus to BENTNVL2 (506965) 69 kV Bus CKT 1 b. 2. Trip branch from BENTNVL2 (506965) 69 kV Bus to DIXLAND2 (506925) 69 kV Bus CKT 1 b. 3. Trip branch from DIXLAND2 (506925) 69 kV Bus to NROGERS2 (506940) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BENTNVL2 (506965) 69 kV Bus b. 5. Drop Load 1 at DIXLAND2 (506925) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0167_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV1 5 (513593) 161 kV Bus to IGLOTER1 1 (513592) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0168_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV2 5 (513595) 161 kV Bus to IGLOTER2 1 (513594) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0169_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0170_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0171_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0172_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0173_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to BROOKLINE 7 (549984) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0174_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0175_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0176_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to LOCSTGVKM 5 (513050) 161 kV Bus CKT 1 b. 2. Trip branch from LOCSTGVKM 5 (513050) 161 kV Bus to 5CDRCRST (301344) 161 kV Bus CKT 1 b. 3. Drop Load 1 at LOCSTGVKM 5 (513050) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0177_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER1 1 (512836) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0178_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER2 1 (512837) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0179_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0180_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to GERALDGAY5 (512760) 161 kV Bus CKT 1 b. 2. Trip branch from GERALDGAY5 (512760) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 b. 3. Drop Load 1 at GERALDGAY5 (512760) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0181_P1 | 3 phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply Fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WMAIN ST5 (512742) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0182_P1 | 3 phase fault on GRDA1 2 (512727) 69 kV Bus a. Apply Fault at the GRDA1 2 (512727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 2 (512727) 69 kV Bus to MAIDTP2 (512625) 69 kV Bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0183_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to NIXA 5 (505496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0184_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to SHIPERD7 (506979) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0185_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0186_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to CLAY 5 (549970) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0187_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to 5NIXA-1 (300678) 161 kV Bus CKT 1 b. 2. Trip branch from 5NIXA-1 (300678) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5NIXA-1 (300678) 161 kV Bus b. 4. Drop Load 2 at 5NIXA-1 (300678) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0188_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X1 1 (505491) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0189_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X2 1 (505493) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0190_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X3 1 (505495) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0191_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to LAR382 5 (547479) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0192_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0193_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to 5BTLFD (300348) 161 kV Bus CKT 1 b. 2. Trip branch from 5BTLFD (300348) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5BTLFD (300348) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0194_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to SW DISP PLT5 (549960) 161 kV Bus CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 b. 3. Drop Load W at SW DISP PLT5 (549960) 161 kV Bus b. 4. Drop Load E at SW DISP PLT5 (549960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0195_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT1-1 (506921) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0196_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to NICHOLS 5 (549956) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0197_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to PIC WEST 5 (549971) 161 kV Bus CKT 1 b. 2. Trip branch from PIC WEST 5 (549971) 161 kV Bus to SUMMIT 5 (549966) 161 kV Bus CKT 1 b. 3. Drop Load S at PIC WEST 5 (549971) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0198_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAMSPR7 (506945) 345 kV Bus to CHAMSPR5 (506944) 161 kV Bus to CHAMSPR1 (506919) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0199_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0200_P1 | 3 phase fault on IGLOOV1 5 (513593) 161 kV Bus a. Apply Fault at the IGLOOV1 5 (513593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV1 5 (513593) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0201_P1 | 3 phase fault on IGLOOV2 5 (513595) 161 kV Bus a. Apply Fault at the IGLOOV2 5 (513595) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV2 5 (513595) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0202_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to REDDEN 2 (512698) 69 kV Bus CKT 1 b. 2. Trip branch from REDDEN 2 (512698) 69 kV Bus to CASTING TAP2 (512685) 69 kV Bus CKT 1 b. 3. Trip branch from CASTING TAP2 (512685) 69 kV Bus to AMERCAST N2 (512683) 69 kV Bus CKT 1 b. 4. Drop Load 1 at REDDEN 2 (512698) 69 kV Bus b. 5. Drop Load 1 at AMERCAST N2 (512683) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0203_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to AMERCAST S2 (512681) 69 kV Bus CKT 1 b. 2. Trip branch from AMERCAST S2 (512681) 69 kV Bus to CPPTAP 2 (512661) 69 kV Bus CKT 1 b. 3. Trip branch from CPPTAP 2 (512661) 69 kV Bus to PRYORCHEM2 (512699) 69 kV Bus CKT 1 b. 4. Trip branch from PRYORCHEM2 (512699) 69 kV Bus to AIRPROD2 (512687) 69 kV Bus CKT 1 b. 5. Trip branch from AIRPROD2 (512687) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 b. 6. Drop Load 1 at AMERCAST S2 (512681) 69 kV Bus b. 7. Drop Load 1 at PRYORCHEM2 (512699) 69 kV Bus b. 8. Drop Load 1 at AIRPROD2 (512687) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0204_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD5 (549959) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0205_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BATTLEFIELD5 (549959) 161 kV Bus to BATTLEFIELD2 (549979) 69 kV Bus to BATLEFLDXF11 (549980) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0206_P4 | a. Apply single phase fault at FLINTCR7 (506935) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR7 (506935) 345 kV to TONECE7 (512750) 345 kV CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345 kV to SHIPERD7 (506979) 345 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from SHIPERD5 (506980) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 5. Trip branch from CENTRTN5 (506952) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 6. Drop Load 1 CENTRTN5 (506952) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0207_P4 | a. Apply single phase fault at SILMCTY5 (512643) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SILMCTY5 (512643) 161 kV to SILOAM 5 (506948) 161 kV CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161 kV to SILSPWW5 (512642) 161 kV CKT 1 b. 3. Trip branch from SILSPWW5 (512642) 161 kV to KANSATP5 (512714) 161 kV CKT 1 b. 4. Drop Load 1 SILSPWW5 (512642) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0208_P4 | a. Apply single phase fault at FLINTCR5 (506934) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR5 (506934) 161 kV to GENTRY 5 (504201) 161 kV CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV to BEN279_5 (506960) 161 kV CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV to GREENHOUSE 5 (506990) 161 kV CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 5. Trip branch from FLINTCR5 (506934) 161 kV to TONTITN5 (506957) 161 kV CKT 1 b. 6. Drop Load A1 GENTRY 5 (504201) 161 kV b. 7. Drop Load 1 BEN279_5 (506960) 161 kV b. 8. Drop Load 1 GREENHOUSE 5 (506990) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0210_P4 | a. Apply single phase fault at BROOKLINE 5 (549969) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV CKT 1 b. 2. Trip branch from BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0211_P4 | a. Apply single phase fault at TAHLQH 5 (512655) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TAHLQH 5 (512655) 161 kV to 5CDRCRST (301344) 161 kV CKT 1 b. 2. Trip branch from TAHLQH 5 (512655) 161 kV to 7CLANS 5 (515956) 161 kV CKT 1 b. 3. Trip branch from 7CLANS 5 (515956) 161 kV to KETOWAH5 (516027) 161 kV CKT 1 b. 4. Trip branch from KETOWAH5 (516027) 161 kV to MUSKOGE5 (515222) 161 kV CKT 1 b. 5. Drop Load 1 SILSPWW5 (512642) 161 kV b. 6. Drop Load 1 7CLANS 5 (515956) 161 kV b. 7. Drop Load 1 KETOWAH5 (516027) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0212_P4 | a. Apply single phase fault at CHAMSPR5 (506944) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CHAMSPR5 (506944) 161 kV to CHAMSPR7 (506945) kV to CHAMSPR1 (506919) 13.8 kV CKT1 b. 2. Trip branch from CHAMSPR5 (506944) 161 kV to TONTITN5 (506957) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0213_P4 | a. Apply single phase fault at ECNTRTN5 (506929) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV to SHIPERD5 (506980) 161 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from ECNTRTN5 (506929) 161 kV to BENT_SL5 (506963) 161 kV CKT 1 b. 5. Trip branch from BENT_SL5 (506963) 161 kV to BENTVJ_5 (506962) 161 kV CKT 1 b. 6. Trip branch from BENTVJ_5 (506962) 161 kV to BENT ML5 (506955) 161 kV CKT 1 b. 7. Trip branch from BENT ML5 (506955) 161 kV to WROGERS 5 (504200) 161 kV CKT 1 b. 8. Trip branch from WROGERS 5 (504200) 161 kV to EROGERS5 (506931) 161 kV CKT 1 b. 9. Drop Load 1 CENTRTN5 (506952) 161 kV b. 10. Drop Load 1 BENT_SL5 (506963) 161 kV b. 11. Drop Load 1 BENTVJ_5 (506962) 161 kV b. 12. Drop Load 1 BENT ML5 (506955) 161 kV b. 13. Drop Load A1 WROGERS 5 (504200) 161 kV b. 14. Drop Load A2 WROGERS 5 (504200) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0214_P4 | a. Apply single phase fault at STLWLGR2 (512721) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from STLWLGR2 (512721) 69 kV to STIWEL5 (512704) kV to STLWELL1 (512819) 13.8 kV CKT1 b. 2. Trip branch from STIWEL5 (512704) 161 kV to BRIGSKM 5 (513044) 161 kV CKT 1 b. 3. Trip branch from STLWLGR2 (512721) 69 kV to STILWELLCTY2 (512701) 69 kV CKT 1 b. 4. Drop Load 1 STILWELLCTY2 (512701) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0215_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to SOONER 7 (514803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0216_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MILLERT4 (514704) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0217_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to LBRTYLK4 (515373) 138 kV Bus CKT 1 b. 2. Trip branch from LBRTYLK4 (515373) 138 kV Bus to WATRLOO4 (514831) 138 kV Bus CKT 1 b. 3. Trip branch from WATRLOO4 (514831) 138 kV Bus to WHITESB4 (515467) 138 kV Bus CKT 1 b. 4. Trip branch from WHITESB4 (515467) 138 kV Bus to MITCHSB4 (515466) 138 kV Bus CKT 1 b. 5. Trip branch from MITCHSB4 (515466) 138 kV Bus to KETCHTP4 (514828) 138 kV Bus CKT 1 b. 6. Drop Load 1 at LBRTYLK4 (515373) 138 kV Bus b. 7. Drop Load 1 at WATRLOO4 (514831) 138 kV Bus b. 8. Drop Load 1 at WHITESB4 (515467) 138 kV Bus b. 9. Drop Load 1 at MITCHSB4 (515466) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0218_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to NORTWST4 (514879) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0219_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to KETCH 4 (514834) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0220_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0221_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to FAIRFLD4 (515468) 138 kV Bus CKT 1 b. 2. Trip branch from FAIRFLD4 (515468) 138 kV Bus to CHISHOM4 (515374) 138 kV Bus CKT 1 b. 3. Trip branch from CHISHOM4 (515374) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FAIRFLD4 (515468) 138 kV Bus b. 5. Drop Load 1 at CHISHOM4 (515374) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0222_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to PERRY 4 (514707) 138 kV Bus CKT 1 b. 2. Trip branch from PERRY 4 (514707) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0223_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to SNRPMPT4 (514798) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0224_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MORISNT4 (515447) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0225_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345 kV Bus to SAPLPRD7 (509870) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0226_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV Bus to WEKIWA-4 (509757) 138 kV Bus to WEKIW1-1 (509879) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0227_P1 | 3 phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PINTAIL7 (516010) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0228_P1 | 3 phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply Fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-119-TAP (587804) 345 kV Bus to SPRNGCK7 (514881) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0229_P1 | 3 phase fault on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345 kV Bus to ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0230_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to OPENSKY7 (515621) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0231_P1 | 3 phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEVLND7 (512694) 345 kV Bus to CLEVLND 4 (512729) 138 kV Bus to CLEVLND1 (512817) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0232_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to DMNCRKT4 (515412) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0233_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to OTOETAP4 (515978) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0234_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to OSAGE 4 (514743) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0235_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to SNRPMP 4 (514799) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SNRPMP 4 (514799) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0236_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to STILWTR4 (515011) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0237_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to MORRISN4 (515006) 138 kV Bus CKT 1 b. 2. Trip branch from MORRISN4 (515006) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0238_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SHEFFD-4 (509812) 138 kV Bus CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV Bus to S.S.---4 (509815) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHEFFD-4 (509812) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0239_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to WED-TAP4 (509823) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0240_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to P&P WTP4 (509851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0241_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0242_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SILVCTYGR4 (512726) 138 kV Bus CKT 1 b. 2. Trip branch from SILVCTYGR4 (512726) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0243_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to KEYSTON4 (505610) 138 kV Bus CKT 1 b. 2. Trip branch from KEYSTON4 (505610) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0244_P1 | 3 phase fault on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND 4 (512729) 138 kV Bus to 4CLEVLND (300138) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0245_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to PAWNSW4 (512749) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0246_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0247_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4JAVINE (300996) 138 kV Bus CKT 1 b. 2. Trip branch from 4JAVINE (300996) 138 kV Bus to 4SFORKKTP (301339) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0248_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0249_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0250_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD7 (509870) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0251_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SAPLPRD7 (509870) 345 kV Bus to SAPLPRD4 (509871) 138 kV Bus to SAPLPRD1 (509872) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0252_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G15-066T (560056) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0254_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to HUNTERS7 (515476) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0255_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0256_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV Bus to WOODRNG4 (514714) 138 kV Bus to WOODRNG1 (515770) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0257_P1 | 3 phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPRNGCK7 (514881) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0258_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0259_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0260_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0261_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH1 1 (532826) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH1 1 (532826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0262_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH5 1 (532827) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH5 1 (532827) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0263_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to PINTAIL7 (516010) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0264_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH3 1 (532831) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH3 1 (532831) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0265_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0266_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to DMANCRK4 (515400) 138 kV Bus CKT 1 b. 2. Drop Load 1 at DMANCRK4 (515400) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0267_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to 4REDRCK (301011) 138 kV Bus CKT 1 b. 2. Drop Load 1 at 4REDRCK (301011) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0268_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to OTOE 4 (514737) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OTOE 4 (514737) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0269_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COWCRK 4 (514706) 138 kV Bus to WRVALLY4 (514713) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0270_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COWCRK 4 (514706) 138 kV Bus to COWCRK 2 (514705) 69 kV Bus to COWCRK 1 (515717) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0271_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0272_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WEBBTAP4 (510376) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0273_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to MARLNDT4 (514770) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0274_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G16-119-TAP (587804) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0275_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 31 (515744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0276_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 41 (515745) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0277_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to STDBEAR4 (514758) 138 kV Bus CKT 1 b. 2. Trip branch from STDBEAR4 (514758) 138 kV Bus to CONORTH4 (514753) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0278_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to SPGVLLY4 (515574) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0279_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to MCELROY4 (515009) 138 kV Bus CKT 1 b. 2. Trip branch from MCELROY4 (515009) 138 kV Bus to UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 3. Trip branch from UNVRSTY4 (515181) 138 kV Bus to KINZE 4 (515008) 138 kV Bus CKT 1 b. 4. Drop Load 1 at MCELROY4 (515009) 138 kV Bus b. 5. Drop Load 1 at UNVRSTY4 (515181) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0280_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to PP----W4 (509805) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0281_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0282_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0283_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4BRISTOW (300137) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0284_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0285_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SOONER 7 (514803) 345 kV Bus to SOONER 4 (514802) 138 kV Bus to SOONER 1 (515760) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0286_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0287_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0288_P1 | 3 phase fault on 2CLEVLND (300927) 69 kV Bus a. Apply Fault at the 2CLEVLND (300927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CLEVLND (300927) 69 kV Bus to OSAGEK2 (512876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0289_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to 4FAIRFAX (300139) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0290_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to GLENCOKM 4 (513095) 138 kV Bus CKT 1 b. 2. Trip branch from GLENCOKM 4 (513095) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLENCOKM 4 (513095) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0291_P1 | 3 phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply Fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0292_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0293_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0294_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to OAKSWTP4 (509848) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0295_P1 | 3 phase fault on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345 kV Bus to G15-052T (560053) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0296_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to 72ELWOD4 (509888) 138 kV Bus CKT 1 b. 2. Trip branch from 72ELWOD4 (509888) 138 kV Bus to T.P.S.-4 (509788) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 72ELWOD4 (509888) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0297_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to JENKS--4 (509759) 138 kV Bus CKT 1 b. 2. Trip branch from JENKS--4 (509759) 138 kV Bus to 116JENK4 (509753) 138 kV Bus CKT 1 b. 3. Trip branch from 116JENK4 (509753) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 b. 4. Drop Load 1 at JENKS--4 (509759) 138 kV Bus b. 5. Drop Load 1 at 116JENK4 (509753) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0298_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to OTTER 4 (514708) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0299_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to FRMNTAP4 (514709) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0300_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to WAUKOTP4 (514711) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0301_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to MARSHL 4 (514733) 138 kV Bus CKT 1 b. 2. Trip branch from MARSHL 4 (514733) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 3. Trip branch from MARSHL 4 (514733) 138 kV Bus to MARSHAL4 (521006) 138 kV Bus CKT Z1 b. 4. Drop Load 1 at MARSHAL4 (521006) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0302_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0303_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0304_P1 | 3 phase fault on G15-066T (560056) 345 kV Bus a. Apply Fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0305_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to KINZEGR4 (512710) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0306_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to FITZGRD4 (514830) 138 kV Bus CKT 1 b. 2. Trip branch from FITZGRD4 (514830) 138 kV Bus to PINE ST4 (514829) 138 kV Bus CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FITZGRD4 (514830) 138 kV Bus b. 5. Drop Load 1 at PINE ST4 (514829) 138 kV Bus b. 6. Drop Load 2 at PINE ST4 (514829) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0307_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to NORTHTP4 (512731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0308_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to 19TH ST4 (512712) 138 kV Bus CKT 1 b. 2. Trip branch from 19TH ST4 (512712) 138 kV Bus to 4RAMSEY (300844) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 19TH ST4 (512712) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0309_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to KINZEGR2 (512713) 69 kV Bus CKT 1 b. 2. Trip branch from KINZEGR2 (512713) 69 kV Bus to ADMIRAL2 (512660) 69 kV Bus CKT 1 b. 3. Drop Shunt 1 at KINZEGR2 (512713) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0310_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to ARCADIA4 (514907) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0311_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to CRESENT4 (515377) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0312_P4 | a. Apply single phase fault at SOONER 4 (514802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SOONER 4 (514802) 138 kV to MORISNT4 (515447) 138 kV CKT 1 b. 2. Trip branch from SOONER 4 (514802) 138 kV to SNRPMPT4 (514798) 138 kV CKT 1 b. 3. Trip branch from SNRPMPT4 (514798) 138 kV to SNRPMP 4 (514799) 138 kV CKT 1 b. 4. Drop Load 1 SNRPMP 4 (514799) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0313_P4 | a. Apply single phase fault at T.NO.--4 (509817) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from T.NO.--4 (509817) 138 kV to T.NO.2-4 (509895) 138 kV CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138 kV to CDC-WT 4 (509842) 138 kV CKT 1 b. 3. Trip branch from CDC-WT 4 (509842) 138 kV to A.A.---4 (509784) 138 kV CKT 1 b. 4. Trip branch from CDC-WT 4 (509842) 138 kV to WHIRLPO4 (509840) 138 kV CKT 1 b. 5. Drop Load 1 WHIRLPO4 (509840) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0314_P4 | a. Apply single phase fault at MEMRIAL4 (514835) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MEMRIAL4 (514835) 138 kV to TENESTP4 (514837) 138 kV CKT 1 b. 2. Trip branch from MEMRIAL4 (514835) 138 kV to BRYANT 4 (514839) 138 kV CKT 1 b. 3. Trip branch from BRYANT 4 (514839) 138 kV to ACORN 4 (515459) 138 kV CKT 1 b. 4. Trip branch from ACORN 4 (515459) 138 kV to JONESSB4 (515480) 138 kV CKT 1 b. 5. Drop Load 1 BRYANT 4 (514839) 138 kV b. 6. Drop Load 1 ACORN 4 (515459) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0315_P4 | a. Apply single phase fault at S.S.---4 (509815) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S.S.---4 (509815) 138 kV to SHEFFD-4 (509812) 138 kV CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 b. 3. Trip branch from S.S.---4 (509815) 138 kV to PRATTV-4 (509758) 138 kV CKT 1 b. 4. Trip branch from PRATTV-4 (509758) 138 kV to BLUEBEL4 (515242) 138 kV CKT 1 b. 5. Drop Load 1 PRATTV-4 (509758) 138 kV b. 6. Drop Load 1 SHEFFD-4 (509812) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0316_P4 | a. Apply single phase fault at R.S.S.-4 (509783) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from R.S.S.-4 (509783) 138 kV to ORU ETP4 (509849) 138 kV CKT 1 b. 2. Trip branch from ORU ETP4 (509849) 138 kV to WARNTAP4 (509858) 138 kV CKT 1 b. 3. Trip branch from ORU ETP4 (509849) 138 kV to ORU E4 (509738) 138 kV CKT 1 b. 4. Trip branch from R.S.S.-4 (509783) 138 kV to ORU-WTP4 (509853) 138 kV CKT 1 b. 5. Trip branch from ORU-WTP4 (509853) 138 kV to SHILETP4 (509813) 138 kV CKT 1 b. 6. Trip branch from ORU-WTP4 (509853) 138 kV to ORU W4 (509732) 138 kV CKT 1 b. 7. Drop Load 1 ORU W4 (509732) 138 kV b. 8. Drop Shunt 1 ORU W4 (509732) 138 kV b. 9. Drop Load 1 ORU E4 (509738) 138 kV b. 10. Drop Shunt 1 ORU E4 (509738) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0317_P4 | a. Apply single phase fault at DVISION4 (514853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DVISION4 (514853) 138 kV to LAKESID4 (514849) 138 kV CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV to HEFNER 4 (514848) 138 kV CKT 1 b. 3. Trip branch from DVISION4 (514853) 138 kV to SLVRLAK4 (514852) 138 kV CKT 1 b. 4. Drop Load 1 LAKESID4 (514849) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0318_P4 | a. Apply single phase fault at T.NO.--7 (509852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV to T.NO.2-4 (509895) kV to TNO2-1 (509894) 34.5 kV CKT1 b. 2. Trip branch from T.NO.2-4 (509895) 138 kV to T.NO.--4 (509817) 138 kV CKT 1 b. 3. Trip branch from T.NO.--7 (509852) 345 kV to N.E.S.-7 (510406) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0319_P4 | a. Apply single phase fault at WEKIWA-4 (509757) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV to WEKIWA-4 (509757) kV to WEKIW1-1 (509879) 34.5 kV CKT1 b. 2. Trip branch from WEKIWA-4 (509757) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to 4SILVCTY (300140) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0320_P4 | a. Apply single phase fault at WOODRNG7 (514715) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) kV to WOODRNG1 (515770) 13.8 kV CKT1 b. 2. Trip branch from WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0321_P4 | a. Apply single phase fault at 4CLEVLND (300138) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4CLEVLND (300138) 138 kV to CLEVLND 4 (512729) 138 kV CKT Z1 b. 2. Trip three winding transformer from CLEVLND7 (512694) 345 kV to CLEVLND 4 (512729) kV to CLEVLND1 (512817) 13.8 kV CKT1 b. 3. Trip branch from 4CLEVLND (300138) 138 kV to PAWNSW4 (512749) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0322_P4 | a. Apply single phase fault at CTNWOOD4 (514827) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV to ARCADIA4 (514907) 138 kV CKT 1 b. 2. Trip branch from CTNWOOD4 (514827) 138 kV to PINE ST4 (514829) 138 kV CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV to FITZGRD4 (514830) 138 kV CKT 1 b. 4. Trip branch from FITZGRD4 (514830) 138 kV to KINZE 4 (515008) 138 kV CKT 1 b. 5. Drop Load 1 PINE ST4 (514829) 138 kV b. 6. Drop Load 2 PINE ST4 (514829) 138 kV b. 7. Drop Load 1 FITZGRD4 (514830) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0324_P4 | a. Apply single phase fault at SAPLPRD4 (509871) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SAPLPRD4 (509871) 138 kV to SAPLPRD7 (509870) kV to SAPLPRD1 (509872) 13.8 kV CKT1 b. 2. Trip branch from SAPLPRD4 (509871) 138 kV to OAKSWTP4 (509848) 138 kV CKT 1 b. 3. Trip branch from OAKSWTP4 (509848) 138 kV to OAKS W4 (509727) 138 kV CKT 1 b. 4. Trip branch from OAKSWTP4 (509848) 138 kV to T.P.S.-4 (509788) 138 kV CKT 1 b. 5. Drop Load 1 OAKS W4 (509727) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0325_P4 | a. Apply single phase fault at ARCADIA4 (514907) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA4 (514907) 138 kV to RNDBARN4 (515461) 138 kV CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV to BURGETT4 (514510) 138 kV CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV to DANFRTH4 (514833) 138 kV CKT 1 b. 4. Trip three winding transformer from ARCADIA4 (514907) 138 kV to ARCADIA7 (514908) kV to ARCADI41 (515700) 13.8 kV CKT1 b. 5. Drop Load 1 BURGETT4 (514510) 138 kV b. 6. Drop Load 1 RNDBARN4 (515461) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0326_P4 | a. Apply single phase fault at BV-SE--4 (510391) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BV-SE--4 (510391) 138 kV to RICE CK4 (510385) 138 kV CKT 1 b. 2. Trip branch from RICE CK4 (510385) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 3. Trip branch from BV-SE--4 (510391) 138 kV to BV-COM-4 (510390) 138 kV CKT 1 b. 4. Drop Load M1 RICE CK4 (510385) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0328_P4 | a. Apply single phase fault at NEOSHO 7 (532793) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV to G17-209-TAP (760921) 345 kV CKT 1 b. 2. Trip three winding transformer from NEOSHO 7 (532793) 345 kV to NEOSHO 5 (532937) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0329_P4 | a. Apply single phase fault at N.E.S.-4 (510396) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N.E.S.-4 (510396) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 2. Trip branch from OOLOGAHKM 4 (513124) 138 kV to CLARMR 4 (512707) 138 kV CKT 1 b. 3. Trip three winding transformer from CLARMR 4 (512707) 138 kV to CLARMR 5 (512651) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 4. Trip branch from N.E.S.-4 (510396) 138 kV to OWASO2_4 (509843) 138 kV CKT 1 b. 5. Trip branch from OWASO2_4 (509843) 138 kV to PCATSAT4 (509841) 138 kV CKT 1 b. 6. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0330_P4 | a. Apply single phase fault at NEOSHO 4 (533021) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHO 7 (532793) kV to N345 1 1 (532824) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 4 (533021) 138 kV to NEOSHON4 (533022) 138 kV CKT Z1 b. 3. Drop Shunt 1 N345 1 1 (532824) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0331_P4 | a. Apply single phase fault at NEOSHO 5 (532937) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV to NEOSHO 7 (532793) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 5 (532937) 161 kV to RIV4525 (547469) 161 kV CKT 1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0332_P4 | a. Apply single phase fault at NEOSHOS2 (533778) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHOS2 (533778) kV to NSES 2X1 (532710) 13.2 kV CKT1 b. 2. Trip branch from NEOSHOS2 (533778) 69 kV to BAKER 2 (532926) 69 kV CKT 1 b. 3. Trip branch from BAKER 2 (532926) 69 kV to SOPITT 2 (533773) 69 kV CKT 1 b. 4. Drop Load 1 BAKER 2 (532926) 69 kV b. 5. Drop Load 2 BAKER 2 (532926) 69 kV b. 6. Drop Load 3 BAKER 2 (532926) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0333_P4 | a. Apply single phase fault at ALTOONA4 (533001) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ALTOONA4 (533001) 138 kV to G17-022-TAP (588664) 138 kV CKT 1 b. 2. Trip branch from ALTOONA4 (533001) 138 kV to TAYLOR 4 (533006) 138 kV CKT 1 b. 3. Trip branch from TAYLOR 4 (533006) 138 kV to MONTGOM4 (533004) 138 kV CKT 1 b. 4. Drop Load 1 TAYLOR 4 (533006) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0334_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to DELWARE4 (510379) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0335_P1 | 3 phase fault on N.E.S.-7 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345 kV Bus to ONETA--7 (509807) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0336_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to 7BLACKBERRY (300739) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0337_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-009-TAP (532777) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0338_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-209-TAP (760921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0339_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 4 (533021) 138 kV Bus to N345 1 1 (532824) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 1 1 (532824) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0340_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 5 (532937) 161 kV Bus to N345 2 1 (532825) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 2 1 (532825) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0341_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0342_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHON4 (533022) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0343_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to FARML 4 (512734) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0344_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS4 (533020) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0345_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHO 4 (533021) 138 kV Bus to NEOSH4 1 (532958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0346_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS2 (533778) 69 kV Bus to NSES 2X1 (532710) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0347_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to MARMTNW5 (532935) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0348_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to RIV4525 (547469) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0349_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHOS4 (533020) 138 kV Bus to NEOSH5 1 (532959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0350_P1 | 3 phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138 kV Bus to TV1MNDV4 (533008) 138 kV Bus CKT 1 b. 2. Trip branch from TV1MNDV4 (533008) 138 kV Bus to LIBERTY4 (533003) 138 kV Bus CKT 1 b. 3. Drop Load K1 at TV1MNDV4 (533008) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0351_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0352_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHON4 (533022) 138 kV Bus to NEOSHON2 (533768) 69 kV Bus to NEC U3 (532711) 12 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0353_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0354_P1 | 3 phase fault on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DELWARE7 (510380) 345 kV Bus to DELWARE4 (510379) 138 kV Bus to DELAWAR1 (510370) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0355_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to NEOSHON2 (533768) 69 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0356_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to BAKER 2 (532926) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0357_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to CRAWFOR2 (533758) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0358_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to ORDNJCT2 (533703) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0359_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to DEARING4 (533002) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0360_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to NBVILLE4 (510386) 138 kV Bus CKT 1 b. 2. Trip branch from NBVILLE4 (510386) 138 kV Bus to BV-SE--4 (510391) 138 kV Bus CKT 1 b. 3. Drop Load M1 at NBVILLE4 (510386) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0361_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0362_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0363_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0364_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0365_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML 4 (512734) 138 kV Bus to SCOFCTY4 (510378) 138 kV Bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138 kV Bus to SCOFFEYV4 (510420) 138 kV Bus CKT 1 b. 3. Trip branch from SCOFCTY4 (510378) 138 kV Bus to COFFEYT4 (510422) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SCOFFEYV4 (510420) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0366_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA1-1 (509881) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0367_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA2-1 (509868) 34.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0368_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA5-1 (509874) 34.5 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0369_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0370_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0371_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0372_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0373_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV Bus to T.NO.2-4 (509895) 138 kV Bus to TNO2-1 (509894) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0374_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0375_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0376_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY2 (512741) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0377_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7JASPER (300949) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0378_P1 | 3 phase fault on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-209-TAP (760921) 345 kV Bus to LACYGNE7 (542981) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0379_P1 | 3 phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CANEYRV7 (532780) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0381_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARMTNW5 (532935) 161 kV Bus to MARMTNE5 (532934) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0382_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARMTNW5 (532935) 161 kV Bus to MARMATN2 (533639) 69 kV Bus to MARMATN1 (532955) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0383_P1 | 3 phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFOR2 (533758) 69 kV Bus to SE1GREE2 (533772) 69 kV Bus CKT 1 b. 2. Trip branch from SE1GREE2 (533772) 69 kV Bus to GIR JCT2 (533762) 69 kV Bus CKT 1 b. 3. Drop Load K1 at CRAWFOR2 (533758) 69 kV Bus b. 4. Drop Load 1 at CRAWFOR2 (533758) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0384_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 5JASPER (300950) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0385_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0387_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY1 (512740) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0388_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to NEOSHO 7 (532793) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0389_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0390_P4 | a. Apply single phase fault at SUNNYSD7 (515136) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV to SUNNYSD4 (515135) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip branch from SUNNYSD7 (515136) 345 kV to TERRYRD7 (511568) 345 kV CKT 1 b. 3. Drop Shunt SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0391_P4 | a. Apply single phase fault at ARBUCKL4 (515117) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARBUCKL4 (515117) 138 kV to VANOSTP4 (515531) 138 kV CKT 1 b. 2. Trip branch from ARBUCKL4 (515117) 138 kV to SULPHR 4 (515559) 138 kV CKT 1 b. 3. Trip branch from SULPHR 4 (515559) 138 kV to JOLLYVL4 (515118) 138 kV CKT 1 b. 4. Trip branch from JOLLYVL4 (515118) 138 kV to PRICESF4 (514814) 138 kV CKT 1 b. 5. Trip branch from PRICESF4 (514814) 138 kV to HONEYCK4 (515643) 138 kV CKT 1 b. 6. Drop Load 1 SULPHR 4 (515559) 138 kV b. 7. Drop Load 1 JOLLYVL4 (515118) 138 kV b. 8. Drop Load 1 PRICESF4 (514814) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0392_P4 | a. Apply single phase fault at FTSMTHW5 (515301) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FTSMTHW5 (515301) 161 kV to FTSMITH7 (515302) kV to FTSMTH51 (515728) 13.8 kV CKT5 b. 2. Trip branch from FTSMTHW5 (515301) 161 kV to ARKOMA 5 (515306) 161 kV CKT 1 b. 3. Trip branch from ARKOMA 5 (515306) 161 kV to 3RDST 5 (515308) 161 kV CKT 1 b. 4. Drop Shunt 1 ARKOMA 5 (515306) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0393_P4 | a. Apply single phase fault at PARKLN 4 (515178) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PARKLN 4 (515178) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to SEMINOL4 (515044) 138 kV CKT 1 b. 3. Trip branch from PARKLN 4 (515178) 138 kV to SOTHADA4 (515318) 138 kV CKT 1 b. 4. Trip branch from SOTHADA4 (515318) 138 kV to HARDEN 4 (515362) 138 kV CKT 1 b. 5. Trip branch from HARDEN 4 (515362) 138 kV to EFITSTP4 (515699) 138 kV CKT 1 b. 6. Trip branch from EFITSTP4 (515699) 138 kV to LULA 4 (515192) 138 kV CKT 1 b. 7. Trip branch from EFITSTP4 (515699) 138 kV to EFITTS 4 (515809) 138 kV CKT 1 b. 8. Drop Load 1 LKKONWA4 (515977) 138 kV b. 9. Drop Load 1 SOTHADA4 (515318) 138 kV b. 10. Drop Load 1 HARDEN 4 (515362) 138 kV b. 11. Drop Load 1 EFITTS 4 (515809) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0394_P4 | a. Apply single phase fault at LONEOAK4 (510897) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LONEOAK4 (510897) 138 kV to HARTSHN4 (520934) 138 kV CKT 1 b. 2. Trip branch from LONEOAK4 (510897) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 3. Trip branch from SMCALTP4 (510906) 138 kV to MCALEST4 (510908) 138 kV CKT 1 b. 4. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 5. Drop Load 1 S-MCALT4 (510865) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0395_P4 | a. Apply single phase fault at FTSMTHE5 (515300) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FTSMTHE5 (515300) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 2. Trip branch from QUANXTP5 (515310) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 4. Trip branch from BARLING5 (515311) 161 kV to MASSARD5 (515343) 161 kV CKT 1 b. 5. Trip branch from FTSMTHE5 (515300) 161 kV to COLONY 5 (515345) 161 kV CKT 1 b. 6. Trip branch from COLONY 5 (515345) 161 kV to BATTLEF5 (515349) 161 kV CKT 1 b. 7. Trip branch from BATTLEF5 (515349) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 8. Drop Load 1 BARLING5 (515311) 161 kV b. 9. Drop Load 1 QUANEXS5 (515474) 161 kV b. 10. Drop Load 1 COLONY 5 (515345) 161 kV b. 11. Drop Load 1 BATTLEF5 (515349) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0396_P4 | a. Apply single phase fault at WELETK4 (510902) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WELETK4 (510902) 138 kV to WELEETK4 (505592) 138 kV CKT 1 b. 2. Trip branch from WELETK4 (510902) 138 kV to EC.HEN-4 (510923) 138 kV CKT 1 b. 3. Trip branch from EC.HEN-4 (510923) 138 kV to OKMULGE4 (510898) 138 kV CKT 1 b. 4. Drop Load 1 EC.HEN-4 (510923) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0397_P4 | a. Apply single phase fault at MASSARD5 (515343) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MASSARD5 (515343) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 2. Trip branch from MASSARD5 (515343) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from BARLING5 (515311) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 4. Trip branch from QUANXTP5 (515310) 161 kV to FTSMTHE5 (515300) 161 kV CKT 1 b. 5. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 6. Drop Load 1 BARLING5 (515311) 161 kV b. 7. Drop Load 1 QUANEXS5 (515474) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0398_P4 | a. Apply single phase fault at ARCADIA7 (514908) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA7 (514908) 345 kV to REDBUD 7 (514909) 345 kV CKT 1 b. 2. Trip branch from ARCADIA7 (514908) 345 kV to NORTWST7 (514880) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0399_P4 | a. Apply single phase fault at DRAPER 7 (514934) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV to DRAPER 4 (514933) kV to DRAPER41 (515721) 13.8 kV CKT1 b. 2. Trip branch from DRAPER 7 (514934) 345 kV to NSUB345 (555234) kV CKT 1 b. 3. Drop Shunt 1 DRAPER41 (515721) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0400_P4 | a. Apply single phase fault at MUSKOGE7 (515224) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV to FTSMITH7 (515302) 345 kV CKT 1 b. 2. Trip branch from MUSKOGE7 (515224) 345 kV to H_SPRNG-TAP (588839) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0401_P4 | a. Apply single phase fault at SEMINOL4 (515044) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOL4 (515044) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to PARKLN 4 (515178) 138 kV CKT 1 b. 3. Trip branch from SEMINOL4 (515044) 138 kV to MAUD 4 (515055) 138 kV CKT 1 b. 4. Drop Load 1 LKKONWA4 (515977) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0402_P4 | a. Apply single phase fault at CHIKSAW4 (515171) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHIKSAW4 (515171) 138 kV to CARTER 4 (515138) 138 kV CKT 1 b. 2. Trip branch from CHIKSAW4 (515171) 138 kV to FNDTION4 (515162) 138 kV CKT 1 b. 3. Trip branch from FNDTION4 (515162) 138 kV to SPRNDAL4 (515172) 138 kV CKT 1 b. 4. Drop Load 1 FNDTION4 (515162) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0403_P4 | a. Apply single phase fault at SUNNYSD4 (515135) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNNYSD1 (515762) 13.8 kV CKT1 b. 3. Drop Shunt 1 SUNYSD 1 (515405) 13.8 kV b. 4. Drop Shunt 1 SUNNYSD1 (515762) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0404_P4 | a. Apply single phase fault at MCALEST4 (510908) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MCALEST4 (510908) 138 kV to TALAWANDA 4 (510951) 138 kV CKT 1 b. 2. Trip branch from TALAWANDA 4 (510951) 138 kV to MCALESTIND 4 (510909) 138 kV CKT 1 b. 3. Trip branch from TALAWANDA 4 (510951) 138 kV to C-RIVER4 (510946) 138 kV CKT 1 b. 4. Trip branch from MCALEST4 (510908) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 5. Trip branch from SMCALTP4 (510906) 138 kV to LONEOAK4 (510897) 138 kV CKT 1 b. 6. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 7. Drop Load 1 S-MCALT4 (510865) 138 kV b. 8. Drop Load 1 MCALESTIND 4 (510909) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0405_P4 | a. Apply single phase fault at S BROWN4 (505602) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S BROWN4 (505602) 138 kV to RUSSETT4 (521044) 138 kV CKT 1 b. 2. Trip branch from RUSSETT4 (521044) 138 kV to RUSSET-4 (515120) 138 kV CKT 1 b. 3. Trip branch from RUSSETT4 (521044) 138 kV to REAGAN 4 (520465) 138 kV CKT 1 b. 4. Trip branch from S BROWN4 (505602) 138 kV to COLBRTP4 (515159) 138 kV CKT 1 b. 5. Drop Load 1 RUSSETT4 (521044) 138 kV b. 6. Drop Load 1 REAGAN 4 (520465) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0406_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to C-RIVER7 (515422) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0407_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to HUGO 7 (521157) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0408_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN3-1 (510939) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0409_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN2-1 (510938) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0410_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 7 (514809) 345 kV Bus to SUNNYSD7 (515136) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0411_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JOHNCO 7 (514809) 345 kV Bus to JOHNCO 4 (514808) 138 kV Bus to JOHNCO11 (514810) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at JOHNCO11 (514810) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0412_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to ARCADIA7 (514908) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0413_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0414_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0415_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0416_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to SEMINOL7 (515045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0417_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO11 (515756) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO11 (515756) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0418_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO21 (515757) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO21 (515757) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0419_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from C-RIVER7 (515422) 345 kV Bus to C-RIVER4 (510946) 138 kV Bus to C-RIVER1 (510947) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0420_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0421_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT4 (510918) 138 kV Bus to VALIANT2 (510910) 69 kV Bus to VALN1-1 (510937) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0422_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to V-WEYCO4 (510866) 138 kV Bus CKT 1 b. 2. Drop Shunt 1 at V-WEYCO4 (510866) 138 kV Bus1 b. 3. Drop Load 1 at V-WEYCO4 (510866) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0423_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to IDABEL-4 (510886) 138 kV Bus CKT 1 b. 2. Trip branch from IDABEL-4 (510886) 138 kV Bus to B.BOWTP4 (510888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IDABEL-4 (510886) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0424_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO---4 (510901) 138 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0425_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO PP4 (520948) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0426_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to CANEYCK4 (515150) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0427_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to JOHNCO 7 (514809) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0428_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to RUSSET-4 (515120) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0429_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to SXMLCKT4 (515122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0430_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to VANOSTP4 (515531) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0431_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to PAOLI- 4 (515100) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0432_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to MAUD 4 (515055) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0433_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to LKKONWA4 (515977) 138 kV Bus CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV Bus to PARKLN 4 (515178) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0434_P1 | 3 phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply Fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER4 (510946) 138 kV Bus to TALAWANDA 4 (510951) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0435_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to WCITYTP2 (510870) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0436_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to KIPUMPT2 (510876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0437_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TURK 7 (507455) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0438_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0439_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 7 (507455) 345 kV Bus to TURK 4 (507454) 138 kV Bus to TURK 1 (507457) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0440_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX1-1 (508100) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NWTEX1-1 (508100) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0441_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX2-1 (508101) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at NWTEX2-1 (508101) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0442_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0443_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0444_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0445_P1 | 3 phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA 7 (508298) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0446_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO 7 (521157) 345 kV Bus to HUGOITC4 (520560) 138 kV Bus to HUGO TERTA (521189) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0447_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNNYSD1 (515762) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNNYSD1 (515762) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0448_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNYSD 1 (515405) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNYSD 1 (515405) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0449_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0450_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0451_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0452_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0453_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0454_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0455_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0456_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER21 (515792) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0457_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER41 (515721) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER41 (515721) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0458_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER31 (515720) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER31 (515720) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0459_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0460_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to TURK 7 (507455) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0461_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0462_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0463_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0464_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0465_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25S | Transfer | Group4_Fault_0466_P1 | 3 phase fault on HUGO---4 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO---4 (510901) 138 kV Bus to HUGO---2 (510893) 69 kV Bus to HUGO4-1 (510859) 13.8 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus b. 3. Drop Load 1 at HUGO---2 (510893) 69 kV Bus b. 4. Drop Shunt 1 at HUGO---2 (510893) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0467_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to HUGOITC4 (520560) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0468_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to VALLANT4 (521079) 138 kV Bus CKT 1 b. 2. Trip branch from VALLANT4 (521079) 138 kV Bus to GARVIN4 (520419) 138 kV Bus CKT 1 b. 3. Trip branch from GARVIN4 (520419) 138 kV Bus to IDABEL 4 (520953) 138 kV Bus CKT 1 b. 4. Drop Load 1 at VALLANT4 (521079) 138 kV Bus b. 5. Drop Load 1 at GARVIN4 (520419) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0469_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to FROGVIL4 (520918) 138 kV Bus CKT 1 b. 2. Trip branch from FROGVIL4 (520918) 138 kV Bus to WSBNKTP4 (521098) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0470_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to SAWYER4 (520411) 138 kV Bus CKT 1 b. 2. Trip branch from SAWYER4 (520411) 138 kV Bus to RATTAN 4 (521036) 138 kV Bus CKT 1 b. 3. Trip branch from RATTAN 4 (521036) 138 kV Bus to DARWIN 4 (520874) 138 kV Bus CKT 1 b. 4. Trip branch from DARWIN 4 (520874) 138 kV Bus to LANE 4 (520968) 138 kV Bus CKT 1 b. 5. Trip branch from LANE 4 (520968) 138 kV Bus to ATOKA--4 (510887) 138 kV Bus CKT 1 b. 6. Drop Load 1 at SAWYER4 (520411) 138 kV Bus b. 7. Drop Load 1 at RATTAN 4 (521036) 138 kV Bus b. 8. Drop Load 1 at DARWIN 4 (520874) 138 kV Bus b. 9. Drop Load 1 at LANE 4 (520968) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0471_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0472_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to RUSSETT4 (521044) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0473_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to GLASSES4 (515147) 138 kV Bus CKT 1 b. 2. Trip branch from GLASSES4 (515147) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASSES4 (515147) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0474_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to STIRLNG4 (515932) 138 kV Bus CKT 1 b. 2. Trip branch from STIRLNG4 (515932) 138 kV Bus to DRPSPRG4 (515873) 138 kV Bus CKT 1 b. 3. Trip branch from DRPSPRG4 (515873) 138 kV Bus to SPRNDAL4 (515172) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STIRLNG4 (515932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0475_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to HOWE 4 (521122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0476_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to MILLCKT4 (515121) 138 kV Bus CKT 1 b. 2. Trip branch from MILLCKT4 (515121) 138 kV Bus to MILLCRK4 (515196) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0477_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0478_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0479_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to LTLCITY4 (515151) 138 kV Bus CKT 1 b. 2. Trip branch from LTLCITY4 (515151) 138 kV Bus to BROWNTP4 (515152) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0480_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0481_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0482_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0483_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0484_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0485_P4 | a. Apply single phase fault at LYDIA 7 (508298) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LYDIA 7 (508298) 345 kV to WELSH 7 (508359) 345 kV CKT 1 b. 2. Trip branch from LYDIA 7 (508298) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0486_P4 | a. Apply single phase fault at DIANA 4 (508831) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DIANA 4 (508831) 138 kV to DIANA 7 (508832) kV to DIANA-N1 (508845) 13.8 kV CKT3 b. 2. Trip branch from DIANA 4 (508831) 138 kV to PERDUE 4 (508351) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0487_P4 | a. Apply single phase fault at BANN 4 (508054) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BANN 4 (508054) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip branch from BANN 4 (508054) 138 kV to REDSPRG4 (508075) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0488_P4 | a. Apply single phase fault at LONGWD 4 (508808) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from LONGWD 4 (508808) 138 kV to LONGWD 7 (508809) kV to LONGW1-1 (508819) 13.2 kV CKT1 b. 2. Trip branch from LONGWD 4 (508808) 138 kV to LIEBERM4 (508806) 138 kV CKT 1 b. 3. Drop Shunt 1 LONGW1-1 (508819) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0489_P4 | a. Apply single phase fault at SW SHV 4 (507759) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SW SHV 4 (507759) 138 kV to SW SHV 7 (507760) kV to SWSHV1-1 (507778) 13.8 kV CKT1 b. 2. Trip branch from SW SHV 4 (507759) 138 kV to LEASIDE 4 (507793) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0490_P4 | a. Apply single phase fault at PIRKEY 4 (508562) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV to EASTON 4 (509092) 138 kV CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV to BRANDYBR (508596) 138 kV CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV to KNOXLEE4 (508548) 138 kV CKT 1 b. 4. Trip branch from PIRKEY 4 (508562) 138 kV to HALLSVLS4 (508595) 138 kV CKT 1 b. 5. Trip branch from HALLSVLS4 (508595) 138 kV to WHITNEY4 (508575) 138 kV CKT 1 b. 6. Drop Load 1 EASTON 4 (509092) 138 kV b. 7. Drop Load 1 WHITNEY4 (508575) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0491_P4 | a. Apply single phase fault at NWTXARK7 (508072) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK7 (508072) 345 kV to TURK 7 (507455) 345 kV CKT 1 b. 2. Trip branch from NWTXARK7 (508072) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0492_P4 | a. Apply single phase fault at VALIANT7 (510911) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 1 b. 2. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0493_P4 | a. Apply single phase fault at NWTXARK4 (508071) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK4 (508071) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip three winding transformer from NWTXARK7 (508072) 345 kV to NWTXARK4 (508071) kV to NWTEX1-1 (508100) 13.8 kV CKT1 b. 3. Drop Shunt 1 NWTEX1-1 (508100) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0494_P4 | a. Apply single phase fault at PITTSB-7 (510907) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PITTSB-7 (510907) 345 kV to SEMINOL7 (515045) 345 kV CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0495_P4 | a. Apply single phase fault at VALIANT4 (510918) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT4 (510918) 138 kV to HUGO PP4 (520948) 138 kV CKT 1 b. 2. Trip branch from VALIANT4 (510918) 138 kV to IDABEL-4 (510886) 138 kV CKT 1 b. 3. Trip branch from IDABEL-4 (510886) 138 kV to B.BOWTP4 (510888) 138 kV CKT 1 b. 4. Trip branch from B.BOWTP4 (510888) 138 kV to CRAIGJT4 (510890) 138 kV CKT 1 b. 5. Trip branch from B.BOWTP4 (510888) 138 kV to B.BOW 4 (510864) 138 kV CKT 1 b. 6. Drop Load 1 IDABEL-4 (510886) 138 kV b. 7. Drop Load 1 B.BOW 4 (510864) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0496_P4 | a. Apply single phase fault at TURK 4 (507454) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV to TURK 7 (507455) kV to TURK 1 (507457) 13.8 kV CKT1 b. 2. Trip branch from TURK 4 (507454) 138 kV to MANDEVILTP4 (508105) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0497_P4 | a. Apply single phase fault at WILKES 4 (508840) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WILKES 4 (508840) 138 kV to WILKES 7 (508841) kV to WILKES-1 (508826) 13.2 kV CKT1 b. 2. Trip branch from WILKES 4 (508840) 138 kV to LSSOUTH4 (508297) 138 kV CKT 1 b. 3. Drop Shunt 1 WILKES-1 (508826) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0498_P4 | a. Apply single phase fault at PIRKEY 7 (508563) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 7 (508563) 345 kV to DIANA 7 (508832) 345 kV CKT 1 b. 2. Trip branch from PIRKEY 7 (508563) 345 kV to LEBROCK7 (508572) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0499_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-M1 (508843) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0500_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-N1 (508845) 13.8 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0501_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0502_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV Bus to TURK 3 (507456) 115 kV Bus to TURK1 1 (507458) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0503_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0504_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to SPPMAINBUS (5917) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0505_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0506_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-S1 (508844) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0507_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0508_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY4 (508575) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0509_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT1-1 (508589) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0510_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT2-1 (508590) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0511_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to OAKPH 4 (508816) 138 kV Bus CKT 1 b. 2. Trip branch from OAKPH 4 (508816) 138 kV Bus to FLOURNY4 (507727) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OAKPH 4 (508816) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0512_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to NORAM 4 (507774) 138 kV Bus CKT 1 b. 2. Trip branch from NORAM 4 (507774) 138 kV Bus to RAINES 4 (507749) 138 kV Bus CKT 1 b. 3. Trip branch from RAINES 4 (507749) 138 kV Bus to ARSHILL4 (507711) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NORAM 4 (507774) 138 kV Bus b. 5. Drop Load 1 at RAINES 4 (507749) 138 kV Bus b. 6. Drop Shunt 1 at RAINES 4 (507749) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0513_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0514_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLOURNY4 (507727) 138 kV Bus to FLOURNY2 (507726) 69 kV Bus to FLOURNY1 (507740) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0515_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138 kV Bus to GENMOTR4 (507732) 138 kV Bus CKT 1 b. 2. Trip branch from GENMOTR4 (507732) 138 kV Bus to SW SHV 4 (507759) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GENMOTR4 (507732) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0516_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WOOLWTP2 (507770) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0517_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to PINESRD2 (507747) 69 kV Bus CKT 1 b. 2. Trip branch from PINESRD2 (507747) 69 kV Bus to HARDY 2 (507734) 69 kV Bus CKT 1 b. 3. Drop Load 1 at PINESRD2 (507747) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0518_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WASKOM 2 (508839) 69 kV Bus CKT 1 b. 2. Trip branch from WASKOM 2 (508839) 69 kV Bus to MVPIPET2 (508825) 69 kV Bus CKT 1 b. 3. Drop Load 1 at WASKOM 2 (508839) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0519_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to FTHUMBG4 (507731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0520_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to MCWILLI4 (507742) 138 kV Bus CKT 1 b. 2. Trip branch from MCWILLI4 (507742) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MCWILLI4 (507742) 138 kV Bus b. 4. Drop Shunt 1 at MCWILLI4 (507742) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0521_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH1-1 (507712) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0522_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH2-1 (507714) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0523_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0524_P1 | 3 phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply Fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138 kV Bus to IPCJEFF4 (508833) 138 kV Bus CKT 1 b. 2. Trip branch from IPCJEFF4 (508833) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IPCJEFF4 (508833) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0526_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0527_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to TENRUSK7 (508585) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0528_P1 | 3 phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345 kV Bus to CROCKET7 (509241) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0529_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345 kV Bus to 7GRIMES% (334028) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0530_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to LEASIDE 4 (507793) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0531_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to S SHV 4 (507755) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0532_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to POWELL 4 (507748) 138 kV Bus CKT 1 b. 2. Trip branch from POWELL 4 (507748) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POWELL 4 (507748) 138 kV Bus b. 4. Drop Shunt 1 at POWELL 4 (507748) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0533_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to SPRIDGE4 (507757) 138 kV Bus CKT 1 b. 2. Trip branch from SPRIDGE4 (507757) 138 kV Bus to WLNTSPRINGS4 (509103) 138 kV Bus CKT 1 b. 3. Trip branch from WLNTSPRINGS4 (509103) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SPRIDGE4 (507757) 138 kV Bus b. 5. Drop Load 2 at SPRIDGE4 (507757) 138 kV Bus b. 6. Drop Load 1 at WLNTSPRINGS4 (509103) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0534_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to CARROLL6 (500140) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0535_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to REDBAYOU_6 (500255) 230 kV Bus CKT 1 b. 2. Trip branch from REDBAYOU_6 (500255) 230 kV Bus to MANCOMP 6 (500525) 230 kV Bus CKT 1 b. 3. Trip branch from MANCOMP 6 (500525) 230 kV Bus to J1673 POI (46734) 230 kV Bus CKT 1 b. 4. Drop Load IN at REDBAYOU_6 (500255) 230 kV Bus b. 5. Drop Load IN at MANCOMP 6 (500525) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0536_P1 | 3 phase fault on J1673 POI (46734) 230 kV Bus a. Apply Fault at the J1673 POI (46734) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from J1673 POI (46734) 230 kV Bus to FISHER 6 (500310) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0537_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0538_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0539_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to B.BOW 4 (510864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at B.BOW 4 (510864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0540_P1 | 3 phase fault on SUGARHL4 (508080) 138 kV Bus a. Apply Fault at the SUGARHL4 (508080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUGARHL4 (508080) 138 kV Bus to SUGARHL2 (508079) 69 kV Bus to SHILL1-1 (508103) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0541_P1 | 3 phase fault on HOPE 3 (507453) 115 kV Bus a. Apply Fault at the HOPE 3 (507453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOPE 3 (507453) 115 kV Bus to HOPESWI3 (507452) 115 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOPE 3 (507453) 115 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0542_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MANDEVILTP4 (508105) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0543_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MANDEVILTP4 (508105) 138 kV Bus to NE-TEXARK2 (504363) 69 kV Bus to NE-TEXARK1 (504364) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0544_P1 | 3 phase fault on OKAY 4 (507428) 138 kV Bus a. Apply Fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAY 4 (507428) 138 kV Bus to OKAY 2 (507427) 69 kV Bus to OKAY1-1 (507442) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0545_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN1-1 (508097) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0546_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN2-1 (508096) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0547_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to REDSPRG4 (508075) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0548_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0549_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0550_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CROCKET7 (509241) 345 kV Bus to CROCKET4 (509240) 138 kV Bus to CROCK-B1 (509243) 13.8 kV Bus CKT 1 b. 2. Trip branch from CROCKET4 (509240) 138 kV Bus to GRAPLND4 (509322) 138 kV Bus CKT 1 b. 3. Trip branch from GRAPLND4 (509322) 138 kV Bus to SLOCUM 4 (509326) 138 kV Bus CKT 1 b. 4. Trip branch from SLOCUM 4 (509326) 138 kV Bus to ALTO 4 (509320) 138 kV Bus CKT 1 b. 5. Trip branch from ALTO 4 (509320) 138 kV Bus to PINEGRV4 (509324) 138 kV Bus CKT 1 b. 6. Trip branch from PINEGRV4 (509324) 138 kV Bus to JACKSNV4 (509242) 138 kV Bus CKT 1 b. 7. Trip branch from JACKSNV4 (509242) 138 kV Bus to OVERTON4 (509080) 138 kV Bus CKT 1 b. 8. Drop Load 1 at GRAPLND4 (509322) 138 kV Bus b. 9. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 10. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 11. Drop Load 1 at ALTO 4 (509320) 138 kV Bus b. 12. Drop Load 1 at PINEGRV4 (509324) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0551_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 7ROCKYCRK% (334197) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0552_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_1 (334163) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at 1GRIMES_1 (334163) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0553_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_2 (334018) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at 1GRIMES_2 (334018) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0554_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 6GRIMES! (334027) 230 kV Bus CKT 1 b. 2. Trip branch from 6GRIMES! (334027) 230 kV Bus to 6PONDEROSA! (334088) 230 kV Bus CKT 1 b. 3. Trip three winding transformer from 6PONDEROSA! (334088) 230 kV Bus to 4PONDEROSA% (334087) 138 kV Bus to 1PONDEROSA (334094) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0555_P1 | 3 phase fault on 7ROCKYCRK% (334197) 345 kV Bus a. Apply Fault at the 7ROCKYCRK% (334197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7ROCKYCRK% (334197) 345 kV Bus to 6ROCKYCRK (334198) 230 kV Bus CKT 1 b. 2. Trip branch from 6ROCKYCRK (334198) 230 kV Bus to J1671 POI (46714) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0556_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LEASIDE 4 (507793) 138 kV Bus to LEASIDE 2 (507794) 69 kV Bus to LEASIDE 1-1 (507795) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0557_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to WESTELC4 (507767) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0558_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to STONWAL4 (509052) 138 kV Bus CKT 1 b. 2. Trip branch from STONWAL4 (509052) 138 kV Bus to KEATCHI4 (509050) 138 kV Bus CKT 1 b. 3. Trip branch from KEATCHI4 (509050) 138 kV Bus to GEORPAC4 (509064) 138 kV Bus CKT 1 b. 4. Trip branch from GEORPAC4 (509064) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 b. 5. Drop Load 1 at STONWAL4 (509052) 138 kV Bus b. 6. Drop Load 1 at KEATCHI4 (509050) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0559_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to LSSOUTH4 (508297) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0560_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WELSHRE4 (508355) 138 kV Bus CKT 1 b. 2. Trip branch from WELSHRE4 (508355) 138 kV Bus to CHAPELH4 (508337) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WELSHRE4 (508355) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0561_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0562_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0563_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WATLANT4 (508090) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0564_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to MUNZCTY4 (508064) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0565_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP1 (5921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0566_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP2 (5922) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0567_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP3 (5923) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0568_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-REAC1 (5924) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0569_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to WELSHDC1 (5919) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0570_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to 7SAREPTA% (337376) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0571_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0572_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LONGWD 7 (508809) 345 kV Bus to LONGWD 4 (508808) 138 kV Bus to LONGW1-1 (508819) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at LONGW1-1 (508819) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0573_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 2. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 3. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 5. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 6. Drop Load 1 at ALUMAX 4 (508091) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault b. 12. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 13. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 14. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0574_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to PATTERS4 (507431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0575_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0576_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0577_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to PITTSB_4 (508313) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0578_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to DIANA 4 (508831) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0579_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LSSOUTH4 (508297) 138 kV Bus to LSSOUTH2 (508296) 69 kV Bus to LSS-1 (508325) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0580_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to PETTY 4 (508310) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0581_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 7 (508841) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0582_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to CHAPLHL4 (509664) 138 kV Bus CKT 1 b. 2. Trip branch from CHAPLHL4 (509664) 138 kV Bus to LIBERTH4 (509643) 138 kV Bus CKT 1 b. 3. Trip branch from LIBERTH4 (509643) 138 kV Bus to ARGO 4 (509665) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHAPLHL4 (509664) 138 kV Bus b. 5. Drop Load 1 at LIBERTH4 (509643) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0583_P1 | 3 phase fault on ARGO 4 (509665) 138 kV Bus a. Apply Fault at the ARGO 4 (509665) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARGO 4 (509665) 138 kV Bus to ARGO 2 (509642) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0584_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to PERDUE 4 (508351) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0585_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to NGPLTAP4 (508837) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0586_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to DIANASW4 (509639) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0587_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to SPRHILL4 (508571) 138 kV Bus CKT 1 b. 2. Trip branch from SPRHILL4 (508571) 138 kV Bus to LLAMOND4 (508552) 138 kV Bus CKT 1 b. 3. Trip three winding transformer from LLAMOND4 (508552) 138 kV Bus to LLAMOND2 (508551) 69 kV Bus to LLAMON1- (508593) 13.8 kV Bus CKT 1 b. 4. Drop Load 1 at SPRHILL4 (508571) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0588_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY1-1 (508587) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0589_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY2-1 (508588) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0590_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0591_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV1-1 (507778) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SWSHV1-1 (507778) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0592_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV2-1 (507777) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at SWSHV2-1 (507777) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0593_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HUGO 7 (521157) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0594_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WILKES 7 (508841) 345 kV Bus to WILKES 4 (508840) 138 kV Bus to WILKES-1 (508826) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at WILKES-1 (508826) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0595_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0596_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0597_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to MANDEVILTP4 (508105) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0598_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWNR4 (507402) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWNR4 (507402) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWNR4 (507402) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0599_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWN_W 4 (504124) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWN_W 4 (504124) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWN_W 4 (504124) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0600_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN1-1 (507443) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0601_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN2-1 (507444) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0602_P1 | 3 phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply Fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWT-BNT4 (508070) 138 kV Bus to G18-003-TAP (762431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0603_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PERDUE 4 (508351) 138 kV Bus to PERDUE 2 (508350) 69 kV Bus to PERDUE 1 (508356) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0604_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to EXXONM 4 (508369) 138 kV Bus CKT 1 b. 2. Trip branch from EXXONM 4 (508369) 138 kV Bus to LHAWKIN4 (508358) 138 kV Bus CKT 1 b. 3. Drop Load 1 at EXXONM 4 (508369) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0605_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to BIGSAND4 (509603) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0606_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to NEWGLAD4 (508560) 138 kV Bus CKT 1 b. 2. Trip branch from NEWGLAD4 (508560) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 b. 3. Drop Load 1 at NEWGLAD4 (508560) 138 kV Bus b. 4. Drop Shunt 1 at NEWGLAD4 (508560) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0607_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to NGPL 4 (508827) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NGPL 4 (508827) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0608_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to PLILER 4 (508564) 138 kV Bus CKT 1 b. 2. Trip branch from PLILER 4 (508564) 138 kV Bus to LONGVHT4 (508554) 138 kV Bus CKT 1 b. 3. Trip branch from LONGVHT4 (508554) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PLILER 4 (508564) 138 kV Bus b. 5. Drop Load 1 at LONGVHT4 (508554) 138 kV Bus b. 6. Drop Shunt 1 at LONGVHT4 (508554) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0609_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to MARSHL-4 (508557) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0610_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to SABMINT4 (508566) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0611_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to HALLSVLS4 (508595) 138 kV Bus CKT 1 b. 2. Trip branch from HALLSVLS4 (508595) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HALLSVLS4 (508595) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0612_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to EASTON 4 (509092) 138 kV Bus CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV Bus to BRANDYBR (508596) 138 kV Bus CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 4. Drop Load 1 at EASTON 4 (509092) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0613_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#11 (508591) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0614_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#21 (508592) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0615_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARSHL-4 (508557) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0616_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to CHEROKE4 (509059) 138 kV Bus CKT 1 b. 2. Trip branch from CHEROKE4 (509059) 138 kV Bus to TATUM 4 (509087) 138 kV Bus CKT 1 b. 3. Trip branch from TATUM 4 (509087) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHEROKE4 (509059) 138 kV Bus b. 5. Drop Load 1 at TATUM 4 (509087) 138 kV Bus b. 6. Drop Load 2 at TATUM 4 (509087) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0617_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to OAK2HIL4 (509078) 138 kV Bus CKT 1 b. 2. Trip branch from OAK2HIL4 (509078) 138 kV Bus to OAK1HIL4 (509077) 138 kV Bus CKT 1 b. 3. Trip branch from OAK1HIL4 (509077) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 4. Drop Load 1 at OAK2HIL4 (509078) 138 kV Bus b. 5. Drop Load 1 at OAK1HIL4 (509077) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0618_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SABINEM4 (508577) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SABINEM4 (508577) 138 kV Bus b. 3. Drop Load 2 at SABINEM4 (508577) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0619_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SEMRSHL4 (508569) 138 kV Bus CKT 1 b. 2. Trip branch from SEMRSHL4 (508569) 138 kV Bus to SCOTTSV4 (508567) 138 kV Bus CKT 1 b. 3. Trip branch from SCOTTSV4 (508567) 138 kV Bus to LONGWD 4 (508808) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SEMRSHL4 (508569) 138 kV Bus b. 5. Drop Load 1 at SCOTTSV4 (508567) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0620_P4 | a. Apply single phase fault at 3SAREPTA! (337363) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3SAREPTA! (337363) 115 kV to 7SAREPTA% (337376) 345 kV CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115 kV to 3MINDEN_LA! (337361) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0621_P4 | a. Apply single phase fault at 3STERLING% (337415) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3STERLING% (337415) 115 kV to 8STERLING% (337420) kV to 1STERLING3 (337412) 13.8 kV CKT3 b. 2. Trip branch from 3STERLING% (337415) 115 kV to 8STERLING2% (337413) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0622_P4 | a. Apply single phase fault at 3STERL2% (337414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3STERL2% (337414) 115 kV to 3DREW_LA (337382) 115 kV CKT 1 b. 2. Trip branch from 3DREW_LA (337382) 115 kV to 3CHENIERE (337383) 115 kV CKT 1 b. 3. Trip branch from 3CHENIERE (337383) 115 kV to 3RISER (337384) 115 kV CKT 1 b. 4. Trip branch from 3RISER (337384) 115 kV to 3FROSTKRAFT! (337385) 115 kV CKT 1 b. 5. Trip branch from 3STERL2% (337414) 115 kV to 8STERLING2% (337413) 500 kV CKT 2 b. 6. Drop Load 1 3DREW_LA (337382) 115 kV b. 7. Drop Load 1 3CHENIERE (337383) 115 kV b. 8. Drop Load 1 3RISER (337384) 115 kV b. 9. Drop Shunt 1 3SHULER (337521) 115 kV b. 10. Drop Shunt 1 3RISER (337384) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0623_P4 | a. Apply single phase fault at 8EL DORADO% (337561) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8EL DORADO% (337561) 500 kV to 8MT_OLIVE% (337368) 500 kV CKT 1 b. 2. Trip branch from 8EL DORADO% (337561) 500 kV to 8STERLING% (337420) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0624_P4 | a. Apply single phase fault at LIEBERM4 (508806) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LIEBERM4 (508806) 138 kV to LONGWD 4 (508808) 138 kV CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138 kV to G16-167-TAP (588404) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0625_P4 | a. Apply single phase fault at 3MINDEN_LA! (337361) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3SAREPTA! (337363) 115 kV CKT 1 b. 2. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3MINDEN_LG (303302) 115 kV CKT 1 b. 3. Trip branch from 3MINDEN_LG (303302) 115 kV to 3ARCADIA (337367) 115 kV CKT 1 b. 4. Trip branch from 3ARCADIA (337367) 115 kV to 3REESE (337380) 115 kV CKT 1 b. 5. Trip branch from 3REESE (337380) 115 kV to 3TRUSSEL_CR (303310) 115 kV CKT 1 b. 6. Trip branch from 3TRUSSEL_CR (303310) 115 kV to 3VIENNA_LA! (337371) 115 kV CKT 1 b. 7. Drop Load 1 3MINDEN_LG (303302) 115 kV b. 8. Drop Load 1 3ARCADIA (337367) 115 kV b. 9. Drop Load LG 3ARCADIA (337367) 115 kV b. 10. Drop Load IN 3REESE (337380) 115 kV b. 11. Drop Load 1 3TRUSSEL_CR (303310) 115 kV b. 12. Drop Shunt 1 3MINDEN_LG (303302) 115 kV b. 13. Drop Load 1 3ARCADIA (337367) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0626_P4 | a. Apply single phase fault at 3EL DORADO! (337539) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3EL DORADO! (337539) 115 kV to 8EL DORADO% (337561) kV to 1EL DORADO1 (337564) 13.8 kV CKT1 b. 2. Trip branch from 3EL DORADO! (337539) 115 kV to 3ELDORADO.E! (337553) 115 kV CKT 1 b. 3. Drop Shunt 1 1EL DORADO1 (337564) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0627_P4 | a. Apply single phase fault at ARSHILL4 (507711) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARSHILL4 (507711) 138 kV to FTHUMBG4 (507731) 138 kV CKT 1 b. 2. Trip three winding transformer from ARSHILL4 (507711) 138 kV to ARSHILL2 (507710) kV to ARSH1-1 (507712) 12.47 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0628_P4 | a. Apply single phase fault at 3MCNEIL! (337516) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MCNEIL! (337516) 115 kV to 8MCNEIL% (337515) 500 kV CKT 1 b. 2. Trip branch from 3MCNEIL! (337516) 115 kV to 3MAGNOLIA.W (337519) 115 kV CKT 1 b. 3. Trip branch from 3MAGNOLIA.W (337519) 115 kV to 3MAGNOLIA.S (337520) 115 kV CKT 1 b. 4. Trip branch from 3MAGNOLIA.S (337520) 115 kV to 3SHULER (337521) 115 kV CKT 1 b. 5. Trip branch from 3SHULER (337521) 115 kV to 3WYATT! (337544) 115 kV CKT 1 b. 6. Drop Load IN 3MAGNOLIA.W (337519) 115 kV b. 7. Drop Load 1 3MAGNOLIA.S (337520) 115 kV b. 8. Drop Load IN 3SHULER (337521) 115 kV b. 9. Drop Load 1 3SHULER (337521) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0629_P4 | a. Apply single phase fault at 8STERLING2% (337413) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8STERLING2% (337413) 500 kV to 8PERRYVILLE% (337427) 500 kV CKT 1 b. 2. Trip branch from 8STERLING2% (337413) 500 kV to 8STERLING% (337420) 500 kV CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0630_P4 | a. Apply single phase fault at 8PERRYVILLE% (337427) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8BXTRWILSON% (336830) 500 kV CKT 1 b. 2. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8STERLING% (337420) 500 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0631_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G16-091-TAP (587744) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0632_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0633_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0634_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0635_P1 | 3 phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply Fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0636_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0637_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0638_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0639_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 b. 2. Drop Shunt 1 at OKLAUN HVDC7 (511565) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0640_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0641_P1 | 3 phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply Fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800]
04 - Southeast | 25S | Transfer | Group4_Fault_0642_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to G18-015-TAP (762467) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0643_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0644_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G17-171-TAP (760938) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0645_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0646_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NSUB345 (555234) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0647_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750000) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0648_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750001) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0649_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0650_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#4-1 (511414) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0651_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0652_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0653_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO11 (515714) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO11 (515714) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0654_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO21 (515715) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO21 (515715) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0655_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#5-1 (511411) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0656_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to FLETCHR4 (511422) 138 kV Bus CKT 1 b. 2. Drop Load 1 at FLETCHR4 (511422) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0657_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0658_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to L.E.S.-4 (511467) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0659_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to ELGINJT4 (511486) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0660_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to LWSTAP 4 (511439) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0661_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to SHERID4 (511474) 138 kV Bus CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV Bus to ARTVLTP4 (511537) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHERID4 (511474) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0662_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMMTAP4 (511494) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0663_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#1-1 (511416) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0664_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#2-1 (511415) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0665_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0666_P1 | 3 phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply Fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345 kV Bus to GRACMNT7 (515800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587773 [G16-095-GEN10.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0667_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0668_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0669_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to OMDUNCN4 (529304) 138 kV Bus CKT 1 b. 2. Trip branch from OMDUNCN4 (529304) 138 kV Bus to DUNCAN-4 (511453) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0670_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to G16-097-TAP (587794) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0671_P1 | 3 phase fault on COMANC-4 (511437) 138 kV Bus a. Apply Fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMANC-4 (511437) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0672_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to LWS S4 (511431) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LWS S4 (511431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0673_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to RPPAPER4 (511512) 138 kV Bus CKT 1 b. 2. Trip branch from RPPAPER4 (511512) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 b. 3. Drop Load 1 at RPPAPER4 (511512) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0674_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELGINJT4 (511486) 138 kV Bus to ELSWORTH 4 (511563) 138 kV Bus CKT 1 b. 2. Trip branch from ELSWORTH 4 (511563) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ELSWORTH 4 (511563) 138 kV Bus b. 4. Drop Load 2 at ELSWORTH 4 (511563) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0675_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELGINJT4 (511486) 138 kV Bus to ELGINJT2 (511487) 69 kV Bus to ELGJT1-1 (511412) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0676_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to SEQUOYAHJ4 (520422) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0677_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to MINCO 7 (514801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0678_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CLVLDSW4 (520508) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0679_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CHERRYRD 4 (521129) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0680_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to POCASET4 (521031) 138 kV Bus CKT 1 b. 2. Trip branch from POCASET4 (521031) 138 kV Bus to TUTLETP4 (521072) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POCASET4 (521031) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0681_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to GEORGIA4 (520923) 138 kV Bus CKT 1 b. 2. Trip branch from GEORGIA4 (520923) 138 kV Bus to FLETCH-4 (520912) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GEORGIA4 (520923) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0682_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANADARK4 (520814) 138 kV Bus to ANADARK2 (520810) 69 kV Bus to ADRKTERT (521181) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0683_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0685_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WASHITA4 (521089) 138 kV Bus to WASHITA2 (521088) 69 kV Bus to WASHTERT (521179) 7.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0686_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to ONEY 4 (521017) 138 kV Bus CKT 1 b. 2. Trip branch from ONEY 4 (521017) 138 kV Bus to BINGERJ4 (520827) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ONEY 4 (521017) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 599003 [BLUCAN2-WTG50.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0687_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to G16-037-TAP (560078) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0688_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0689_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 2. Trip branch from L.E.S.-4 (511467) 138 kV to COMMTAP4 (511494) 138 kV CKT 1 b. 3. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0690_P4 | a. Apply single phase fault at MINCO 7 (514801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MINCO 7 (514801) 345 kV to NSUB345 (555234) kV CKT 1 b. 2. Trip branch from MINCO 7 (514801) 345 kV to GRACMNT7 (515800) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0691_P4 | a. Apply single phase fault at GRACMNT4 (515802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GRACMNT4 (515802) 138 kV to GRACMNT7 (515800) kV to GRCMNT11 (515801) 13.8 kV CKT2 b. 2. Trip branch from GRACMNT4 (515802) 138 kV to ANADARK4 (520814) 138 kV CKT 1 b. 3. Drop Shunt 1 GRCMNT11 (515801) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0692_P4 | a. Apply single phase fault at L.E.S.-2 (511466) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-2 (511466) 69 kV to L.E.S.-4 (511467) kV to LES#1-1 (511416) 13.8 kV CKT1 b. 2. Trip branch from L.E.S.-2 (511466) 69 kV to LGORE-S2 (511470) 69 kV CKT 1 b. 3. Trip branch from LGORE-S2 (511470) 69 kV to LAW WC2 (511503) 69 kV CKT 1 b. 4. Drop Load 1 LGORE-S2 (511470) 69 kV b. 5. Drop Load 1 LAW WC2 (511503) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0693_P4 | a. Apply single phase fault at 112GORE4 (511488) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 112GORE4 (511488) 138 kV to COMANC-4 (511437) 138 kV CKT 1 b. 2. Trip branch from 112GORE4 (511488) 138 kV to LAIRGST4 (511510) 138 kV CKT 1 b. 3. Trip branch from LAIRGST4 (511510) 138 kV to CACHE4 (511500) 138 kV CKT 1 b. 4. Trip branch from LAIRGST4 (511510) 138 kV to L AIRGS4 (511429) 138 kV CKT 1 b. 5. Trip branch from CACHE4 (511500) 138 kV to G17-036_TAP (588779) 138 kV CKT 1 b. 6. Drop Load 1 CACHE4 (511500) 138 kV b. 7. Drop Load 1 L AIRGS4 (511429) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0694_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0696_P4 | a. Apply single phase fault at ELKCTY-4 (511458) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ELKCTY-4 (511458) 138 kV to CLINTJC4 (511485) 138 kV CKT 1 b. 2. Trip branch from ELKCTY-4 (511458) 138 kV to REDHLSW4 (521116) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0697_P4 | a. Apply single phase fault at WWRDEHV4 (515376) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WWRDEHV4 (515376) 138 kV to WWRDEHV7 (515375) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 2. Trip branch from WWRDEHV4 (515376) 138 kV to IODINE-4 (514796) 138 kV CKT 1 b. 3. Trip branch from IODINE-4 (514796) 138 kV to REDCLFT4 (515533) 138 kV CKT 1 b. 4. Trip branch from REDCLFT4 (515533) 138 kV to DEWEY 4 (514787) 138 kV CKT 1 b. 5. Trip branch from REDCLFT4 (515533) 138 kV to REDCLF 4 (515863) 138 kV CKT 1 b. 6. Drop Load 1 IODINE-4 (514796) 138 kV b. 7. Drop Load 1 REDCLF 4 (515863) 138 kV b. 8. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0698_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TOLK 6 (525531) 230 kV to TOLK 7 (525549) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 2. Trip branch from TOLK 6 (525531) 230 kV to PLANT_X 6 (525481) 230 kV CKT 2 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0699_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0700_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0701_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0702_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHEELER 6 (523777) 230 kV Bus to WHEELER 3 (523776) 115 kV Bus to WHEELER_TR11 (523774) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0703_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0704_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0705_P1 | 3 phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRAPEVINE 6 (523771) 230 kV Bus to GRAPEVINE 3 (523770) 115 kV Bus to GRAPEVN_TR11 (523769) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0706_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0707_P1 | 3 phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTTER_CO 7 (523961) 345 kV Bus to POTTER_CO 6 (523959) 230 kV Bus to POTTER_TR 1 (523957) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at POTTER_TR 1 (523957) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0708_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0709_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0710_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0711_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELKCITY6 (511490) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0712_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0713_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0714_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0715_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0716_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0717_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0718_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0719_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF3 (525539) kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0720_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0721_P4 | a. Apply single phase fault at CLARMR 5 (512651) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 4 (512707) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 4 (512707) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 3. Trip branch from OOLOGAHKM 4 (513124) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 4. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 2 (512679) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 5. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0722_P4 | a. Apply single phase fault at 4SILVCTY (300140) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4SILVCTY (300140) 138 kV to 4BRISTOW (300137) 138 kV CKT 1 b. 2. Trip branch from 4SILVCTY (300140) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0723_P4 | a. Apply single phase fault at GORE GR2 (512644) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GORE GR2 (512644) 69 kV to GORE 5 (505552) kV to GORTER1 (512832) 13.8 kV CKT1 b. 2. Trip branch from GORE GR2 (512644) 69 kV to 2VIAN (300879) 69 kV CKT 1 b. 3. Drop Load 1 2VIAN (300879) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0724_P4 | a. Apply single phase fault at CATSAGR5 (512638) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATSAGR5 (512638) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to COLINS 5 (512627) 161 kV CKT 1 b. 3. Trip branch from CATSAGR5 (512638) 161 kV to MAID 5 (512648) 161 kV CKT 1 b. 4. Drop Load 1 5ELMCRK (300993) 161 kV b. 5. Drop Load 2 5ELMCRK (300993) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0725_P4 | a. Apply single phase fault at CLARMR 2 (512679) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 2 (512679) 69 kV to CLARMR 5 (512651) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 2 (512679) 69 kV to CLARCTY4 2 (513014) 69 kV CKT 1 b. 3. Trip branch from CLARCTY4 2 (513014) 69 kV to CLARCTY1 2 (513010) 69 kV CKT 1 b. 4. Drop Load 1 CLARCTY4 2 (513014) 69 kV b. 5. Drop Load 1 CLARCTY1 2 (513010) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0726_P4 | a. Apply single phase fault at CATOOSA4 (509790) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATOOSA4 (509790) 138 kV to TERNITP4 (509835) 138 kV CKT 1 b. 2. Trip branch from TERNITP4 (509835) 138 kV to TER-NIT4 (509723) 138 kV CKT 1 b. 3. Trip branch from TERNITP4 (509835) 138 kV to VERDIGS4 (509854) 138 kV CKT 1 b. 4. Trip branch from VERDIGS4 (509854) 138 kV to CLARTOK4 (509864) 138 kV CKT 1 b. 5. Trip branch from CLARTOK4 (509864) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 6. Trip branch from CATOOSA4 (509790) 138 kV to INOLATP4 (509752) 138 kV CKT 1 b. 7. Trip branch from INOLATP4 (509752) 138 kV to INOLA 4 (509736) 138 kV CKT 1 b. 8. Trip branch from INOLATP4 (509752) 138 kV to ROCKPT-4 (510437) 138 kV CKT 1 b. 9. Trip branch from ROCKPT-4 (510437) 138 kV to CHOUTEA4 (510373) 138 kV CKT 1 b. 10. Trip branch from CHOUTEA4 (510373) 138 kV to EXCLART4 (510401) 138 kV CKT 1 b. 11. Drop Load 1 TER-NIT4 (509723) 138 kV b. 12. Drop Shunt 1 TER-NIT4 (509723) 138 kV b. 13. Drop Load M1 VERDIGS4 (509854) 138 kV b. 14. Drop Load M2 VERDIGS4 (509854) 138 kV b. 15. Drop Load 1 CLARTOK4 (509864) 138 kV b. 16. Drop Load 1 INOLA 4 (509736) 138 kV b. 17. Drop Load 1 ROCKPT-4 (510437) 138 kV b. 18. Drop Load 1 CHOUTEA4 (510373) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0727_P4 | a. Apply single phase fault at COLINS 5 (512627) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from COLINS 5 (512627) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to CATSAGR5 (512638) 161 kV CKT 1 b. 3. Trip branch from COLINS 5 (512627) 161 kV to 5KETONVL (300997) 161 kV CKT 1 b. 4. Trip branch from 5KETONVL (300997) 161 kV to CLARMR 5 (512651) 161 kV CKT 1 b. 5. Drop Load 2 5ELMCRK (300993) 161 kV b. 6. Drop Load 1 5KETONVL (300997) 161 kV b. 7. Drop Load 2 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0728_P4 | a. Apply single phase fault at HUNT 2 (512671) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HUNT 2 (512671) 69 kV to MAIDTP2 (512625) 69 kV CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV to GRDA1 2 (512727) 69 kV CKT 1 b. 3. Trip three winding transformer from GRDA1 2 (512727) 69 kV to GRDA1 5 (512656) kV to GRDA1 1 (512816) 13.8 kV CKT1 b. 4. Trip branch from HUNT 2 (512671) 69 kV to PRY0RC22 (512639) 69 kV CKT 1 b. 5. Trip branch from PRY0RC22 (512639) 69 kV to PRYORC32 (512622) 69 kV CKT 1 b. 6. Trip branch from PRYORC32 (512622) 69 kV to PRYORC12 (512810) 69 kV CKT 1 b. 7. Drop Load 1 PRY0RC22 (512639) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0729_P4 | a. Apply single phase fault at COLNSGR2 (512870) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from COLNSGR2 (512870) 69 kV to COLINS 5 (512627) kV to COLLIN3 1 (512840) 13.8 kV CKT2 b. 2. Trip branch from COLNSGR2 (512870) 69 kV to PARKMEDTP (512703) 69 kV CKT 1 b. 3. Trip branch from PARKMEDTP (512703) 69 kV to 2PARKMDWS (301999) 69 kV CKT 1 b. 4. Trip branch from PARKMEDTP (512703) 69 kV to SKIATTP2 (512871) 69 kV CKT 1 b. 5. Drop Load 1 2PARKMDWS (301999) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0730_P4 | a. Apply single phase fault at SPRGFLD5 (505492) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV to BROOKLINE 5 (549969) 161 kV CKT 1 b. 2. Trip branch from SPRGFLD5 (505492) 161 kV to CLAY 5 (549970) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0731_P4 | a. Apply single phase fault at JTEC 5 (549954) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JTEC 5 (549954) 161 kV to SW DISP PLT5 (549960) 161 kV CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 b. 3. Trip branch from JTEC 5 (549954) 161 kV to 5BTLFD (300348) 161 kV CKT 1 b. 4. Trip branch from 5BTLFD (300348) 161 kV to 5JAMESV (300089) 161 kV CKT 1 b. 5. Drop Load W SW DISP PLT5 (549960) 161 kV b. 6. Drop Load E SW DISP PLT5 (549960) 161 kV b. 7. Drop Load E 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0732_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to 2CDRCRST (301345) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0733_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0734_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0735_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0736_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to W.GRDNR7 (542965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0737_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFCRK7 (532797) 345 kV Bus to WOLFCRK2 (533653) 69 kV Bus to WOLFCRK1 (532962) 17 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0738_P1 | 3 phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0739_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 532712 [G17-009-GEN10.6900], 532713 [G17-009-GEN20.6900], 532714 [G17-009-GEN30.6900], 532715 [G17-009-GEN40.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0740_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 4 (512707) 138 kV Bus to CLARMR4 (512813) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0741_P1 | 3 phase fault on FT GIB 5 (505560) 161 kV Bus a. Apply Fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FT GIB 5 (505560) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0742_P1 | 3 phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply Fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAYGR 5 (512640) 161 kV Bus to OKAYGR 2 (512646) 69 kV Bus to OKAY1 (512848) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0743_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KETCHUM5 (512669) 161 kV Bus CKT 1 b. 2. Trip branch from KETCHUM5 (512669) 161 kV Bus to AFTON 5 (512632) 161 kV Bus CKT 1 b. 3. Drop Load 1 at KETCHUM5 (512669) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0744_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENSA 5 (512654) 161 kV Bus to PENSA 2 (512628) 69 kV Bus to PENSA 1 (512841) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0745_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to TAHLQH 5 (512655) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0746_P4 | a. Apply single phase fault at TATONGA7 (515407) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TATONGA7 (515407) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345 kV to WWRDEHV7 (515375) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0747_P4 | a. Apply single phase fault at HARPER 4 (539668) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HARPER 4 (539668) 138 kV to FLATRDG4 (539638) 138 kV CKT 1 b. 2. Trip branch from HARPER 4 (539668) 138 kV to MILANTP4 (539675) 138 kV CKT 1 b. 3. Trip branch from MILANTP4 (539675) 138 kV to CONWAY (539009) 138 kV CKT 1 b. 4. Trip branch from CONWAY (539009) 138 kV to VIOLA 4 (533075) 138 kV CKT 1 b. 5. Drop Load 1 CONWAY (539009) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0748_P4 | a. Apply single phase fault at DGRASSE7 (515852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0749_P4 | a. Apply single phase fault at MATHWSN7 (515497) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MATHWSN7 (515497) 345 kV to CIMARON7 (514901) 345 kV CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345 kV to TATONGA7 (515407) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0750_P4 | a. Apply single phase fault at BADGER 7 (515677) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 1 b. 2. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0751_P4 | a. Apply single phase fault at THISTLE7 (539801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0752_P4 | a. Apply single phase fault at DGRASSE4 (515853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0753_P4 | a. Apply single phase fault at CIMARON7 (514901) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CIMARON7 (514901) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from CIMARON7 (514901) 345 kV to NSUB345 (555234) kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0754_P4 | a. Apply single phase fault at CLARKCOUNTY7 (539800) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0755_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to WWDBORDT (755000) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0756_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV21 (515799) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at WWDEHV21 (515799) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0758_P1 | 3 phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FINNEY 7 (523853) 345 kV Bus to HOLCOMB7 (531449) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0761_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TR 1 (525537) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TOLK_TR 1 (525537) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0762_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF2 (525538) kV Bus CKT 2 b. 2. Drop Shunt 1 at TOLK_TF2 (525538) kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0763_P1 | 3 phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OCHILTREE 6 (523155) 230 kV Bus to OCHILTREE 3 (523154) 115 kV Bus to OCHLTRE_TR11 (523151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0764_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to HARPER 4 (539668) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0765_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0766_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV31 (515795) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at WWDEHV31 (515795) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0767_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0768_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to SETAB 7 (531465) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0769_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOLCOMB7 (531449) 345 kV Bus to HOLCOMB3 (531448) 115 kV Bus to HOLCTER1 (531450) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOLCTER1 (531450) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0770_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to BUCKNER7 (531501) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0771_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0772_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to CIM-PLT3 (539654) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0773_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0774_P1 | 3 phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply Fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from REDCLFT4 (515533) 138 kV Bus to REDCLF 4 (515863) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0775_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0776_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0777_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0778_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0779_P1 | 3 phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPERVIL7 (531469) 345 kV Bus to IRONWOOD7 (539803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0780_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to LAMB_CNTY 6 (525637) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_TR3 1 (525633) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0781_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0782_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0783_P1 | 3 phase fault on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIM-PLT3 (539654) 115 kV Bus to N-CIMRN3 (539749) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0784_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0785_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0786_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0787_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to BORDER 7 (515458) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0788_P1 | 3 phase fault on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BORDER 7 (515458) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0789_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0790_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0791_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0792_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345 kV Bus to GRAPEVINE (560035) 345 kV Bus CKT 1 b. 2. Trip branch from GRAPEVINE (560035) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0793_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0794_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0796_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0797_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0798_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0799_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS41 (514885) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS41 (514885) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0800_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS31 (515743) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS31 (515743) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0801_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS21 (515742) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS21 (515742) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0802_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0803_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to BVRCNTY7 (515554) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0804_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0805_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0806_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0807_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0808_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0809_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0810_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0811_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0812_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from THISTLE7 (539801) 345 kV Bus to THISTLE4 (539804) 138 kV Bus to THISTLE T1 (539802) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0813_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0814_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0815_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0816_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0817_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0818_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0819_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0820_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR21 (523094) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0821_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR01 (523091) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0822_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0823_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at CHISHOLM1 (511558) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0824_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to ELKCITY6 (511490) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0825_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to SWEETWT6 (511541) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0826_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to FINNEY 7 (523853) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0827_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 b. 2. Trip three winding transformer from HARBNGR7 (531512) 345 kV Bus to HARBNGR3 (531510) 115 kV Bus to HARBNGR-T (531511) 13.8 kV Bus CKT 1 b. 3. Trip branch from HARBNGR3 (531510) 115 kV Bus to WALKMYR3 (531405) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0828_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0829_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587958 [G16-119-GEN20.6900], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0830_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0831_P1 | 3 phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDNGTN7 (515875) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0832_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to OCHILTREE 6 (523155) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0833_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0834_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR11 (523092) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0835_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR41 (523098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0836_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0837_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0839_P1 | 3 phase fault on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE4 (539804) 138 kV Bus to FLATRDG4 (539638) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0840_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORLND4 (520999) 138 kV Bus to MOORLND2 (520995) 69 kV Bus to MLNDTERT (521180) 2.4 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0841_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to IODINE 4 (520957) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE 4 (520957) 138 kV Bus to FTSUPLY4 (520920) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE 4 (520957) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0842_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to SEILING4 (520553) 138 kV Bus CKT 1 b. 2. Trip branch from SEILING4 (520553) 138 kV Bus to TALOGA 4 (521065) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SEILING4 (520553) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0843_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to ASPEN 4 (520462) 138 kV Bus CKT 1 b. 2. Trip branch from ASPEN 4 (520462) 138 kV Bus to BEARCAT4 (520500) 138 kV Bus CKT 1 b. 3. Trip branch from BEARCAT4 (520500) 138 kV Bus to NINMLTP4 (521128) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ASPEN 4 (520462) 138 kV Bus b. 5. Drop Load 1 at BEARCAT4 (520500) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0844_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to PIC4 (520425) 138 kV Bus CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV Bus to CDRDLTP4 (520848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at PIC4 (520425) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0845_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0846_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0847_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0848_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_0849_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0850_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 2. Trip branch from STLN-DEMARC6 (523779) 230 kV Bus to WHEELER 6 (523777) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25S | Transfer | Group4_Fault_0854_P1 | 3 phase fault on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LAMAR7 (599950) 345 kV Bus to G18-030-TAP (762662) 345 kV Bus CKT 1 b. 2. Drop Load 1 at LAMAR7 (599950) 345 kV Bus b. 3. Drop Shunt 1 at LAMAR7 (599950) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0855_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to COBRN_CREEK3 (523772) 115 kV Bus CKT 1 b. 2. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus b. 3. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0856_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to HOWARD 3 (523797) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0857_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR11 (524041) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0858_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR21 (524042) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0859_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HUTCHISON 6 (523551) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0860_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0861_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0862_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0863_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to BOWERS 3 (523748) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0864_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0865_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_N 3 (523544) 115 kV Bus to HUTCH_TR1N 1 (523540) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0866_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_S 3 (523546) 115 kV Bus to HUTCH_TR2S 1 (523541) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0867_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0868_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to EAST_PLANT 6 (524163) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0869_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0870_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0871_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0872_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0873_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0874_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to NEWHART 6 (525461) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0875_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0876_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0877_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0878_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to FAIN 3 (523339) 115 kV Bus CKT 1 b. 2. Trip branch from FAIN 3 (523339) 115 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FAIN 3 (523339) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0879_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO 3 (524016) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ASARCO 3 (524016) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0880_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO_TP 3 (524018) 115 kV Bus CKT 1 b. 2. Trip branch from ASARCO_TP 3 (524018) 115 kV Bus to HIGHLAND_TP3 (523931) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0881_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 5. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 6. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0882_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to CAMX/AGR TP3 (523485) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0883_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to HUTCH_S 3 (523546) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0884_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0885_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0886_P1 | 3 phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply Fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAN+TASCOS6 (523869) 230 kV Bus to XIT_INTG 6 (523221) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from XIT_INTG 6 (523221) 230 kV Bus to XIT_INTG 3 (523220) 115 kV Bus to XIT_INTG TR1 (523219) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0887_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to CAMEX/AGRM 3 (523486) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CAMEX/AGRM 3 (523486) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0888_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0889_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0890_P1 | 3 phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138 kV Bus to IODINE-4 (514796) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE-4 (514796) 138 kV Bus to REDCLFT4 (515533) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE-4 (514796) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0891_P4 | a. Apply single phase fault at MOORLND4 (520999) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MOORLND4 (520999) 138 kV to PIC4 (520425) 138 kV CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV to CDRDLTP4 (520848) 138 kV CKT 1 b. 3. Trip branch from CDRDLTP4 (520848) 138 kV to CEDRDAL4 (520507) 138 kV CKT 1 b. 4. Trip branch from CDRDLTP4 (520848) 138 kV to OKEENE 4 (521016) 138 kV CKT 1 b. 5. Trip branch from MOORLND4 (520999) 138 kV to ASPEN 4 (520462) 138 kV CKT 1 b. 6. Trip branch from ASPEN 4 (520462) 138 kV to BEARCAT4 (520500) 138 kV CKT 1 b. 7. Trip branch from BEARCAT4 (520500) 138 kV to NINMLTP4 (521128) 138 kV CKT 1 b. 8. Trip branch from NINMLTP4 (521128) 138 kV to NINMILE4 (520492) 138 kV CKT 1 b. 9. Trip branch from NINMLTP4 (521128) 138 kV to MORWODS4 (521001) 138 kV CKT 1 b. 10. Drop Load 1 CEDRDAL4 (520507) 138 kV b. 11. Drop Load 1 PIC4 (520425) 138 kV b. 12. Drop Load 1 ASPEN 4 (520462) 138 kV b. 13. Drop Load 1 BEARCAT4 (520500) 138 kV b. 14. Drop Load 1 NINMILE4 (520492) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0892_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0893_P1 | 3 phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138 kV Bus to AVARD 4 (520601) 138 kV Bus CKT 1 b. 2. Drop Load 1 at AVARD 4 (520601) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0894_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0895_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0896_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0897_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0898_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD4 (514785) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0899_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to ALVAOGE2 (514792) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0900_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to CZYCRVT2 (515560) 69 kV Bus CKT 1 b. 2. Trip branch from CZYCRVT2 (515560) 69 kV Bus to SALINE 2 (514716) 69 kV Bus CKT 1 b. 3. Trip branch from SALINE 2 (514716) 69 kV Bus to HELENAT2 (515371) 69 kV Bus CKT 1 b. 4. Drop Load 1 at CZYCRVT2 (515560) 69 kV Bus b. 5. Drop Shunt 1 at CZYCRVT2 (515560) 69 kV Bus1 b. 6. Drop Load 1 at SALINE 2 (514716) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0901_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0902_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0903_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODWRD4 (514785) 138 kV Bus to WODWRD 2 (514782) 69 kV Bus to WOODWR21 (515771) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0904_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to MORWODS4 (521001) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0905_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to NINMILE4 (520492) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NINMILE4 (520492) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0906_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0907_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to CURTIS 2 (520480) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CURTIS 2 (520480) 69 kV Bus b. 3. Drop Load 2 at CURTIS 2 (520480) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0908_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALVA 2 (520806) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0909_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALINETP2 (515803) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0910_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0911_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOCOR4 (514778) 138 kV Bus to CLEOPLT4 (515562) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0912_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEOCOR4 (514778) 138 kV Bus to CLEOCOR2 (514777) 69 kV Bus to CLEOCOR1 (515716) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0913_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to OKEENE 4 (521016) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0914_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to CEDRDAL4 (520507) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CEDRDAL4 (520507) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0915_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TALOGA 4 (521065) 138 kV Bus to TALOGA 2 (521064) 69 kV Bus to TLGTERT (521178) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0916_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TALOGA 4 (521065) 138 kV Bus to DEWEY 4 (514787) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0917_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERT (521170) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0918_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERTB (521182) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0919_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0920_P1 | 3 phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOBHIL4 (514795) 138 kV Bus to KNOBHIL2 (514794) 69 kV Bus to KNOBHIL1 (515732) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0921_P1 | 3 phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV Bus to SPERVIL7 (531469) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763895 [G19-058-GEN20.6000]
04 - Southeast | 25S | Transfer | Group4_Fault_0922_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to NEWGRTP2 (514776) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0923_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0924_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to CEDARAV2 (514781) 69 kV Bus CKT 1 b. 2. Trip branch from CEDARAV2 (514781) 69 kV Bus to TANGRTP2 (514775) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CEDARAV2 (514781) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0925_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to SALTPLN4 (520437) 138 kV Bus CKT 1 b. 2. Trip branch from SALTPLN4 (520437) 138 kV Bus to CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 3. Trip branch from CHRKCTY4 (520431) 138 kV Bus to DRIFTWD4 (521200) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SALTPLN4 (520437) 138 kV Bus b. 5. Drop Load 2 at SALTPLN4 (520437) 138 kV Bus b. 6. Drop Load 1 at CHRKCTY4 (520431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0926_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to MORWOOD4 (521002) 138 kV Bus CKT 1 b. 2. Trip branch from MORWOOD4 (521002) 138 kV Bus to BRANTLEY4 (520832) 138 kV Bus CKT 1 b. 3. Trip branch from BRANTLEY4 (520832) 138 kV Bus to DURHAM 4 (520885) 138 kV Bus CKT 1 b. 4. Trip branch from DURHAM 4 (520885) 138 kV Bus to SWEETWR4 (521060) 138 kV Bus CKT 1 b. 5. Trip branch from SWEETWR4 (521060) 138 kV Bus to BULOJ4 (520402) 138 kV Bus CKT 1 b. 6. Trip branch from BULOJ4 (520402) 138 kV Bus to ERICK 4 (520903) 138 kV Bus CKT 1 b. 7. Trip branch from ERICK 4 (520903) 138 kV Bus to SAYRE--4 (511504) 138 kV Bus CKT 1 b. 8. Trip branch from SAYRE--4 (511504) 138 kV Bus to FALCNRD4 (511511) 138 kV Bus CKT 1 b. 9. Trip branch from FALCNRD4 (511511) 138 kV Bus to ELKCTY-4 (511458) 138 kV Bus CKT 1 b. 10. Drop Load 1 at BRANTLEY4 (520832) 138 kV Bus b. 11. Drop Load 1 at DURHAM 4 (520885) 138 kV Bus b. 12. Drop Load 1 at SWEETWR4 (521060) 138 kV Bus b. 13. Drop Load 1 at BULOJ4 (520402) 138 kV Bus b. 14. Drop Load 1 at ERICK 4 (520903) 138 kV Bus b. 15. Drop Load 1 at SAYRE--4 (511504) 138 kV Bus b. 16. Drop Load 1 at FALCNRD4 (511511) 138 kV Bus b. 17. Drop Shunt 1 at SAYRE--4 (511504) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0927_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to ELLIS 4 (511561) 138 kV Bus CKT 1 b. 2. Trip branch from ELLIS 4 (511561) 138 kV Bus to CUSTER 4 (520459) 138 kV Bus CKT 1 b. 3. Trip branch from CUSTER 4 (520459) 138 kV Bus to REDHLSW4 (521116) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ELLIS 4 (511561) 138 kV Bus b. 5. Drop Load 1 at CUSTER 4 (520459) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0928_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MORWODS4 (521001) 138 kV Bus to MORWODS2 (521000) 69 kV Bus to MRWDTERT (521172) 13.8 kV Bus CKT 1 b. 2. Trip branch from MORWODS2 (521000) 69 kV Bus to BTLRJCT2 (520457) 69 kV Bus CKT 1 b. 3. Trip branch from BTLRJCT2 (520457) 69 kV Bus to BUTLER 2 (520458) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0929_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to FARGOJCT2 (521196) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0930_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to VICI 2 (521082) 69 kV Bus CKT 1 b. 2. Trip branch from VICI 2 (521082) 69 kV Bus to TALOGA 2 (521064) 69 kV Bus CKT 1 b. 3. Drop Load 1 at VICI 2 (521082) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0931_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRIFTWD4 (521200) 138 kV Bus to DRIFTWD2 (521201) 69 kV Bus to DRFTWDTERT (521185) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0932_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138 kV Bus to BYRONTP4 (520432) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0933_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to CLEO PL4 (515553) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO PL4 (515553) 138 kV Bus b. 3. Drop Shunt 1 at CLEO PL4 (515553) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0934_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to MENOTAP4 (514789) 138 kV Bus CKT 1 b. 2. Trip branch from MENOTAP4 (514789) 138 kV Bus to IMO 4 (514790) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MENOTAP4 (514789) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0935_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0936_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to ALINE 2 (514793) 69 kV Bus CKT 1 b. 2. Drop Load 1 at ALINE 2 (514793) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0937_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to CLEOTP 2 (515804) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0938_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEOCOR2 (514777) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0939_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEO 2 (514791) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO 2 (514791) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0940_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTBJ2 (521202) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTBJ2 (521202) 69 kV Bus to MEDLDGE2 (522396) 69 kV Bus CKT 1 b. 3. Trip branch from MEDLDGE2 (522396) 69 kV Bus to HAZELTN2 (520937) 69 kV Bus CKT 1 b. 4. Drop Load 1 at MEDLDGE2 (522396) 69 kV Bus b. 5. Drop Load 1 at HAZELTN2 (520937) 69 kV Bus b. 6. Drop Shunt 1 at HAZELTN2 (520937) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0941_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTAJ2 (520938) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTAJ2 (520938) 69 kV Bus to BRLNGTN2 (520833) 69 kV Bus CKT 1 b. 3. Trip branch from BRLNGTN2 (520833) 69 kV Bus to CHEROKS2 (520851) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BRLNGTN2 (520833) 69 kV Bus b. 5. Drop Load 2K at BRLNGTN2 (520833) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0942_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to WILKINS4 (514950) 138 kV Bus CKT 1 b. 2. Trip branch from WILKINS4 (514950) 138 kV Bus to OAKTRET4 (514930) 138 kV Bus CKT 1 b. 3. Trip branch from OAKTRET4 (514930) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Drop Load 1 at WILKINS4 (514950) 138 kV Bus b. 5. Drop Load 1 at OAKTRET4 (514930) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0943_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to OUBROOK4 (514903) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OUBROOK4 (514903) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0944_P1 | 3 phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply Fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from QUAILCK4 (514851) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0945_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to WRAIRPT4 (514889) 138 kV Bus CKT 1 b. 2. Trip branch from WRAIRPT4 (514889) 138 kV Bus to 36&MER 4 (514888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WRAIRPT4 (514889) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0946_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to SANTAFE4 (514926) 138 kV Bus CKT 1 b. 2. Trip branch from SANTAFE4 (514926) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SANTAFE4 (514926) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0947_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENN 4 (514925) 138 kV Bus to PENN 2 (514924) 69 kV Bus to PENN 1 (515751) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0948_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to TUTCONT4 (511425) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0949_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to EL-RENO4 (514819) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0950_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0951_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to HAYMAKR4 (514863) 138 kV Bus CKT 1 b. 2. Trip branch from HAYMAKR4 (514863) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HAYMAKR4 (514863) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0952_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to SARA 4 (514895) 138 kV Bus CKT 1 b. 2. Trip branch from SARA 4 (514895) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SARA 4 (514895) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0953_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to CZECHAL4 (514894) 138 kV Bus CKT 1 b. 2. Trip branch from CZECHAL4 (514894) 138 kV Bus to XEROX 4 (514893) 138 kV Bus CKT 1 b. 3. Trip branch from XEROX 4 (514893) 138 kV Bus to MORGAN 4 (514896) 138 kV Bus CKT 1 b. 4. Trip branch from MORGAN 4 (514896) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 b. 5. Drop Load 1 at CZECHAL4 (514894) 138 kV Bus b. 6. Drop Load 1 at XEROX 4 (514893) 138 kV Bus b. 7. Drop Load 1 at MORGAN 4 (514896) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0954_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0955_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to PIEDMNT4 (514864) 138 kV Bus CKT 1 b. 2. Trip branch from PIEDMNT4 (514864) 138 kV Bus to RICHRDS4 (514862) 138 kV Bus CKT 1 b. 3. Trip branch from RICHRDS4 (514862) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PIEDMNT4 (514864) 138 kV Bus b. 5. Drop Load 1 at RICHRDS4 (514862) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0956_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to LNEOAK 4 (514873) 138 kV Bus CKT 1 b. 2. Trip branch from LNEOAK 4 (514873) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LNEOAK 4 (514873) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0957_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to HOLLYWD4 (514953) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0958_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0959_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to TURNER 4 (514992) 138 kV Bus CKT 1 b. 2. Trip branch from TURNER 4 (514992) 138 kV Bus to SOGATE 4 (514928) 138 kV Bus CKT 1 b. 3. Trip branch from SOGATE 4 (514928) 138 kV Bus to SW134TP4 (514876) 138 kV Bus CKT 1 b. 4. Drop Load 1 at TURNER 4 (514992) 138 kV Bus b. 5. Drop Load 1 at SOGATE 4 (514928) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0960_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to CHERYCK4 (514957) 138 kV Bus CKT 1 b. 2. Trip branch from CHERYCK4 (514957) 138 kV Bus to BOYD 4 (514958) 138 kV Bus CKT 1 b. 3. Trip branch from BOYD 4 (514958) 138 kV Bus to CEDARLN4 (514948) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHERYCK4 (514957) 138 kV Bus b. 5. Drop Load 1 at BOYD 4 (514958) 138 kV Bus b. 6. Drop Shunt 1 at BOYD 4 (514958) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0961_P1 | 3 phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDBUD 7 (514909) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0962_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0963_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to INDNHIL4 (514954) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0964_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to STUBMAN4 (514952) 138 kV Bus CKT 1 b. 2. Trip branch from STUBMAN4 (514952) 138 kV Bus to MLENIUM4 (514932) 138 kV Bus CKT 1 b. 3. Trip branch from MLENIUM4 (514932) 138 kV Bus to OU TAP 4 (514931) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STUBMAN4 (514952) 138 kV Bus b. 5. Drop Load 1 at MLENIUM4 (514932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0965_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0966_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to WESTHSE4 (514904) 138 kV Bus CKT 1 b. 2. Drop Load 1 at WESTHSE4 (514904) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0967_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to INDIANH4 (515380) 138 kV Bus CKT 1 b. 2. Trip branch from INDIANH4 (515380) 138 kV Bus to MOORE 4 (514955) 138 kV Bus CKT 1 b. 3. Trip branch from MOORE 4 (514955) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 4. Drop Load 1 at INDIANH4 (515380) 138 kV Bus b. 5. Drop Load 1 at MOORE 4 (514955) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0968_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0969_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to LAKESID4 (514849) 138 kV Bus CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV Bus to HEFNER 4 (514848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LAKESID4 (514849) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0970_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to G17-152_TAP (914902) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0971_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to WESTMOR4 (514887) 138 kV Bus CKT 1 b. 2. Trip branch from WESTMOR4 (514887) 138 kV Bus to PENN 4 (514925) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WESTMOR4 (514887) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0972_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to TUTTLE4 (511501) 138 kV Bus CKT 1 b. 2. Trip branch from TUTTLE4 (511501) 138 kV Bus to LEONARD4 (511575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at TUTTLE4 (511501) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0973_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to CEMRD_TP4 (511576) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25S | Transfer | Group4_Fault_0974_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to T-CONCO4 (511424) 138 kV Bus CKT 1 b. 2. Drop Load 1 at T-CONCO4 (511424) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0975_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to CMTRYRD4 (515864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CMTRYRD4 (515864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0976_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0977_P1 | 3 phase fault on JENSENT4 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JENSENT4 (514820) 138 kV Bus to JENSEN 4 (514821) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0978_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to OMEGA 4 (515962) 138 kV Bus CKT 1 b. 2. Trip branch from OMEGA 4 (515962) 138 kV Bus to ROMNOSE4 (514823) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OMEGA 4 (515962) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0979_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EL-RENO4 (514819) 138 kV Bus to ELRENO 2 (514818) 69 kV Bus to EL RENO1 (515722) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0980_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to JNSKAMO4 (514906) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0981_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to RNDBARN4 (515461) 138 kV Bus CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV Bus to BURGETT4 (514510) 138 kV Bus CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 b. 4. Drop Load 1 at RNDBARN4 (515461) 138 kV Bus b. 5. Drop Load 1 at BURGETT4 (514510) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0982_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to LGARBER4 (515465) 138 kV Bus CKT 1 b. 2. Trip branch from LGARBER4 (515465) 138 kV Bus to CHTWOOD4 (514842) 138 kV Bus CKT 1 b. 3. Trip branch from CHTWOOD4 (514842) 138 kV Bus to JONESSB4 (515480) 138 kV Bus CKT 1 b. 4. Drop Load 1 at LGARBER4 (515465) 138 kV Bus b. 5. Drop Load 1 at CHTWOOD4 (514842) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0983_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to BARNES 4 (515003) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0984_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0985_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0986_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to GM 4 (514961) 138 kV Bus CKT 1 b. 2. Trip branch from GM 4 (514961) 138 kV Bus to AIRDEPT4 (515457) 138 kV Bus CKT 1 b. 3. Trip branch from AIRDEPT4 (515457) 138 kV Bus to WILDMRY4 (514984) 138 kV Bus CKT 1 b. 4. Trip branch from WILDMRY4 (514984) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 5. Drop Load 1 at GM 4 (514961) 138 kV Bus b. 6. Drop Load 1 at AIRDEPT4 (515457) 138 kV Bus b. 7. Drop Load 1 at WILDMRY4 (514984) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_0987_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from R.S.S.-7 (509782) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0989_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T1 4 (509773) 138 kV Bus to RSST1 T1 (509882) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T1 4 (509773) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0990_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T2 4 (509875) 138 kV Bus to RSST2 T1 (509876) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T2 4 (509875) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0991_P1 | 3 phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply Fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FRNKLNS4 (520917) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0992_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to DAYTON 4 (514892) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0993_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to SW 5TH 4 (514920) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0994_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to COUNCIL4 (514865) 138 kV Bus CKT 1 b. 2. Trip branch from COUNCIL4 (514865) 138 kV Bus to WESTOAK4 (514866) 138 kV Bus CKT 1 b. 3. Trip branch from WESTOAK4 (514866) 138 kV Bus to MERIDAN4 (514867) 138 kV Bus CKT 1 b. 4. Trip branch from MERIDAN4 (514867) 138 kV Bus to DOUGLTP4 (514868) 138 kV Bus CKT 1 b. 5. Drop Load 1 at COUNCIL4 (514865) 138 kV Bus b. 6. Drop Load 1 at WESTOAK4 (514866) 138 kV Bus b. 7. Drop Load 1 at MERIDAN4 (514867) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0995_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MUSTANG4 (514861) 138 kV Bus to MSTANG 2 (514860) 69 kV Bus to MUSTANG1 (515740) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0996_P1 | 3 phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply Fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARAUTO2 (508576) 69 kV Bus to MARSHAL2 (508556) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0997_P1 | 3 phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply Fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JEFFRSN4 (508835) 138 kV Bus to LAKEPIN4 (509624) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0998_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to HARRISN4 (508544) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_0999_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to NMINEOL4 (508349) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1000_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to REDSPRW4 (508366) 138 kV Bus CKT 1 b. 2. Trip branch from REDSPRW4 (508366) 138 kV Bus to PECANHL4 (508365) 138 kV Bus CKT 1 b. 3. Trip branch from PECANHL4 (508365) 138 kV Bus to GARDVAL4 (508364) 138 kV Bus CKT 1 b. 4. Trip branch from GARDVAL4 (508364) 138 kV Bus to KENSULI4 (508363) 138 kV Bus CKT 1 b. 5. Trip branch from KENSULI4 (508363) 138 kV Bus to BENWHEL4 (508362) 138 kV Bus CKT 1 b. 6. Trip branch from BENWHEL4 (508362) 138 kV Bus to STARR 4 (508361) 138 kV Bus CKT 1 b. 7. Trip branch from STARR 4 (508361) 138 kV Bus to EBURGES4 (508360) 138 kV Bus CKT 1 b. 8. Trip branch from EBURGES4 (508360) 138 kV Bus to BURGEST4 (508357) 138 kV Bus CKT 1 b. 9. Drop Load 1 at REDSPRW4 (508366) 138 kV Bus b. 10. Drop Load 1 at PECANHL4 (508365) 138 kV Bus b. 11. Drop Load 1 at GARDVAL4 (508364) 138 kV Bus b. 12. Drop Load 1 at KENSULI4 (508363) 138 kV Bus b. 13. Drop Load 1 at BENWHEL4 (508362) 138 kV Bus b. 14. Drop Load 1 at STARR 4 (508361) 138 kV Bus b. 15. Drop Load 1 at EBURGES4 (508360) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1001_P1 | 3 phase fault on BURGEST4 (508357) 138 kV Bus a. Apply Fault at the BURGEST4 (508357) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BURGEST4 (508357) 138 kV Bus to MORTONST 4 (508373) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1002_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to (763010) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1003_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to SOTXEST4 (508570) 138 kV Bus CKT 1 b. 2. Trip branch from SOTXEST4 (508570) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SOTXEST4 (508570) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1004_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOXLEE4 (508548) 138 kV Bus to KNOXLEE2 (508547) 69 kV Bus to KXLEE-1 (508584) 12.47 kV Bus CKT 1 b. 2. Trip branch from KNOXLEE2 (508547) 69 kV Bus to SELONGV2 (508568) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1005_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN1-1 (509095) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1006_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN2-1 (509096) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1007_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to MONROCR2 (508558) 69 kV Bus CKT 1 b. 2. Trip branch from MONROCR2 (508558) 69 kV Bus to WHITNEY2 (508574) 69 kV Bus CKT 1 b. 3. Drop Load 1 at MONROCR2 (508558) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1008_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to HOWELL 2 (508545) 69 kV Bus CKT 1 b. 2. Trip branch from HOWELL 2 (508545) 69 kV Bus to SABINE 2 (508565) 69 kV Bus CKT 1 b. 3. Trip branch from SABINE 2 (508565) 69 kV Bus to SPIPETP2 (508573) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HOWELL 2 (508545) 69 kV Bus b. 5. Drop Load 1 at SABINE 2 (508565) 69 kV Bus b. 6. Drop Shunt 1 at HOWELL 2 (508545) 69 kV Bus1 b. 7. Drop Shunt 1 at SABINE 2 (508565) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1009_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON1-1 (509097) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1010_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to SVCPIPE2 (508578) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SVCPIPE2 (508578) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1011_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to CLARKSV2 (508540) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1012_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1013_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1014_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON2-1 (509098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1015_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1016_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1017_P1 | 3 phase fault on LIBCYTP4 (508550) 138 kV Bus a. Apply Fault at the LIBCYTP4 (508550) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIBCYTP4 (508550) 138 kV Bus to LIBCITY4 (508535) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LIBCITY4 (508535) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1018_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL1-1 (509090) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1019_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL2-1 (509091) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1020_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL4 (509083) 138 kV Bus to NEWPROS4 (509102) 138 kV Bus CKT 1 b. 2. Trip branch from NEWPROS4 (509102) 138 kV Bus to CARTPOD4 (509057) 138 kV Bus CKT 1 b. 3. Trip branch from CARTPOD4 (509057) 138 kV Bus to HULLTAP4 (509099) 138 kV Bus CKT 1 b. 4. Trip branch from HULLTAP4 (509099) 138 kV Bus to CARTHGT4 (509060) 138 kV Bus CKT 1 b. 5. Drop Load 1 at NEWPROS4 (509102) 138 kV Bus b. 6. Drop Load 1 at CARTPOD4 (509057) 138 kV Bus b. 7. Drop Load 1 at HULLTAP4 (509099) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1021_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to BIG3TAP2 (508539) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1022_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1023_P1 | 3 phase fault on G19-065-TAP (763010) kV Bus a. Apply Fault at the G19-065-TAP (763010) kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) kV Bus to LONDON 4 (509072) 138 kV Bus CKT 1 b. 2. Trip branch from LONDON 4 (509072) 138 kV Bus to FRIARSW4 (509062) 138 kV Bus CKT 1 b. 3. Trip branch from FRIARSW4 (509062) 138 kV Bus to FRIRSWR4 (509063) 138 kV Bus CKT 1 b. 4. Trip branch from FRIRSWR4 (509063) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LONDON 4 (509072) 138 kV Bus b. 6. Drop Load 1 at FRIARSW4 (509062) 138 kV Bus b. 7. Drop Load 1 at FRIRSWR4 (509063) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1024_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to EVENSID2 (509061) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1025_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1026_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1027_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to LEVERET4 (509069) 138 kV Bus CKT 1 b. 2. Trip branch from LEVERET4 (509069) 138 kV Bus to KILGORR4 (509067) 138 kV Bus CKT 1 b. 3. Trip branch from KILGORR4 (509067) 138 kV Bus to MONROER4 (509073) 138 kV Bus CKT 1 b. 4. Trip branch from MONROER4 (509073) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LEVERET4 (509069) 138 kV Bus b. 6. Drop Load 1 at KILGORR4 (509067) 138 kV Bus b. 7. Drop Load 1 at MONROER4 (509073) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1028_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1029_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVUE2 (508555) 69 kV Bus CKT 1 b. 2. Trip branch from LONGVUE2 (508555) 69 kV Bus to GATES 2 (508541) 69 kV Bus CKT 1 b. 3. Trip branch from GATES 2 (508541) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 b. 4. Drop Load 1 at LONGVUE2 (508555) 69 kV Bus b. 5. Drop Shunt 1 at LONGVUE2 (508555) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1030_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to KILGORE2 (508546) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1031_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1032_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1033_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to TURNERT2 (509089) 69 kV Bus CKT 1 b. 2. Drop Load 1 at TURNERT2 (509089) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1034_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to MURVAULTP (509048) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1035_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1036_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1037_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to ROSBORO2 (509085) 69 kV Bus CKT 1 b. 2. Trip branch from ROSBORO2 (509085) 69 kV Bus to BLOCKRT2 (509055) 69 kV Bus CKT 1 b. 3. Drop Load 1 at ROSBORO2 (509085) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1038_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to CARTHAG2 (509056) 69 kV Bus CKT 1 b. 2. Trip branch from CARTHAG2 (509056) 69 kV Bus to LAPACIF2 (509068) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CARTHAG2 (509056) 69 kV Bus b. 4. Drop Load 2 at CARTHAG2 (509056) 69 kV Bus b. 5. Drop Load 1 at LAPACIF2 (509068) 69 kV Bus b. 6. Drop Shunt 1 at CARTHAG2 (509056) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1039_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to BIG 3 2 (508537) 69 kV Bus CKT 1 b. 2. Drop Load 1 at BIG 3 2 (508537) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1040_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1041_P1 | 3 phase fault on LETOURT2 (508549) 69 kV Bus a. Apply Fault at the LETOURT2 (508549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LETOURT2 (508549) 69 kV Bus to LETOURN2 (508581) 69 kV Bus CKT 1 b. 2. Trip branch from LETOURN2 (508581) 69 kV Bus to LETRNST2 (508536) 69 kV Bus CKT 1 b. 3. Drop Load 1 at LETOURN2 (508581) 69 kV Bus b. 4. Drop Load 1 at LETRNST2 (508536) 69 kV Bus b. 5. Drop Shunt 1 at LETOURN2 (508581) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1042_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to FEARSCO2 (509086) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1043_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1044_P1 | 3 phase fault on POYNTER2 (509081) 69 kV Bus a. Apply Fault at the POYNTER2 (509081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POYNTER2 (509081) 69 kV Bus to HNDRSNR2 (509065) 69 kV Bus CKT 1 b. 2. Trip branch from HNDRSNR2 (509065) 69 kV Bus to BEARCATTP 2 (509127) 69 kV Bus CKT 1 b. 3. Trip branch from BEARCATTP 2 (509127) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HNDRSNR2 (509065) 69 kV Bus b. 5. Drop Load 1 at BEARCATTP 2 (509127) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1045_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4COLSTTA% (334021) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1046_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MT.ZION (334060) 138 kV Bus CKT 1 b. 2. Trip branch from 4MT.ZION (334060) 138 kV Bus to 4L558T485 (334058) 138 kV Bus CKT 1 b. 3. Drop Load BZ at 4MT.ZION (334060) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1047_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MAG AND (334025) 138 kV Bus CKT 1 b. 2. Trip branch from 4MAG AND (334025) 138 kV Bus to 4SOTA 1 (334024) 138 kV Bus CKT 1 b. 3. Trip branch from 4SOTA 1 (334024) 138 kV Bus to 4NAVSSPLT! (334019) 138 kV Bus CKT 1 b. 4. Drop Load BZ at 4SOTA 1 (334024) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1048_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4BENTWATER! (334039) 138 kV Bus CKT 1 b. 2. Trip branch from 4BENTWATER! (334039) 138 kV Bus to 4WALDEN (334040) 138 kV Bus CKT 1 b. 3. Trip branch from 4WALDEN (334040) 138 kV Bus to 4APRILTX (334041) 138 kV Bus CKT 1 b. 4. Trip branch from 4APRILTX (334041) 138 kV Bus to 4LFOREST (334042) 138 kV Bus CKT 1 b. 5. Trip branch from 4LFOREST (334042) 138 kV Bus to 4RABONCHAPEL (334049) 138 kV Bus CKT 1 b. 6. Trip branch from 4RABONCHAPEL (334049) 138 kV Bus to 4WDHAVN (334105) 138 kV Bus CKT 1 b. 7. Trip branch from 4WDHAVN (334105) 138 kV Bus to 4PONDEROSA% (334087) 138 kV Bus CKT 1 b. 8. Drop Load 1 at 4BENTWATER! (334039) 138 kV Bus b. 9. Drop Load 1 at 4WALDEN (334040) 138 kV Bus b. 10. Drop Load 1 at 4APRILTX (334041) 138 kV Bus b. 11. Drop Load BZ at 4LFOREST (334042) 138 kV Bus b. 12. Drop Load BZ at 4RABONCHAPEL (334049) 138 kV Bus b. 13. Drop Load BZ at 4WDHAVN (334105) 138 kV Bus b. 14. Drop Shunt 1 at 4BENTWATER! (334039) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1049_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4FISHCRK (334045) 138 kV Bus CKT 1 b. 2. Trip branch from 4FISHCRK (334045) 138 kV Bus to 4DEERLAKE (334048) 138 kV Bus CKT 1 b. 3. Trip branch from 4DEERLAKE (334048) 138 kV Bus to 4SPRINGBRNCH (334046) 138 kV Bus CKT 1 b. 4. Trip branch from 4SPRINGBRNCH (334046) 138 kV Bus to 4DOBBIN! (334044) 138 kV Bus CKT 1 b. 5. Trip branch from 4DOBBIN! (334044) 138 kV Bus to 4TUBULAR (334043) 138 kV Bus CKT 1 b. 6. Drop Load BZ at 4FISHCRK (334045) 138 kV Bus b. 7. Drop Load BZ at 4DEERLAKE (334048) 138 kV Bus b. 8. Drop Load BZ at 4SPRINGBRNCH (334046) 138 kV Bus b. 9. Drop Load 1 at 4DOBBIN! (334044) 138 kV Bus b. 10. Drop Load BZ at 4DOBBIN! (334044) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1050_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4LONGMIR! (334075) 138 kV Bus CKT 1 b. 2. Trip branch from 4LONGMIR! (334075) 138 kV Bus to 4PANORAM (334074) 138 kV Bus CKT 1 b. 3. Trip branch from 4PANORAM (334074) 138 kV Bus to 4EGYPT (334073) 138 kV Bus CKT 1 b. 4. Trip branch from 4EGYPT (334073) 138 kV Bus to 4LEWIS% (334072) 138 kV Bus CKT 1 b. 5. Drop Load 1 at 4LONGMIR! (334075) 138 kV Bus b. 6. Drop Load 1 at 4PANORAM (334074) 138 kV Bus b. 7. Drop Load 1 at 4EGYPT (334073) 138 kV Bus b. 8. Drop Shunt 1 at 4LONGMIR! (334075) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1051_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4CONROE1! (334104) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1052_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to GREGGTN2 (508542) 69 kV Bus CKT 1 b. 2. Trip branch from GREGGTN2 (508542) 69 kV Bus to NETTLTP2 (508559) 69 kV Bus CKT 1 b. 3. Drop Load 1 at GREGGTN2 (508542) 69 kV Bus b. 4. Drop Load 2 at GREGGTN2 (508542) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1053_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to AIRLINE2 (508538) 69 kV Bus CKT 1 b. 2. Trip branch from AIRLINE2 (508538) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 b. 3. Drop Load 1 at AIRLINE2 (508538) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1054_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1055_P4 | a. Apply single-phase fault on 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1056_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1060_P4 | a. Apply single-phase fault on T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 3. Disconnect BUS 513592 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1061_P4 | a. Apply single-phase fault on CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Disconnect BUS 512700 b. 4. Disconnect BUS 512818 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1062_P4 | a. Apply single-phase fault on MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Trip branch GRDA1 5 (512656) 161 kV Bus TO WMAIN ST5 (512742) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1063_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Trip branch from CLEVLND7 (512694) 345 kV Bus TO G15-066T (560056) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1064_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Disconnect bus CLEVLND1 (512817) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1065_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles: b. 2. Trip branch from CLEVLND7 (512694) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Trip three winding from CLEVLND7 (512694) 345 kV Bus TO CLEVLND 4 (512729) 138 kV Bus TO CLEVLND1 (512817) 13.8 kV CKT 1 b. 4. Clear fault at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1066_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1067_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1068_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1069_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1070_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1071_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GERALDGAY5 (512760) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1072_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1073_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1074_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1076_P4 | a. Apply single-phase fault at KERR GR5 (512635) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at KERR GR5 (512635) 161 kV Bus b. 3. Trip branch from KERR GR5 ( 512635 ) 161 kV Bus TO MAID 5 ( 512648 ) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1078_P4 | a. Apply single-phase fault at KETCHUM5 (512669) 161 kV Bus b. 1. Run for 15 cycles, Disconnect Bus 512632 b. 2. Clear fault at KETCHUM5 (512669) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 b. 4. Drop Load 1 Bus 512669 b. 5. Disconnect Bus 512669 b. 6. Disconnect Bus 512845 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1079_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1080_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1081_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1084_P4 | a. Apply single-phase fault at TONECE5 (512751) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from SILMCTY5 (512643) 161 kV Bus TO TONECE5 (512751) 161 kV Bus CKT 1 b. 2. Clear fault at TONECE5 (512751) 161 kV Bus b. 3. Disconnect Bus 512754 b. 4. Drop Load 1 Bus 512745 b. 5. Drop Load 1 Bus 512746 b. 6. Disconnect Bus 512728 b. 7. Disconnect Bus 512745 b. 8. Disconnect Bus 512746 b. 9. Disconnect Bus 512747 b. 10. Disconnect Bus 512756 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25S | Transfer | Group4_Fault_1085_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from FLINTCR7 (506935) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1086_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Disconnect Bus 512752 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1087_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1088_P4 | a. Apply single-phase fault at WINDFRM4 (515785) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WINDFRM4 (515785) 138 kV Bus TO MOORLND4 (520999) 138 kV Bus CKT 1 b. 3. Trip branch from WOODWRD4 (514785) 138 kV Bus TO WINDFRM4 (515785) 138 kV Bus CKT 1 b. 4. Clear fault at WINDFRM4 (515785) 138 kV Bus b. 5. Drop Generator 1 Bus 515895 b. 6. Drop Load S1 Bus 515787 b. 7. Disconnect Bus 515785 b. 8. Disconnect Bus 515786 b. 9. Disconnect Bus 515787 b. 10. Disconnect Bus 515790 b. 11. Disconnect Bus 515895 b. 12. Disconnect Bus 515896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1089_P4 | a. Apply single-phase fault at SUNNYSD7 (515136) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus TO SUNNYSD4 (515135) 138 kV TO SUNYSD 1 (515405) 13.8 kV CKT 1 b. 3. Disconnect Bus SUNYSD 1 (515405) 13.8 kV CKT 1 b. 4. Trip branch from SUNNYSD7 (515136) 345 kV Bus TO G16-063-TAP (560088) 138 kV Bus CKT 1 b. 5. Clear fault at SUNNYSD7 (515136) 345 kV Bus b. 6. Drop Shunt 1 Bus SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1090_P4 | a. Apply single-phase fault at DRAPER 4 (514933) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus 514946 b. 3. Trip branch from DRAPER 4 (514933) 138 kV Bus TO SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Clear fault at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1091_P4 | a. Apply single-phase fault at WAUKOTP4 (514711) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 3. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 4. Run for 10 cycles: b. 5. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO FAIRMON4 (514712) 138 kV Bus CKT 1 b. 6. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 7. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 8. Clear fault at WAUKOTP4 (514711) 138 kV Bus b. 9. Disconnect Bus WAUKOTP4 (514711) 138 kV b. 10. Disconnect Bus FRMNTAP4 (514709) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1092_P4 | a. Apply single-phase fault at JOHNCO 7 (514809) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO JOHNCO 7 (514809) 345 kV Bus CKT 1 b. 3. Trip branch from JOHNCO 7 (514809) 345 kV Bus TO SUNNYSD7 (515136) 345 kV Bus CKT 1 b. 4. Clear fault at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1093_P4 | a. Apply single-phase fault at GRACMNT7 (515800) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G16-091-TAP (587744) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 3. Trip branch from MINCO 7 (514801) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 4. Clear fault at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1095_P4 | a. Apply single-phase fault at PECANCK7 (515235) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO PECANCK7 (515235) 345 kV Bus CKT 1 b. 3. Disconnect Bus PECANC21 (515759) 13.8 kV b. 4. Clear fault at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1097_P4 | a. Apply single-phase fault at REDBUD 7 (514909) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from ARCADIA7 (514908) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 2 b. 3. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 4. Clear fault at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1098_P4 | a. Apply single-phase fault at FTSMITH8 (515305) 500 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus FTSMTH31 (515727) 13.8 kV b. 3. Trip branch from 8ANO% (337909) 500 kV Bus TO FTSMITH8 (515305) 500 kV Bus CKT 1 b. 4. Clear fault at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1099_P4 | a. Apply single-phase fault at SEMINOL7 (515045) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO SEMINOL7 (515045) 345 kV Bus CKT 1 b. 3. Disconnect Bus SEMINO21 (515757) 14.4 kV b. 4. Clear fault at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1100_P4 | a. Apply single-phase fault at SOONER 7 (514803) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G15-066T (560056) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Disconnect Bus SOONER 1 (515760) 13.8 kV b. 4. Clear fault at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1101_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1102_P4 | a. Apply single-phase fault at VBI 5 (515339) 161 kV Bus b. 1. Run for 23.52 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 2. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 3. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 4. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 5. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 6. Run for 11.28 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 7. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 8. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 9. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 10. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 11. Run for 1.62 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 12. Run for 9.18 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 13. Run for 4.02 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 14. Run for 4.2 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 15. Run for 2.4 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 16. Run for 0.18 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 17. Run for 2.82 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 18. Run for 6.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 19. Run for 1.44 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 20. Run for 19.38 cycles, Disconnect Bus VBI 1 (515769) 13.8 kV b. 21. Run for 23.82 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 22. Run for 18.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 23. Clear fault at bus VBI 5 (515339) 161 kV Bus b. 24. Drop Load A1 Bus 504191 b. 25. Drop Load A1 Bus 504192 b. 26. Drop Load 1 Bus 515332 b. 27. Drop Load A1 Bus 515332 b. 28. Drop Load A1 Bus 515333 b. 29. Drop Load 1 Bus 515334 b. 30. Drop Load A1 Bus 515337 b. 31. Drop Load A1 Bus 515340 b. 32. Drop Load 1 Bus 515341 b. 33. Drop Load A1 Bus 515346 b. 34. Drop Load 1 Bus 515350 b. 35. Drop Load 1 Bus 515351 b. 36. Drop Load 1 Bus 515360 b. 37. Drop Load 1 Bus 515406 b. 38. Disconnect Bus 504191 b. 39. Disconnect Bus 504192 b. 40. Disconnect Bus 515326 b. 41. Disconnect Bus 515329 b. 42. Disconnect Bus 515332 b. 43. Disconnect Bus 515333 b. 44. Disconnect Bus 515334 b. 45. Disconnect Bus 515337 b. 46. Disconnect Bus 515340 b. 47. Disconnect Bus 515341 b. 48. Disconnect Bus 515346 b. 49. Disconnect Bus 515348 b. 50. Disconnect Bus 515350 b. 51. Disconnect Bus 515351 b. 52. Disconnect Bus 515360 b. 53. Disconnect Bus 515406 b. 54. Disconnect Bus 515524 b. 55. Disconnect Bus 515527 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1103_P4 | a. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus b. 1. Run for 56.88 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 2. Run for 19.22 cycles, Disconnect Bus WOODWR21 (515771) 13.2 kV b. 3. Run for 0.66 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 4. Run for 49.74 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 b. 5. Run for 7.14 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 6. Clear fault at WODWRD 2 (514782) 69 kV Bus c. 1. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus c. 2. Run for 12.84 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 3. Run for 126.6 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 4. Clear fault at WODWRD 2 (514782) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1104_P4 | a. Apply single-phase fault at CTNWOOD4 (514827) 138 kV Bus b. 1. Run for 22 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 2. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 3. Run for 0.3 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 5. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 6. Run for 10.38 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 7. Run for 3.3 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 8. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 9. Run for 0.3 cycles, Trip CRESENT4 515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 10. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 11. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 12. Run for 9.3 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 13. Run for 1.08 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 14. Run for 5.34 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 15. Run for 7.92 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 16. Run for 0.6 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 17. Run for 3.48 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 18. Run for 0.6 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 19. Run for 0.96 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 20. Run for 19.8 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 21. Run for 37.8 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 22. Clear fault at CTNWOOD4 ( 514827 ) 138 kV Bus b. 23. Drop Load 1 Bus 514827 b. 24. Drop Load 1 Bus 514829 b. 25. Drop Load 2 Bus 514829 b. 26. Drop Load 1 Bus 514830 b. 27. Drop Load 1 Bus 514831 b. 28. Drop Load 1 Bus 515181 b. 29. Drop Load 1 Bus 515373 b. 30. Drop Load 1 Bus 515466 b. 31. Drop Load 1 Bus 515467 b. 32. Drop Load 1 Bus 521006 b. 33. Disconnect Bus 514733 b. 34. Disconnect Bus 514827 b. 35. Disconnect Bus 514828 b. 36. Disconnect Bus 514829 b. 37. Disconnect Bus 514830 b. 38. Disconnect Bus 514831 b. 39. Disconnect Bus 515008 b. 40. Disconnect Bus 515181 b. 41. Disconnect Bus 515373 b. 42. Disconnect Bus 515466 b. 43. Disconnect Bus 515467 b. 44. Disconnect Bus 521006 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1105_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV CB OR335 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1106_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip branch from RSVLT_CC_E 7 (527655) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1107_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB 4R00 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1108_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1109_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB J24 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1110_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1111_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV CB OR70 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1112_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R15 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1113_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt 1 HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1114_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R75 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1115_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV CB 4R240 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1117_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1118_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1119_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25S | Transfer | Group4_Fault_1120_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S105 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 3. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1121_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S110 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 4. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1122_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S120 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1123_P4 | a. Apply single phase fault at BATTLEFIELD5 (549959) 161 kV CB 111 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 3. Trip branch from MAIN STREET5 (549958) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1124_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1125_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV CB 2R05 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus BUFF_DUNES23 (523061) 0.69 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1126_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV CB PRE19S Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1128_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR05 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1129_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR20 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1130_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J17 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 3. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1131_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1132_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1133_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 4. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 5. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 6. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1134_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV Bus TO 5SOUTHLAND# (338814) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338125 b. 8. Drop Load A1 Bus 338813 b. 9. Drop Load A1 Bus 338814 b. 10. Disconnect Bus 338125 b. 11. Disconnect Bus 338606 b. 12. Disconnect Bus 338607 b. 13. Disconnect Bus 338608 b. 14. Disconnect Bus 338609 b. 15. Disconnect Bus 338813 b. 16. Disconnect Bus 338814 b. 17. Disconnect Bus 505462 b. 18. Disconnect Bus 505464 b. 19. Disconnect Bus 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1135_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 Cycles, Trip branch from Bus 5HARRISON.E! (338104) 161 kV To Bus 5SUMMIT (338121) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338121 b. 8. Drop Load 1 Bus 338122 b. 9. Drop Load 1 Bus 338124 b. 10. Disconnect Bus 338121 b. 11. Disconnect Bus 338122 b. 12. Disconnect Bus 338123 b. 13. Disconnect Bus 338124 b. 14. Disconnect Bus 505462 b. 15. Disconnect Bus 505464 b. 16. Disconnect Bus 505466 b. 17. Drop Load A1 Bus 338813 b. 18. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1136_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus 5MANSFDMN (300095) 161 kV To Bus 5GAINES (300081) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Disconnect Bus 505462 b. 8. Disconnect Bus 505464 b. 9. Disconnect Bus 505466 b. 10. Drop Load A1 Bus 338813 b. 11. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1137_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip branch from Bus BULL SH W5 (505461) 161 kV To Bus 5S.LEAD HILL (338120) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505473 b. 12. Disconnect Bus 505475 b. 13. Disconnect Bus 505476 b. 14. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1138_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus 5RENOHLWTP (300130) 161 kV To Bus 5RIVERSIDE (300805) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1139_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV Run For 5.0 Cycles, Open Line From Bus 5GRANDVIEW% (338099) 161 kV To Bus TABLE R5 (505472) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1140_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run For 5.0 Cycles, Open Line From Bus NIXA 5 (505496) 161 kV To Bus TABLE R5 (505472) 161 CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1141_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus RVS438 5 (547497) 161 kV To TABLE R5 (505472) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1142_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X1 1 (505473) 13.8 kV CKT 1 b. 2. Run For 12.0 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X2 1 (505475) 13.8 kV CKT 1 b. 3. Clear fault at TABLE R5 (505472) 161 kV b. 4. Disconnect Bus TBR X1 1 (505473) 13.8 kV b. 5. Drop Generator 1 Bus 505476 b. 6. Drop Generator 2 Bus 505476 b. 7. Drop Generator 3 Bus 505478 b. 8. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 9. Disconnect Bus 505475 b. 10. Disconnect Bus 505476 b. 11. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1143_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus TABLE R5 (505472) 161 kV To Bus 5CLEVCOV (300718) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505468 b. 12. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1144_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV To Bus BUFORD 5 (504440) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load A1 Bus 504440 b. 8. Disconnect Bus 504440 b. 9. Disconnect Bus 505468 b. 10. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1145_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus Run For 5 Cycles, Trip branch from Bus 5HILLTOP% (338110) 161 kV To Bus BULL SH W5 (505461) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Disconnect Bus 505468 b. 8. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1146_P4 | a. Apply single-phase fault at BATTLEFIELD2 (549979) 69 kV b. 1. Run for 8 cycles: b. 2. Trip branch from GOLDEN 2 (549911) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 3. Trip branch from DAYTON 2 (549913) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 4. Clear fault and run for 10 cycles, Trip branch from MAIN STREET5 (549958) 161 kV Bus TO BATTLEFIELD5 (549959) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1147_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1148_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1150_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1151_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1152_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1153_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1154_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1155_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1156_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1157_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1158_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1159_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1160_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1161_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1162_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1163_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_1164_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1165_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1167_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1168_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1169_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1170_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1171_P4 | a. Apply single-phase fault at WHEELER 6 (523777) 230 kV Bus b. 1. Run for 21.0 Cycles: b. 2. WHEELER 6 (523777) 230 kV Bus TO STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1172_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25S | Transfer | Group4_Fault_1173_P4 | a. Apply fault at bus HITCHLAND 7 (523097) 345 kV b. 1. Run for 5.0 cycles, Disconnect bus 523091 b. 2. Run for 11.0 cycles, Disconnect bus 523091 b. 3. Clear fault bus 523097 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1174_P4 | a. Apply Fault at Bus WHEELER 6 (523777) 230 kV b. 1. Run for 5 cycles, Disconnect Bus 523774 b. 2. Run for 11 cycles: b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1175_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1176_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus 524267 b. 4. Disconnect bus 524285 b. 5. Disconnect bus 524287 b. 6. Clear fault at bus 524267 b. 7. Disconnect Bus 524263 b. 8. Disconnect Bus 524275 b. 9. Disconnect Bus 524276 b. 10. Disconnect Bus 524289 b. 11. Disconnect Bus 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1177_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1178_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus TUCO_TR3 1 (525819) 13.2 kV b. 4. Clear fault at bus TUCO_INT 6 (525830) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1179_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1182_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1184_P4 | a. Apply single-phase fault at 531449 b. 1. Run For 12.0 Cycles, Open Line From Bus 531449 To Bus 531465 CKT 1 b. 2. Clear Fault Bus 531449 b. 3. Open Line From Bus 523853 To Bus 531449 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1185_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520864 To Bus 520900 CKT 1 b. 3. Open Line From Bus 520912 To Bus 520900 CKT 1 b. 4. Open Line From Bus 520923 To Bus 520912 CKT 1 b. 5. Run For 9.0 Cycles b. 6. Open Line From Bus 520814 To Bus 520422 CKT 1 b. 7. Open Line From Bus 520422 To Bus 520473 CKT 1 b. 8. Open Line From Bus 520473 To Bus 520867 CKT 1 b. 9. Open Line From Bus 520888 To Bus 520510 CKT 1 b. 10. Open Line From Bus 520867 To Bus 520510 CKT 1 b. 11. Clear Fault Bus 520814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1187_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles, Open Line From Bus 520814 To Bus 521129 CKT 1 b. 1. Clear fault and run For 9.0 Cycles, Open Line From Bus 511477 To Bus 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1188_P4 | a. Apply single-phase fault at 520917 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520400 To Bus 520842 CKT 1 b. 3. Run For 9.0 Cycles b. 4. Disconnect Bus 514946 b. 5. Open Line From Bus 520917 To Bus 520975 CKT 1 b. 6. Clear Fault Bus 520917 b. 7. Drop Load 1 Bus 520400 b. 8. Drop Load 1 Bus 520975 b. 9. Disconnect Bus 520400 b. 10. Disconnect Bus 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1189_P4 | a. Apply single-phase fault at 520920 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520920 To Bus 520922 CKT 1 b. 3. Drop Generator 1 Bus 521145 b. 4. Disconnect Bus 520922 b. 5. Disconnect Bus 521141 b. 6. Disconnect Bus 521144 b. 7. Disconnect Bus 521145 b. 8. Disconnect Bus 521151 b. 9. Run For 9.0 Cycles Print 0 Plot 3 Crtplt 0 b. 10. Open Line From Bus 520957 To Bus 520999 CKT 1 b. 11. Clear Fault Bus 520920 b. 12. Open Line From Bus 520920 To Bus 520957 CKT 1 b. 13. Drop Load 1 Bus 520957 b. 14. Disconnect Bus 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1190_P4 | a. Apply single-phase fault at 520948 b. 1. Run For 6.0 Cycles, Open Line From Bus 510887 To Bus 520968 CKT 1 b. 2. Run For 9.0 Cycles b. 3. Open Line From Bus 520948 To Bus 520918 CKT 1 b. 4. Open Line From Bus 505602 To Bus 521049 CKT 1 b. 5. Clear Fault Bus 520948 b. 6. Drop Load 1 Bus 515370 b. 7. Drop Load 1 Bus 515568 b. 8. Drop Load 1 Bus 520463 b. 9. Drop Load 1 Bus 520483 b. 10. Drop Load 1 Bus 520497 b. 11. Drop Load 1 Bus 520918 b. 12. Drop Load 1 Bus 521077 b. 13. Drop Load 1 Bus 521115 b. 14. Disconnect Bus 515370 b. 15. Disconnect Bus 515568 b. 16. Disconnect Bus 520463 b. 17. Disconnect Bus 520483 b. 18. Disconnect Bus 520497 b. 19. Disconnect Bus 520826 b. 20. Disconnect Bus 520884 b. 21. Disconnect Bus 520918 b. 22. Disconnect Bus 521049 b. 23. Disconnect Bus 521077 b. 24. Disconnect Bus 521098 b. 25. Disconnect Bus 521115 b. 26. Drop Load 1 Bus 520411 b. 27. Drop Load 1 Bus 520874 b. 28. Drop Load 1 Bus 520968 b. 29. Drop Load 1 Bus 521036 b. 30. Disconnect Bus 520411 b. 31. Disconnect Bus 520874 b. 32. Disconnect Bus 520968 b. 33. Disconnect Bus 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1192_P4 | a. Apply single-phase fault at MARIETA4 (520988) 138 kV CB 472 Stuck b. 1. Run for 6 cycles, Trip branch from CANEYCK4 (515150) 138 kV To Bus 521067 CKT 1 b. 2 Run For 9 cycles: b. 3. Trip branch from 5MARIETA4 (520988) 138 kV To Bus TEXOMAJ4 (521061)138 kV CKT 1 b. 4. Trip branch from 520981 To Bus 520939 CKT 1 b. 5. Clear Fault Bus 520988 b. 6. Drop Load 1 Bus 520455 b. 7. Drop Load 1 Bus 520487 b. 8. Drop Load 1 Bus 520488 b. 9. Drop Load 1 Bus 520511 b. 10. Drop Load 1 Bus 520901 b. 11. Drop Load 1 Bus 521038 b. 12. Drop Load 1 Bus 521061 b. 13. Drop Load 1 Bus 521066 b. 14. Disconnect Bus 520455 b. 15. Disconnect Bus 520467 b. 16. Disconnect Bus 520487 b. 17. Disconnect Bus 520488 b. 18. Disconnect Bus 520511 b. 19. Disconnect Bus 520901 b. 20. Disconnect Bus 520939 b. 21. Disconnect Bus 520972 b. 22. Disconnect Bus 521038 b. 23. Disconnect Bus 521061 b. 24. Disconnect Bus 521066 b. 25. Disconnect Bus 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1193_P4 | a. Apply single-phase fault at NOELSW 4 (520430) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DRIFTWD4 (521200) 138 kV Bus TO CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch from ROSEVLY4 (520436) 138 kV Bus TO NOELSW 4 (520430) 138 kV Bus CKT 1 b. 4. Trip branch from NOELSW 4 (520430) 138 kV Bus TO SALTPLN4 (520437) 138 kV Bus CKT 1 b. 5. Clear fault at NOELSW 4 (520430) 138 kV Bus b. 6. Drop Load 1 Bus 520431 b. 7. Drop Load 1 Bus 520437 b. 8. Drop Load 2 Bus 520437 b. 9. Disconnect Bus 520431 b. 10. Disconnect Bus 520437 b. 11. Drop Load 1 Bus 520436 b. 12. Drop Load 1 Bus 520601 b. 13. Disconnect Bus 520436 b. 14. Disconnect Bus 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1194_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DOVERSW4 (520882) 138 kV Bus TO OKEENE 4 (521016) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch MOORLND4 (520999) 138 kV Bus TO PIC4 (520425) 138 kV Bus CKT 1 Bus CKT 1 b. 3. Drop Load 1 Bus 520425 b. 4. Drop Load 1 Bus 520507 b. 5. Disconnect Bus 520425 b. 6. Disconnect Bus 520848 b. 7. Disconnect Bus 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1195_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1196_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch CLINTJC4 (511485) 138 kV Bus TO CLINTON4 (520856) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 3. Trip branch ONEY 4 (521017) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 4. Clear fault at WASHITA4 (521089) 138 kV Bus b. 5. Drop Load 1 Bus 520468 b. 6. Drop Load 1 Bus 520503 b. 7. Drop Load 1 Bus 520856 b. 8. Drop Load 1 Bus 520950 b. 9. Drop Load 1 Bus 521010 b. 10. Drop Load 2 Bus 521010 b. 11. Drop Load 1 Bus 521017 b. 12. Drop Load 1 Bus 521050 b. 13. Drop Load 1 Bus 521092 b. 14. Disconnect Bus 520468 b. 15. Disconnect Bus 520503 b. 16. Disconnect Bus 520827 b. 17. Disconnect Bus 520856 b. 18. Disconnect Bus 520950 b. 19. Disconnect Bus 521010 b. 20. Disconnect Bus 521017 b. 21. Disconnect Bus 521050 b. 22. Disconnect Bus 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1197_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1198_P4 | a. Apply single-phase fault at ANADARK4 (520814) 138 kV Bus b. 1. Run for 6 cycles: b. 2. Trip branch from COMANCH4 (520864) 138 kV Bus TO EMPIRE 4 (520900) kV 138 kV Bus CKT 1 b. 3. Trip Three winding transformer from FLETCH-4 (520912) 138 kV TO FLETCHR2 (520911) 69 kV TO FLCHTERT (521168) 13.8 kV CKT 1 b. 4. Run for 9 cycles: b. 5. Trip branch from SEQUOYAHJ4 (520422) 138 kV Bus TO ANADARK4 (520814) kV 138 kV Bus CKT 1 b. 6. Trip branch from PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) kV 138 kV Bus CKT 1 b. 7. Trip branch from CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 8. Clear fault at ANADARK4 (520814) 138 kV Bus b. 9. Drop Load 1 Bus 520547 b. 10. Drop Load 2 Bus 520547 b. 11. Drop Load 1a Bus 520604 b. 12. Disconnect Bus 520422 b. 13. Disconnect Bus 520510 b. 14. Disconnect Bus 520604 b. 15. Disconnect Bus 520867 b. 16. Disconnect Bus 520547 b. 17. Drop Load 1 Bus 520900 b. 18. Drop Load 1 Bus 520923 b. 19. Disconnect Bus 520900 b. 20. Disconnect Bus 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | Group4_Fault_1199_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520604 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0001_P4 | a. Apply SLG fault at SW SHV 7 (507760) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from SW SHV 7 (507760) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip SW SHV 7 (507760) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0002_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB #10610Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO NWTXARK7 (508072) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0003_P4 | a. Apply SLG fault at WELSH 7 (508359) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WELSH 7 (508359) 345 kV Bus TO DIANA 7 (508832) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0004_P4 | a. Apply single-phase fault at WILKES 7 (508841) 345 kV Bus CB #1W10 Stuck b. 1. Run for 5 cycles, Trip branch from WILKES 7 (508841) 345 kV Bus TO LONGWD 7 (508809) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip WILKES 7 (508841) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0005_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 11990 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO PIRKEY 7 (508563) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0006_P4 | a. Apply single-phase fault at DIANA 7 (508832) 345 kV Bus CB 1N60 Stuck b. 1. Run for 5 cycles, Trip branch from DIANA 7 (508832) 345 kV Bus TO WELSH 7 (508359) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip DIANA 7 (508832) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0007_P4 | a. Apply single-phase fault on ONETA--7 (509807) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from ONETA--7 (509807) 345 kV Bus TO R.S.S.-7 (509782) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip ONETA--7 (509807) 345 kV Bus TO CLARKSV7 (509745) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0008_P4 | a. Apply single-phase fault at R.S.S.-7 (509782) 345 kV Bus CB #3405A Stuck b. 1. Run for 5 cycles, Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip R.S.S.-7 (509782) 345 kV Bus TO SAPLPRD7 (509870) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0009_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10280 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO WILKES 7 (508841) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0010_P4 | a. Apply single-phase fault at LONGWD 7 (508809) 345 kV Bus CB 10500 Stuck b. 1. Run for 5 cycles, Trip branch from LONGWD 7 (508809) 345 kV Bus TO 7SAREPTA% (337376) 345 kV Bus CKT 1 b. 2. Clear Fault after 10 cycles and trip LONGWD 7 (508809) 345 kV Bus TO SW SHV 7 (507760) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0011_P4 | a. Apply single-phase fault at NEO SPA5 (505486) 161 kV Bus 16119 Stuck b. 1. Run for 5 cycles, Trip branch NEO SPA5 (505486) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 2. Run for 60 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 3. Run for 20 cycles, Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 4. Run for 3 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 5. Run for 37 cycles, Trip branch JOP389 5 (547483) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear Fault and run for 13 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 7. Drop Load 1 TIP292 5 (547472) 161 kV b. 8. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0012_P4 | a. Apply single-phase fault at ASB349 5 (547476) 161 kV Bus CB 16118 Stuck b. 1. Run for 5 cycles, Trip branch CAR395 5 (547485) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO PUR421 5 (547491) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 4. Clear fault and run for 15 cycles, Trip branch ASB349 5 (547476) 161 kV Bus TO CJ 366 5 (547477) 161 kV Bus CKT 1 b. 6. Drop Load 1 Bus CAR395 5 (547485) 161 kV b. 7. Drop Load 1 Bus PUR421 5 (547491) 161 kV b. 8. Disconnect Bus CAR395 5 (547485) 161 kV b. 9. Disconnect Bus PUR421 5 (547491) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0013_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO NEOSHO 5 (532937) 161 kV Bus CKT 1 b. 2. Run for 2 cycles, Trip branch NEOSHO 5 (532937) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 3. Run for 12 cycles, Trip branch HOC404 5 (547487) 161 kV Bus TO BAX488 5 (547729) 161 kV Bus CKT 1 b. 4. Clear fault after 86 cycles and Trip BAX488 5 (547729) 161 kV Bus TO HOC404 5 (547487) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0014_P4 | a. Apply single-phase fault on RIV4525 (547469) 161 kV Bus CB 161120 Stuck b. 1. Run for 5 cycles, Trip branch ORO110 5 (547467) 161 kV Bus TO RIV4525 (547469) 161 kV Bus CKT 1 b. 2. Run for 12 cycles, Trip branch RIV4525 (547469) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 b. 3. Clear fault after 98 cycles and Trip branch STL439 5 (547498) 161 kV Bus TO STL439 5 (547498) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0015_P4 | a. Apply single-phase fault on TIP292 5 (547472) 161 kV Bus CB 16110 Stuck b. 1. Run for 5 cycles, Trip branch TIP292 5 (547472) 161 kV Bus TO JOP389 5 (547483) 161 kV Bus CKT 1 b. 2. Run for 60 cycles: b. 3. Trip branch TIP292 5 (547472) 161 kV Bus TO NEO SPA5 (505486) 161 kV Bus CKT 1 b. 4. Trip branch NEO SPA5 (505486) 161 kV Bus TO CARTHAG5 (505488) 161 kV Bus CKT 1 b. 5. Run for 5 cycles, Trip branch RNM393 5 (547500) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 6. Clear fault and run for 15 cycles: b. 7. Trip branch MON383 5 (547480) 161 kV Bus TO TIP292 5 (547472) 161 kV Bus CKT 1 b. 8. Drop Load 1 Bus TIP292 5 (547472) 161 kV b. 9. Disconnect Bus TIP292 5 (547472) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0016_P4 | a. Apply single-phase fault on L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 1. Run for 5 cycles, Trip branch L1G382 1 (547651) 13.2 kV Bus TO LAR382 5 (547479) kV Bus CKT 1 b. 2. Run for 12 cycles, Trip LAR382 5 ( 547479 ) 161 kV Bus TO MON383 5 ( 547480 ) 345 kV Bus CKT 1 b. 3. Clear fault and run for 95 cycles: b. 4. Trip branch MON383 5 ( 547480 ) 161 kV Bus TO LAR382 5 ( 547479 ) 345 kV Bus CKT 1 b. 5. Drop GENERATOR 1 BUS 547651 b. 6. Drop LOAD S1 BUS 547651 b. 7. Disconnect BUS 547651 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0018_P4 | a. Apply single-phase fault on LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 1. Run for 15 cycles, Trip branch LEBROCK7 (508572) 345 kV Bus TO TENRUSK7 (508585) 345 kV Bus CKT 1 b. 2. Clear fault after 15 cycles and Trip LEBROCK7 ( 508572 ) 161 kV Bus TO TENRUSK7 ( 508585 ) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0019_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Disconnect BUS 532791 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0020_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WICHITA7 (532796) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0021_P4 | a. Apply single-phase fault on BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 4.75 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 12 cycles, Trip branch BENTON 7 (532791) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0022_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 13 cycles, Disconnect BUS 532831 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0023_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0024_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO ROSEHIL7 (532794) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0025_P4 | a. Apply single-phase fault on WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 c. Reclose the fault d. 1. Clear fault after 6.75 cycles: d. 2. Trip branch WOLFCRK7 (532797) 345 kV Bus TO BENTON 7 (532791) 345 kV Bus CKT 1 d. 3. Disconnect BUS 532962 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0026_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543641 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0027_P4 | a. Apply single-phase fault on CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 21 cycles: b. 2. Trip branch CRAIG 7 (542977) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 543643 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0028_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0029_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0030_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO WAVERLY7 (532799) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542955 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0031_P4 | a. Apply single-phase fault on LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch LACYGNE7 (542981) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 b. 3. Disconnect BUS 542956 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0032_P4 | a. Apply single-phase fault on PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch PECULR 7 (541198) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 b. 3. Trip branch LACYGNE7 (542981) 345 kV Bus TO STILWEL7 (542968) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0033_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO CRAIG 7 (542977) 345 kV Bus CKT 1 b. 3. Trip branch SWISVAL7 (532774) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0034_P4 | a. Apply single-phase fault on W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 1. Clear fault after 11 cycles: b. 2. Trip branch W.GRDNR7 (542965) 345 kV Bus TO LACYGNE7 (542981) 345 kV Bus CKT 1 b. 3. Trip branch STILWEL7 (542968) 345 kV Bus TO W.GRDNR7 (542965) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0035_P4 | a. Apply single-phase fault on ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 b. 1. Clear fault after 3.75 cycles, Disconnect BUS 532831 c. Reclose the fault d. 1. Clear fault after 13 cycles, Trip branch ROSEHIL7 (532794) 345 kV Bus TO WOLFCRK7 (532797) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0036_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONNEC2 (512753) 69 kV Bus to TONECESTR2 (512756) 69 kV Bus CKT 1 b. 2. Trip branch from TONECESTR2 (512756) 69 kV Bus to ARKLIN2 (512728) 69 kV Bus CKT 1 b. 3. Trip branch from ARKLIN2 (512728) 69 kV Bus to SSNEWN2 (512747) 69 kV Bus CKT 1 b. 4. Trip branch from SSNEWN2 (512747) 69 kV Bus to SSNORT2 (512746) 69 kV Bus CKT 1 b. 5. Trip branch from SSNORT2 (512746) 69 kV Bus to SSLINC2 (512745) 69 kV Bus CKT 1 b. 6. Drop Load 1 at SSNORT2 (512746) 69 kV Bus b. 7. Drop Load 1 at SSLINC2 (512745) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0037_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT2-1 (506920) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0038_P1 | 3 phase fault on SPRGFLD2 (505494) 69 kV Bus a. Apply Fault at the SPRGFLD2 (505494) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD2 (505494) 69 kV Bus to 2ELWOOD (300669) 69 kV Bus CKT 1 b. 2. Trip branch from 2ELWOOD (300669) 69 kV Bus to 2ASHGRV (300657) 69 kV Bus CKT 1 b. 3. Drop Load 1 at 2ELWOOD (300669) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0039_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 5 (549956) 161 kV Bus to NICHOLS 2 (549925) 69 kV Bus to NICHOL XF1 1 (549940) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0040_P1 | 3 phase fault on NICHOLS 5 (549956) 161 kV Bus a. Apply Fault at the NICHOLS 5 (549956) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 5 (549956) 161 kV Bus to WEST BELT 5 (549957) 161 kV Bus CKT 1 b. 2. Trip branch from WEST BELT 5 (549957) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 b. 3. Drop Load W at WEST BELT 5 (549957) 161 kV Bus b. 4. Drop Load E at WEST BELT 5 (549957) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0041_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 1 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0042_P1 | 3 phase fault on HERRON 5 (513591) 161 kV Bus a. Apply Fault at the HERRON 5 (513591) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HERRON 5 (513591) 161 kV Bus to CUSTDAY1 5 (513590) 161 kV Bus CKT 2 b. 2. Drop Load 1 at CUSTDAY1 5 (513590) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0043_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to GOLDEN 2 (549911) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0044_P1 | 3 phase fault on BATTLEFIELD2 (549979) 69 kV Bus a. Apply Fault at the BATTLEFIELD2 (549979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD2 (549979) 69 kV Bus to DAYTON 2 (549913) 69 kV Bus CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV Bus to FORT 2 (549914) 69 kV Bus CKT 1 b. 3. Trip branch from FORT 2 (549914) 69 kV Bus to SUNSET 2 (549907) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DAYTON 2 (549913) 69 kV Bus b. 5. Drop Load N at FORT 2 (549914) 69 kV Bus b. 6. Drop Load S at FORT 2 (549914) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0045_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to LAUREL 2 (549924) 69 kV Bus CKT 1 b. 2. Trip branch from LAUREL 2 (549924) 69 kV Bus to NICHOLS 2 (549925) 69 kV Bus CKT 1 b. 3. Drop Load N at LAUREL 2 (549924) 69 kV Bus b. 4. Drop Load S at LAUREL 2 (549924) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0046_P1 | 3 phase fault on GOLDEN 2 (549911) 69 kV Bus a. Apply Fault at the GOLDEN 2 (549911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV Bus to COX 2 (549910) 69 kV Bus CKT 1 b. 2. Trip branch from COX 2 (549910) 69 kV Bus to PLAINVIEW 2 (549905) 69 kV Bus CKT 1 b. 3. Trip branch from PLAINVIEW 2 (549905) 69 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus CKT 1 b. 4. Drop Load N at COX 2 (549910) 69 kV Bus b. 5. Drop Load S at COX 2 (549910) 69 kV Bus b. 6. Drop Load E at PLAINVIEW 2 (549905) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0047_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to NIC170 2 (547542) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0048_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0049_P1 | 3 phase fault on NICHOLS 2 (549925) 69 kV Bus a. Apply Fault at the NICHOLS 2 (549925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 2 (549925) 69 kV Bus to FRISCO 2 (549926) 69 kV Bus CKT 1 b. 2. Trip branch from FRISCO 2 (549926) 69 kV Bus to N HWY13 2 (549927) 69 kV Bus CKT 1 b. 3. Trip branch from N HWY13 2 (549927) 69 kV Bus to NORTON 2 (549928) 69 kV Bus CKT 1 b. 4. Drop Load N at FRISCO 2 (549926) 69 kV Bus b. 5. Drop Load S at FRISCO 2 (549926) 69 kV Bus b. 6. Drop Load E at N HWY13 2 (549927) 69 kV Bus b. 7. Drop Load W at N HWY13 2 (549927) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0050_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to SED 80 2 (547529) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0051_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to NIX114 2 (547535) 69 kV Bus CKT 1 b. 2. Trip branch from NIX114 2 (547535) 69 kV Bus to BHJ415 2 (547604) 69 kV Bus CKT 1 b. 3. Drop Load 1 at NIX114 2 (547535) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0052_P1 | 3 phase fault on NIC170 2 (547542) 69 kV Bus a. Apply Fault at the NIC170 2 (547542) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIC170 2 (547542) 69 kV Bus to REP345 2 (547576) 69 kV Bus CKT 1 b. 2. Trip branch from REP345 2 (547576) 69 kV Bus to REP451 2 (547443) 69 kV Bus CKT 1 b. 3. Trip branch from REP451 2 (547443) 69 kV Bus to REP359 2 (547580) 69 kV Bus CKT 1 b. 4. Trip branch from REP359 2 (547580) 69 kV Bus to BIL221 2 (547546) 69 kV Bus CKT 1 b. 5. Drop Load 1 at REP345 2 (547576) 69 kV Bus b. 6. Drop Load 1 at REP451 2 (547443) 69 kV Bus b. 7. Drop Load 1 at REP359 2 (547580) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0053_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to SILSPWW5 (512642) 161 kV Bus CKT 1 b. 2. Trip branch from SILSPWW5 (512642) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 b. 3. Drop Load 1 at SILSPWW5 (512642) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0054_P1 | 3 phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply Fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR5 (506944) 161 kV Bus to WEDINGTON (506992) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0055_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to WEDINGTON5 (504275) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0056_P1 | 3 phase fault on WEDINGTON (506992) 161 kV Bus a. Apply Fault at the WEDINGTON (506992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEDINGTON (506992) 161 kV Bus to FARMNGTN 5 (504020) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0058_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 7HUBEN (300042) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25W | Transfer | Group4_Fault_0059_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to GENTRY 5 (504201) 161 kV Bus CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV Bus to BEN279_5 (506960) 161 kV Bus CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV Bus to GREENHOUSE 5 (506990) 161 kV Bus CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 5. Drop Load A1 at GENTRY 5 (504201) 161 kV Bus b. 6. Drop Load 1 at BEN279_5 (506960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0061_P1 | 3 phase fault on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7MORGAN (300045) 345 kV Bus to 5MORGANXF2 (301622) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 999925 [GI85-GEN1 0.6450], 999927 [GI85-ESS1 0.6450], 999935 [GI85-GEN2 0.6450], 999937 [GI85-ESS2 0.6450], 999945 [GI85-GEN3 0.6450], 999947 [GI85-ESS3 0.6450]
04 - Southeast | 25W | Transfer | Group4_Fault_0062_P1 | 3 phase fault on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGANXF2 (301622) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0063_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0064_P1 | 3 phase fault on EROGERS5 (506931) 161 kV Bus a. Apply Fault at the EROGERS5 (506931) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EROGERS5 (506931) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0065_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYESS1-1 (506914) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0066_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES2-1 (506915) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0067_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DYESS 5 (506927) 161 kV Bus to DYESS 2 (506926) 69 kV Bus to DYES3-1 (506916) 13.2 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0068_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to CARLEYRD 5 (504274) 161 kV Bus CKT 1 b. 2. Trip branch from CARLEYRD 5 (504274) 161 kV Bus to VANASCH5 (506939) 161 kV Bus CKT 1 b. 3. Trip branch from VANASCH5 (506939) 161 kV Bus to GREGGST5 (506983) 161 kV Bus CKT 1 b. 4. Trip branch from GREGGST5 (506983) 161 kV Bus to FAYETVL5 (506933) 161 kV Bus CKT 1 b. 5. Trip branch from FAYETVL5 (506933) 161 kV Bus to SFAYTVL5 (506947) 161 kV Bus CKT 1 b. 6. Drop Load A1 at CARLEYRD 5 (504274) 161 kV Bus b. 7. Drop Load 1 at VANASCH5 (506939) 161 kV Bus b. 8. Drop Load 1 at GREGGST5 (506983) 161 kV Bus b. 9. Drop Load 1 at FAYETVL5 (506933) 161 kV Bus b. 10. Drop Shunt 1 at VANASCH5 (506939) 161 kV Bus1 b. 11. Drop Shunt 1 at FAYETVL5 (506933) 161 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0069_P1 | 3 phase fault on DYESS 5 (506927) 161 kV Bus a. Apply Fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DYESS 5 (506927) 161 kV Bus to SOSPRDL5 (506949) 161 kV Bus CKT 1 b. 2. Trip branch from SOSPRDL5 (506949) 161 kV Bus to OSBURN (506985) 161 kV Bus CKT 1 b. 3. Trip branch from OSBURN (506985) 161 kV Bus to EFAYETVL 5 (504015) 161 kV Bus CKT 1 b. 4. Drop Load 1 at SOSPRDL5 (506949) 161 kV Bus b. 5. Drop Load 1 at OSBURN (506985) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0070_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to DEC392 5 (547484) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0071_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to GROVE 5 (510411) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0072_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOL435 5 (547496) 161 kV Bus to NEO184 5 (547471) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0073_P1 | 3 phase fault on NOL435 5 (547496) 161 kV Bus a. Apply Fault at the NOL435 5 (547496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NOL435 5 (547496) 161 kV Bus to NOL435 2 (547610) 69 kV Bus to NOL435 1 (547720) 12.5 kV Bus CKT 1 b. 2. Drop Shunt 1 at NOL435 1 (547720) 12.5 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0074_P1 | 3 phase fault on 5SPORTSMAN (300741) 161 kV Bus a. Apply Fault at the 5SPORTSMAN (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5SPORTSMAN (300741) 161 kV Bus to 5CHOTEAU2 (301348) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0075_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR1 (512814) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0076_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 2 (512679) 69 kV Bus to CLARMR2 (512815) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0077_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLARMR 5 (512651) 161 kV Bus to 5KETONVL (300997) 161 kV Bus CKT 1 b. 2. Trip branch from 5KETONVL (300997) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5KETONVL (300997) 161 kV Bus b. 4. Drop Load 1 at 5KETONVL (300997) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0078_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WAGNOR 5 (512700) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0079_P1 | 3 phase fault on WAGNOR 5 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WAGNOR 5 (512700) 161 kV Bus to WAGNOR 2 (512697) 69 kV Bus to WAGNOR1 (512818) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0080_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to STOCKTN5 (505498) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0081_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to TONTITN5 (506957) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0082_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to DAD368 5 (547478) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0083_P1 | 3 phase fault on 5MORGAN (300101) 161 kV Bus a. Apply Fault at the 5MORGAN (300101) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5MORGAN (300101) 161 kV Bus to 2MORGAN (300782) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0084_P1 | 3 phase fault on SSSWTP2 (512737) 69 kV Bus a. Apply Fault at the SSSWTP2 (512737) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SSMOSS2 (512744) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0085_P1 | 3 phase fault on 5CHOTEAU2 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 (301348) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CHOTEAU2 (301348) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0086_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 b. 2. Drop Load 1 at DRYGULCH5 (512629) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0087_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0088_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to 412SUB 5 (512637) 161 kV Bus CKT 1 b. 2. Trip branch from 412SUB 5 (512637) 161 kV Bus to KANSATP5 (512714) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 412SUB 5 (512637) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0089_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK1 5 (512770) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0090_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to KERR BRK4 5 (512771) 161 kV Bus CKT Z0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0091_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0092_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAMSP 5 (504202) 161 kV Bus CKT 1 b. 2. Trip branch from SILOAMSP 5 (504202) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 b. 3. Drop Load A1 at SILOAMSP 5 (504202) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0093_P1 | 3 phase fault on KERR GR5 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KERR GR5 (512635) 161 kV Bus to SALNCRK5 (512805) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0094_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER1 1 (512833) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0095_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CATSAGR5 (512638) 161 kV Bus to CATOOSA4 (509790) 138 kV Bus to CATTER2 1 (512834) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0096_P1 | 3 phase fault on CATSAGR5 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CATSAGR5 (512638) 161 kV Bus to 5ELMCRK (300993) 161 kV Bus CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV Bus to COLINS 5 (512627) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5ELMCRK (300993) 161 kV Bus b. 4. Drop Load 2 at 5ELMCRK (300993) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0097_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NIXA 5 (505496) 161 kV Bus to TABLE R5 (505472) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0098_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X2 1 (505499) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0099_P1 | 3 phase fault on NIXA 5 (505496) 161 kV Bus a. Apply Fault at the NIXA 5 (505496) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NIXA 5 (505496) 161 kV Bus to NIXA 2 (505501) 69 kV Bus to NXA X1 1 (505497) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0100_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to CARTHAG5 (505488) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0101_P1 | 3 phase fault on LAR382 5 (547479) 161 kV Bus a. Apply Fault at the LAR382 5 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAR382 5 (547479) 161 kV Bus to MON383 5 (547480) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0102_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MILL 5 (549962) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0103_P1 | 3 phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR5 (506934) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0104_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to MENTOR 5 (549963) 161 kV Bus CKT 1 b. 2. Trip branch from MENTOR 5 (549963) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 b. 3. Drop Load S at MENTOR 5 (549963) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0105_P1 | 3 phase fault on CLAY 5 (549970) 161 kV Bus a. Apply Fault at the CLAY 5 (549970) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLAY 5 (549970) 161 kV Bus to 5LOGAN (301161) 161 kV Bus CKT 1 b. 2. Trip branch from 5LOGAN (301161) 161 kV Bus to 5MANSFDMN (300095) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5LOGAN (301161) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0106_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JRPS 69B-2 2 (549903) 69 kV Bus to JRPS XF2 1 (549945) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0107_P1 | 3 phase fault on JAMES RIVER5 (549961) 161 kV Bus a. Apply Fault at the JAMES RIVER5 (549961) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JAMES RIVER5 (549961) 161 kV Bus to JAMES RIVER2 (549904) 69 kV Bus to JRPS XF1 1 (549944) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0108_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF1 1 (549936) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0109_P1 | 3 phase fault on MAIN STREET5 (549958) 161 kV Bus a. Apply Fault at the MAIN STREET5 (549958) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAIN STREET5 (549958) 161 kV Bus to MAIN STREET2 (549921) 69 kV Bus to MAINST XF2 1 (549938) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0110_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to MC CARTNEY 5 (549968) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0111_P1 | 3 phase fault on SUMMIT 5 (549966) 161 kV Bus a. Apply Fault at the SUMMIT 5 (549966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUMMIT 5 (549966) 161 kV Bus to NORTON 5 (549967) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0112_P1 | 3 phase fault on KANSATP5 (512714) 161 kV Bus a. Apply Fault at the KANSATP5 (512714) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSATP5 (512714) 161 kV Bus to KANSAS 5 (512716) 161 kV Bus CKT 1 b. 2. Trip three winding transformer from KANSAS 5 (512716) 161 kV Bus to KANSAS 2 (512715) 69 kV Bus to KANSAS1 (512736) 13.8 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0113_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2KANSASTP (301637) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0114_P1 | 3 phase fault on SHIPERD5 (506980) 161 kV Bus a. Apply Fault at the SHIPERD5 (506980) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHIPERD5 (506980) 161 kV Bus to CENTRTN5 (506952) 161 kV Bus CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV Bus to ECNTRTN5 (506929) 161 kV Bus CKT 1 b. 3. Drop Load 1 at CENTRTN5 (506952) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0115_P1 | 3 phase fault on KANSAS 2 (512715) 69 kV Bus a. Apply Fault at the KANSAS 2 (512715) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KANSAS 2 (512715) 69 kV Bus to 2WATTS (300987) 69 kV Bus CKT 1 b. 2. Trip branch from 2WATTS (300987) 69 kV Bus to 2WESTVIL (300988) 69 kV Bus CKT 1 b. 3. Trip branch from 2WESTVIL (300988) 69 kV Bus to 2BALDOR (300980) 69 kV Bus CKT 1 b. 4. Trip branch from 2BALDOR (300980) 69 kV Bus to STLWLGR2 (512721) 69 kV Bus CKT 1 b. 5. Drop Load 1 at 2WATTS (300987) 69 kV Bus b. 6. Drop Load 1 at 2WESTVIL (300988) 69 kV Bus b. 7. Drop Load 2 at 2WESTVIL (300988) 69 kV Bus b. 8. Drop Load 1 at 2BALDOR (300980) 69 kV Bus b. 9. Drop Shunt 1 at 2WESTVIL (300988) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0116_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2KANSASKM (301638) 69 kV Bus CKT 1 b. 2. Drop Load 2 at 2KANSASKM (301638) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0117_P1 | 3 phase fault on 2KANSASTP (301637) 69 kV Bus a. Apply Fault at the 2KANSASTP (301637) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2KANSASTP (301637) 69 kV Bus to 2COLCOTP (301458) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0118_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY5 (512643) 161 kV Bus to SILOAM 5 (506948) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0119_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY1 1 (512849) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0120_P1 | 3 phase fault on TONNEC2 (512753) 69 kV Bus a. Apply Fault at the TONNEC2 (512753) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE5 (512751) 161 kV Bus to TONNEC2 (512753) 69 kV Bus to TONNEC1 (512754) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0121_P1 | 3 phase fault on SILMCTY5 (512643) 161 kV Bus a. Apply Fault at the SILMCTY5 (512643) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILMCTY5 (512643) 161 kV Bus to SILMCTY2 (512820) 69 kV Bus to SLMCTY2 1 (512850) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0122_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA1 (512821) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRDA1 (512821) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0123_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 7 (512650) 345 kV Bus to GRDA1 5 (512656) 161 kV Bus to GRDA2 1 (512826) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRDA2 1 (512826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0124_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0125_P1 | 3 phase fault on GRDA1 7 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 7 (512650) 345 kV Bus to GREC TAP5 (512865) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0126_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF1 1 (549988) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0127_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BROOKLINE 7 (549984) 345 kV Bus to BROOKLINE 5 (549969) 161 kV Bus to BRKLNE XF2 1 (549989) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0128_P1 | 3 phase fault on BROOKLINE 7 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7 (549984) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 7 (549984) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0129_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 5 (506948) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0130_P1 | 3 phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply Fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SILOAM 5 (506948) 161 kV Bus to SILOAM 2 (506973) 69 kV Bus to SILOAM-1 (506917) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0131_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONECE5 (512751) 161 kV Bus to SILMCTY5 (512643) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0132_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONTITN7 (506959) 345 kV Bus to TONTITN5 (506957) 161 kV Bus to TONTITN1 (506958) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0133_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to CHAMSPR5 (506944) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0134_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEC392 5 (547484) 161 kV Bus to DEC392 2 (547594) 69 kV Bus to DEC392 1 (547714) 12.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0135_P1 | 3 phase fault on DEC392 5 (547484) 161 kV Bus a. Apply Fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 5 (547484) 161 kV Bus to NOL435 5 (547496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0136_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWES2 (512730) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0137_P1 | 3 phase fault on SILMCTY2 (512820) 69 kV Bus a. Apply Fault at the SILMCTY2 (512820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILMCTY2 (512820) 69 kV Bus to SSSWTP2 (512737) 69 kV Bus CKT 1 b. 2. Trip branch from SSSWTP2 (512737) 69 kV Bus to SSMOSS2 (512744) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0138_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0139_P1 | 3 phase fault on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7SPORTSMAN (300740) 345 kV Bus to 5SPORTSMAN (300741) 161 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0140_P1 | 3 phase fault on GREC TAP5 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GREC TAP5 (512865) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0141_P1 | 3 phase fault on TONECE5 (512751) 161 kV Bus a. Apply Fault at the TONECE5 (512751) 161 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TONECE7 (512750) 345 kV Bus to TONECE5 (512751) 161 kV Bus to TONECE1 (512752) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_0142_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0143_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to CLARMR 5 (512651) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0144_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WAGNOR 5 (512700) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0145_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to WMAIN ST5 (512742) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0146_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRDA1 5 (512656) 161 kV Bus to GRDA1 2 (512727) 69 kV Bus to GRDA1 1 (512816) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0147_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to 5MORGAN (300101) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0148_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to SPRGFLD5 (505492) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0149_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JTEC 5 (549954) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0150_P1 | 3 phase fault on BROOKLINE 5 (549969) 161 kV Bus a. Apply Fault at the BROOKLINE 5 (549969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV Bus to JUNCTION 5 (549955) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0151_P1 | 3 phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply Fault at the SILOAM 2 (506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SILOAM 2 (506973) 69 kV Bus to LINCOLN2 (506972) 69 kV Bus CKT 1 b. 2. Trip branch from LINCOLN2 (506972) 69 kV Bus to PRGROVE2 (506941) 69 kV Bus CKT 1 b. 3. Trip branch from PRGROVE2 (506941) 69 kV Bus to GREENLD2 (506936) 69 kV Bus CKT 1 b. 4. Drop Shunt 1 at SILOAM 2 (506973) 69 kV Bus1 b. 5. Drop Load A1 at LINCOLN2 (506972) 69 kV Bus b. 6. Drop Load 1 at PRGROVE2 (506941) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0152_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to GRDA1 7 (512650) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0153_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to ELMSPRGS 5 (504010) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0154_P1 | 3 phase fault on TONTITN5 (506957) 161 kV Bus a. Apply Fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN5 (506957) 161 kV Bus to BRUSHCRK_5 (506991) 161 kV Bus CKT 1 b. 2. Trip branch from BRUSHCRK_5 (506991) 161 kV Bus to LOWELL 5 (506938) 161 kV Bus CKT 1 b. 3. Trip branch from LOWELL 5 (506938) 161 kV Bus to ROGERS 5 (506942) 161 kV Bus CKT 1 b. 4. Trip branch from ROGERS 5 (506942) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 5. Drop Load 1 at BRUSHCRK_5 (506991) 161 kV Bus b. 6. Drop Load 1 at LOWELL 5 (506938) 161 kV Bus b. 7. Drop Load 1 at ROGERS 5 (506942) 161 kV Bus b. 8. Drop Shunt 1 at ROGERS 5 (506942) 161 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0155_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELMSPRGS 5 (504010) 161 kV Bus to DYESS 5 (506927) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0156_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_1 2 (504011) 69 kV Bus to ELMSP_T1 1 (504012) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ELMSPG_1 2 (504011) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0157_P1 | 3 phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply Fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELMSPRGS 5 (504010) 161 kV Bus to ELMSPG_2 2 (504013) 69 kV Bus to ELMSP_T2 1 (504014) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0158_P1 | 3 phase fault on TONTITN7 (506959) 345 kV Bus a. Apply Fault at the TONTITN7 (506959) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONTITN7 (506959) 345 kV Bus to CHAMSPR7 (506945) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0159_P1 | 3 phase fault on DEC392 2 (547594) 69 kV Bus a. Apply Fault at the DEC392 2 (547594) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEC392 2 (547594) 69 kV Bus to DEC467 2 (547569) 69 kV Bus CKT 1 b. 2. Trip branch from DEC467 2 (547569) 69 kV Bus to GRA700 2 (547617) 69 kV Bus CKT 1 b. 3. Trip branch from GRA700 2 (547617) 69 kV Bus to NOL435 2 (547610) 69 kV Bus CKT 1 b. 4. Drop Load 1 at DEC467 2 (547569) 69 kV Bus b. 5. Drop Load 1 at GRA700 2 (547617) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0160_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_1 2 (504006) 69 kV Bus to ECENT_T1 1 (504007) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ECENT_1 2 (504006) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0161_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECENT_2 2 (504008) 69 kV Bus to ECENT_T2 1 (504009) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0162_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR2-1 (506924) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0163_P1 | 3 phase fault on TONECE7 (512750) 345 kV Bus a. Apply Fault at the TONECE7 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TONECE7 (512750) 345 kV Bus to FLINTCR7 (506935) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0164_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ECNTRTN5 (506929) 161 kV Bus to ECNTRTN2 (506928) 69 kV Bus to ECNTR1-1 (506923) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0165_P1 | 3 phase fault on ECNTRTN5 (506929) 161 kV Bus a. Apply Fault at the ECNTRTN5 (506929) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV Bus to BENT_SL5 (506963) 161 kV Bus CKT 1 b. 2. Trip branch from BENT_SL5 (506963) 161 kV Bus to BENTVJ_5 (506962) 161 kV Bus CKT 1 b. 3. Trip branch from BENTVJ_5 (506962) 161 kV Bus to BENT ML5 (506955) 161 kV Bus CKT 1 b. 4. Trip branch from BENT ML5 (506955) 161 kV Bus to WROGERS 5 (504200) 161 kV Bus CKT 1 b. 5. Trip branch from WROGERS 5 (504200) 161 kV Bus to EROGERS5 (506931) 161 kV Bus CKT 1 b. 6. Drop Load 1 at BENT_SL5 (506963) 161 kV Bus b. 7. Drop Load 1 at BENTVJ_5 (506962) 161 kV Bus b. 8. Drop Load 1 at BENT ML5 (506955) 161 kV Bus b. 9. Drop Load A1 at WROGERS 5 (504200) 161 kV Bus b. 10. Drop Load A2 at WROGERS 5 (504200) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0166_P1 | 3 phase fault on ECNTRTN2 (506928) 69 kV Bus a. Apply Fault at the ECNTRTN2 (506928) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ECNTRTN2 (506928) 69 kV Bus to BENTNVL2 (506965) 69 kV Bus CKT 1 b. 2. Trip branch from BENTNVL2 (506965) 69 kV Bus to DIXLAND2 (506925) 69 kV Bus CKT 1 b. 3. Trip branch from DIXLAND2 (506925) 69 kV Bus to NROGERS2 (506940) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BENTNVL2 (506965) 69 kV Bus b. 5. Drop Load 1 at DIXLAND2 (506925) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0167_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV1 5 (513593) 161 kV Bus to IGLOTER1 1 (513592) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0168_P1 | 3 phase fault on IGLOOV 7 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from IGLOOV 7 (513596) 345 kV Bus to IGLOOV2 5 (513595) 161 kV Bus to IGLOTER2 1 (513594) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0169_P1 | 3 phase fault on GRDA1 5 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 5 (512656) 161 kV Bus to MAID 5 (512648) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0170_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to 5CHOTEAU1 (300069) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0171_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0172_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to KERR GR5 (512635) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0173_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to BROOKLINE 7 (549984) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0174_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0175_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to CATSAGR5 (512638) 161 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0176_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to LOCSTGVKM 5 (513050) 161 kV Bus CKT 1 b. 2. Trip branch from LOCSTGVKM 5 (513050) 161 kV Bus to 5CDRCRST (301344) 161 kV Bus CKT 1 b. 3. Drop Load 1 at LOCSTGVKM 5 (513050) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0177_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER1 1 (512836) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0178_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MAID 5 (512648) 161 kV Bus to MAID 2 (512626) 69 kV Bus to MAITER2 1 (512837) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0179_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to DRYGULCH5 (512629) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0180_P1 | 3 phase fault on MAID 5 (512648) 161 kV Bus a. Apply Fault at the MAID 5 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 5 (512648) 161 kV Bus to GERALDGAY5 (512760) 161 kV Bus CKT 1 b. 2. Trip branch from GERALDGAY5 (512760) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 b. 3. Drop Load 1 at GERALDGAY5 (512760) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0181_P1 | 3 phase fault on WMAIN ST5 (512742) 161 kV Bus a. Apply Fault at the WMAIN ST5 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WMAIN ST5 (512742) 161 kV Bus to NWMAID5 (512757) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0182_P1 | 3 phase fault on GRDA1 2 (512727) 69 kV Bus a. Apply Fault at the GRDA1 2 (512727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRDA1 2 (512727) 69 kV Bus to MAIDTP2 (512625) 69 kV Bus CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0183_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to NIXA 5 (505496) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0184_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FLINTCR7 (506935) 345 kV Bus to SHIPERD7 (506979) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0185_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0186_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to CLAY 5 (549970) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0187_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to 5NIXA-1 (300678) 161 kV Bus CKT 1 b. 2. Trip branch from 5NIXA-1 (300678) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5NIXA-1 (300678) 161 kV Bus b. 4. Drop Load 2 at 5NIXA-1 (300678) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0188_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X1 1 (505491) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0189_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X2 1 (505493) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0190_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SPRGFLD5 (505492) 161 kV Bus to SPRGFLD2 (505494) 69 kV Bus to SPF X3 1 (505495) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0191_P1 | 3 phase fault on SPRGFLD5 (505492) 161 kV Bus a. Apply Fault at the SPRGFLD5 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV Bus to LAR382 5 (547479) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0192_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to JAMES RIVER5 (549961) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0193_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to 5BTLFD (300348) 161 kV Bus CKT 1 b. 2. Trip branch from 5BTLFD (300348) 161 kV Bus to 5JAMESV (300089) 161 kV Bus CKT 1 b. 3. Drop Load 1 at 5BTLFD (300348) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0194_P1 | 3 phase fault on JTEC 5 (549954) 161 kV Bus a. Apply Fault at the JTEC 5 (549954) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JTEC 5 (549954) 161 kV Bus to SW DISP PLT5 (549960) 161 kV Bus CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV Bus to BATTLEFIELD5 (549959) 161 kV Bus CKT 1 b. 3. Drop Load W at SW DISP PLT5 (549960) 161 kV Bus b. 4. Drop Load E at SW DISP PLT5 (549960) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0195_P1 | 3 phase fault on FLINTCR7 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLINTCR7 (506935) 345 kV Bus to FLINTCR5 (506934) 161 kV Bus to FLINT1-1 (506921) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0196_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to NICHOLS 5 (549956) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0197_P1 | 3 phase fault on JUNCTION 5 (549955) 161 kV Bus a. Apply Fault at the JUNCTION 5 (549955) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JUNCTION 5 (549955) 161 kV Bus to PIC WEST 5 (549971) 161 kV Bus CKT 1 b. 2. Trip branch from PIC WEST 5 (549971) 161 kV Bus to SUMMIT 5 (549966) 161 kV Bus CKT 1 b. 3. Drop Load S at PIC WEST 5 (549971) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0198_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAMSPR7 (506945) 345 kV Bus to CHAMSPR5 (506944) 161 kV Bus to CHAMSPR1 (506919) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0199_P1 | 3 phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply Fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHAMSPR7 (506945) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0200_P1 | 3 phase fault on IGLOOV1 5 (513593) 161 kV Bus a. Apply Fault at the IGLOOV1 5 (513593) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV1 5 (513593) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0201_P1 | 3 phase fault on IGLOOV2 5 (513595) 161 kV Bus a. Apply Fault at the IGLOOV2 5 (513595) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from IGLOOV2 5 (513595) 161 kV Bus to HERRON 5 (513591) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0202_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to REDDEN 2 (512698) 69 kV Bus CKT 1 b. 2. Trip branch from REDDEN 2 (512698) 69 kV Bus to CASTING TAP2 (512685) 69 kV Bus CKT 1 b. 3. Trip branch from CASTING TAP2 (512685) 69 kV Bus to AMERCAST N2 (512683) 69 kV Bus CKT 1 b. 4. Drop Load 1 at REDDEN 2 (512698) 69 kV Bus b. 5. Drop Load 1 at AMERCAST N2 (512683) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0203_P1 | 3 phase fault on MAID 2 (512626) 69 kV Bus a. Apply Fault at the MAID 2 (512626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MAID 2 (512626) 69 kV Bus to AMERCAST S2 (512681) 69 kV Bus CKT 1 b. 2. Trip branch from AMERCAST S2 (512681) 69 kV Bus to CPPTAP 2 (512661) 69 kV Bus CKT 1 b. 3. Trip branch from CPPTAP 2 (512661) 69 kV Bus to PRYORCHEM2 (512699) 69 kV Bus CKT 1 b. 4. Trip branch from PRYORCHEM2 (512699) 69 kV Bus to AIRPROD2 (512687) 69 kV Bus CKT 1 b. 5. Trip branch from AIRPROD2 (512687) 69 kV Bus to HUNT 2 (512671) 69 kV Bus CKT 1 b. 6. Drop Load 1 at AMERCAST S2 (512681) 69 kV Bus b. 7. Drop Load 1 at PRYORCHEM2 (512699) 69 kV Bus b. 8. Drop Load 1 at AIRPROD2 (512687) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0204_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BATTLEFIELD5 (549959) 161 kV Bus to MAIN STREET5 (549958) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0205_P1 | 3 phase fault on BATTLEFIELD5 (549959) 161 kV Bus a. Apply Fault at the BATTLEFIELD5 (549959) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BATTLEFIELD5 (549959) 161 kV Bus to BATTLEFIELD2 (549979) 69 kV Bus to BATLEFLDXF11 (549980) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0206_P4 | a. Apply single phase fault at FLINTCR7 (506935) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR7 (506935) 345 kV to TONECE7 (512750) 345 kV CKT 1 b. 2. Trip branch from FLINTCR7 (506935) 345 kV to SHIPERD7 (506979) 345 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from SHIPERD5 (506980) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 5. Trip branch from CENTRTN5 (506952) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 6. Drop Load 1 CENTRTN5 (506952) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0207_P4 | a. Apply single phase fault at SILMCTY5 (512643) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SILMCTY5 (512643) 161 kV to SILOAM 5 (506948) 161 kV CKT 1 b. 2. Trip branch from SILMCTY5 (512643) 161 kV to SILSPWW5 (512642) 161 kV CKT 1 b. 3. Trip branch from SILSPWW5 (512642) 161 kV to KANSATP5 (512714) 161 kV CKT 1 b. 4. Drop Load 1 SILSPWW5 (512642) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0208_P4 | a. Apply single phase fault at FLINTCR5 (506934) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLINTCR5 (506934) 161 kV to GENTRY 5 (504201) 161 kV CKT 1 b. 2. Trip branch from GENTRY 5 (504201) 161 kV to BEN279_5 (506960) 161 kV CKT 1 b. 3. Trip branch from BEN279_5 (506960) 161 kV to GREENHOUSE 5 (506990) 161 kV CKT 1 b. 4. Trip branch from GREENHOUSE 5 (506990) 161 kV to ECNTRTN5 (506929) 161 kV CKT 1 b. 5. Trip branch from FLINTCR5 (506934) 161 kV to TONTITN5 (506957) 161 kV CKT 1 b. 6. Drop Load A1 GENTRY 5 (504201) 161 kV b. 7. Drop Load 1 BEN279_5 (506960) 161 kV b. 8. Drop Load 1 GREENHOUSE 5 (506990) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0210_P4 | a. Apply single phase fault at BROOKLINE 5 (549969) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BROOKLINE 5 (549969) 161 kV to SPRGFLD5 (505492) 161 kV CKT 1 b. 2. Trip branch from BROOKLINE 5 (549969) 161 kV to JUNCTION 5 (549955) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0211_P4 | a. Apply single phase fault at TAHLQH 5 (512655) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TAHLQH 5 (512655) 161 kV to 5CDRCRST (301344) 161 kV CKT 1 b. 2. Trip branch from TAHLQH 5 (512655) 161 kV to 7CLANS 5 (515956) 161 kV CKT 1 b. 3. Trip branch from 7CLANS 5 (515956) 161 kV to KETOWAH5 (516027) 161 kV CKT 1 b. 4. Trip branch from KETOWAH5 (516027) 161 kV to MUSKOGE5 (515222) 161 kV CKT 1 b. 5. Drop Load 1 SILSPWW5 (512642) 161 kV b. 6. Drop Load 1 7CLANS 5 (515956) 161 kV b. 7. Drop Load 1 KETOWAH5 (516027) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0212_P4 | a. Apply single phase fault at CHAMSPR5 (506944) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CHAMSPR5 (506944) 161 kV to CHAMSPR7 (506945) kV to CHAMSPR1 (506919) 13.8 kV CKT1 b. 2. Trip branch from CHAMSPR5 (506944) 161 kV to TONTITN5 (506957) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0213_P4 | a. Apply single phase fault at ECNTRTN5 (506929) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ECNTRTN5 (506929) 161 kV to CENTRTN5 (506952) 161 kV CKT 1 b. 2. Trip branch from CENTRTN5 (506952) 161 kV to SHIPERD5 (506980) 161 kV CKT 1 b. 3. Trip three winding transformer from SHIPERD7 (506979) 345 kV to SHIPERD5 (506980) kV to SHIPERD1 (506981) 13.8 kV CKT1 b. 4. Trip branch from ECNTRTN5 (506929) 161 kV to BENT_SL5 (506963) 161 kV CKT 1 b. 5. Trip branch from BENT_SL5 (506963) 161 kV to BENTVJ_5 (506962) 161 kV CKT 1 b. 6. Trip branch from BENTVJ_5 (506962) 161 kV to BENT ML5 (506955) 161 kV CKT 1 b. 7. Trip branch from BENT ML5 (506955) 161 kV to WROGERS 5 (504200) 161 kV CKT 1 b. 8. Trip branch from WROGERS 5 (504200) 161 kV to EROGERS5 (506931) 161 kV CKT 1 b. 9. Drop Load 1 CENTRTN5 (506952) 161 kV b. 10. Drop Load 1 BENT_SL5 (506963) 161 kV b. 11. Drop Load 1 BENTVJ_5 (506962) 161 kV b. 12. Drop Load 1 BENT ML5 (506955) 161 kV b. 13. Drop Load A1 WROGERS 5 (504200) 161 kV b. 14. Drop Load A2 WROGERS 5 (504200) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0214_P4 | a. Apply single phase fault at STLWLGR2 (512721) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from STLWLGR2 (512721) 69 kV to STIWEL5 (512704) kV to STLWELL1 (512819) 13.8 kV CKT1 b. 2. Trip branch from STIWEL5 (512704) 161 kV to BRIGSKM 5 (513044) 161 kV CKT 1 b. 3. Trip branch from STLWLGR2 (512721) 69 kV to STILWELLCTY2 (512701) 69 kV CKT 1 b. 4. Drop Load 1 STILWELLCTY2 (512701) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0215_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to SOONER 7 (514803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0216_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MILLERT4 (514704) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0217_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to LBRTYLK4 (515373) 138 kV Bus CKT 1 b. 2. Trip branch from LBRTYLK4 (515373) 138 kV Bus to WATRLOO4 (514831) 138 kV Bus CKT 1 b. 3. Trip branch from WATRLOO4 (514831) 138 kV Bus to WHITESB4 (515467) 138 kV Bus CKT 1 b. 4. Trip branch from WHITESB4 (515467) 138 kV Bus to MITCHSB4 (515466) 138 kV Bus CKT 1 b. 5. Trip branch from MITCHSB4 (515466) 138 kV Bus to KETCHTP4 (514828) 138 kV Bus CKT 1 b. 6. Drop Load 1 at LBRTYLK4 (515373) 138 kV Bus b. 7. Drop Load 1 at WATRLOO4 (514831) 138 kV Bus b. 8. Drop Load 1 at WHITESB4 (515467) 138 kV Bus b. 9. Drop Load 1 at MITCHSB4 (515466) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0218_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to NORTWST4 (514879) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0219_P1 | 3 phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply Fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCHTP4 (514828) 138 kV Bus to KETCH 4 (514834) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0220_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0221_P1 | 3 phase fault on KETCH 4 (514834) 138 kV Bus a. Apply Fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KETCH 4 (514834) 138 kV Bus to FAIRFLD4 (515468) 138 kV Bus CKT 1 b. 2. Trip branch from FAIRFLD4 (515468) 138 kV Bus to CHISHOM4 (515374) 138 kV Bus CKT 1 b. 3. Trip branch from CHISHOM4 (515374) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FAIRFLD4 (515468) 138 kV Bus b. 5. Drop Load 1 at CHISHOM4 (515374) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0222_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to PERRY 4 (514707) 138 kV Bus CKT 1 b. 2. Trip branch from PERRY 4 (514707) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0223_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to SNRPMPT4 (514798) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0224_P1 | 3 phase fault on SOONER 4 (514802) 138 kV Bus a. Apply Fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 4 (514802) 138 kV Bus to MORISNT4 (515447) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0225_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-7 (509755) 345 kV Bus to SAPLPRD7 (509870) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0226_P1 | 3 phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV Bus to WEKIWA-4 (509757) 138 kV Bus to WEKIW1-1 (509879) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0227_P1 | 3 phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply Fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PINTAIL7 (516010) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0228_P1 | 3 phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply Fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-119-TAP (587804) 345 kV Bus to SPRNGCK7 (514881) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0229_P1 | 3 phase fault on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-052T (560053) 345 kV Bus to ROSEHIL7 (532794) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0230_P1 | 3 phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply Fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RANCHRD7 (515576) 345 kV Bus to OPENSKY7 (515621) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0231_P1 | 3 phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEVLND7 (512694) 345 kV Bus to CLEVLND 4 (512729) 138 kV Bus to CLEVLND1 (512817) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0232_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to DMNCRKT4 (515412) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0233_P1 | 3 phase fault on MILLERT4 (514704) 138 kV Bus a. Apply Fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MILLERT4 (514704) 138 kV Bus to OTOETAP4 (515978) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0234_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to OSAGE 4 (514743) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0235_P1 | 3 phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply Fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SNRPMPT4 (514798) 138 kV Bus to SNRPMP 4 (514799) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SNRPMP 4 (514799) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0236_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to STILWTR4 (515011) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0237_P1 | 3 phase fault on MORISNT4 (515447) 138 kV Bus a. Apply Fault at the MORISNT4 (515447) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORISNT4 (515447) 138 kV Bus to MORRISN4 (515006) 138 kV Bus CKT 1 b. 2. Trip branch from MORRISN4 (515006) 138 kV Bus to COWCRK 4 (514706) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0238_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SHEFFD-4 (509812) 138 kV Bus CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV Bus to S.S.---4 (509815) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHEFFD-4 (509812) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0239_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to WED-TAP4 (509823) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0240_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to P&P WTP4 (509851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0241_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0242_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to SILVCTYGR4 (512726) 138 kV Bus CKT 1 b. 2. Trip branch from SILVCTYGR4 (512726) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0243_P1 | 3 phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply Fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WEKIWA-4 (509757) 138 kV Bus to KEYSTON4 (505610) 138 kV Bus CKT 1 b. 2. Trip branch from KEYSTON4 (505610) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0244_P1 | 3 phase fault on CLEVLND 4 (512729) 138 kV Bus a. Apply Fault at the CLEVLND 4 (512729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEVLND 4 (512729) 138 kV Bus to 4CLEVLND (300138) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0245_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to PAWNSW4 (512749) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0246_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4SILVCTY (300140) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0247_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 4JAVINE (300996) 138 kV Bus CKT 1 b. 2. Trip branch from 4JAVINE (300996) 138 kV Bus to 4SFORKKTP (301339) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0248_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0249_P1 | 3 phase fault on 4CLEVLND (300138) 138 kV Bus a. Apply Fault at the 4CLEVLND (300138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4CLEVLND (300138) 138 kV Bus to 2CLEVLND (300927) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0250_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD7 (509870) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0251_P1 | 3 phase fault on SAPLPRD7 (509870) 345 kV Bus a. Apply Fault at the SAPLPRD7 (509870) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SAPLPRD7 (509870) 345 kV Bus to SAPLPRD4 (509871) 138 kV Bus to SAPLPRD1 (509872) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0252_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G15-066T (560056) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0254_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to HUNTERS7 (515476) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0255_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG7 (514715) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0256_P1 | 3 phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV Bus to WOODRNG4 (514714) 138 kV Bus to WOODRNG1 (515770) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0257_P1 | 3 phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply Fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPRNGCK7 (514881) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0258_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0259_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0260_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ROSEHIL7 (532794) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0261_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH1 1 (532826) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH1 1 (532826) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0262_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH5 1 (532827) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH5 1 (532827) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0263_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to PINTAIL7 (516010) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0264_P1 | 3 phase fault on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROSEHIL7 (532794) 345 kV Bus to ROSEHIL4 (533062) 138 kV Bus to ROSEH3 1 (532831) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ROSEH3 1 (532831) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0265_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0266_P1 | 3 phase fault on DMNCRKT4 (515412) 138 kV Bus a. Apply Fault at the DMNCRKT4 (515412) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DMNCRKT4 (515412) 138 kV Bus to DMANCRK4 (515400) 138 kV Bus CKT 1 b. 2. Drop Load 1 at DMANCRK4 (515400) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0267_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to 4REDRCK (301011) 138 kV Bus CKT 1 b. 2. Drop Load 1 at 4REDRCK (301011) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0268_P1 | 3 phase fault on OTOETAP4 (515978) 138 kV Bus a. Apply Fault at the OTOETAP4 (515978) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OTOETAP4 (515978) 138 kV Bus to OTOE 4 (514737) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OTOE 4 (514737) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0269_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COWCRK 4 (514706) 138 kV Bus to WRVALLY4 (514713) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0270_P1 | 3 phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply Fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COWCRK 4 (514706) 138 kV Bus to COWCRK 2 (514705) 69 kV Bus to COWCRK 1 (515717) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0271_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WHEAGLE4 (514761) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0272_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to WEBBTAP4 (510376) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0273_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to MARLNDT4 (514770) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0274_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SOONER 7 (514803) 345 kV Bus to G16-119-TAP (587804) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0275_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 31 (515744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0276_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OSAGE 4 (514743) 138 kV Bus to OSGE 2 (514742) 69 kV Bus to OSAGE 41 (515745) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0277_P1 | 3 phase fault on OSAGE 4 (514743) 138 kV Bus a. Apply Fault at the OSAGE 4 (514743) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OSAGE 4 (514743) 138 kV Bus to STDBEAR4 (514758) 138 kV Bus CKT 1 b. 2. Trip branch from STDBEAR4 (514758) 138 kV Bus to CONORTH4 (514753) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0278_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to SPGVLLY4 (515574) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0279_P1 | 3 phase fault on STILWTR4 (515011) 138 kV Bus a. Apply Fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from STILWTR4 (515011) 138 kV Bus to MCELROY4 (515009) 138 kV Bus CKT 1 b. 2. Trip branch from MCELROY4 (515009) 138 kV Bus to UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 3. Trip branch from UNVRSTY4 (515181) 138 kV Bus to KINZE 4 (515008) 138 kV Bus CKT 1 b. 4. Drop Load 1 at MCELROY4 (515009) 138 kV Bus b. 5. Drop Load 1 at UNVRSTY4 (515181) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0280_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to PP----W4 (509805) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0281_P1 | 3 phase fault on P&P WTP4 (509851) 138 kV Bus a. Apply Fault at the P&P WTP4 (509851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from P&P WTP4 (509851) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0282_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0283_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4BRISTOW (300137) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0284_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 4FISHERTP (300131) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0285_P1 | 3 phase fault on SOONER 7 (514803) 345 kV Bus a. Apply Fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SOONER 7 (514803) 345 kV Bus to SOONER 4 (514802) 138 kV Bus to SOONER 1 (515760) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0286_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0287_P1 | 3 phase fault on 4SILVCTY (300140) 138 kV Bus a. Apply Fault at the 4SILVCTY (300140) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4SILVCTY (300140) 138 kV Bus to 2SILVCTY (300943) 69 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0288_P1 | 3 phase fault on 2CLEVLND (300927) 69 kV Bus a. Apply Fault at the 2CLEVLND (300927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 2CLEVLND (300927) 69 kV Bus to OSAGEK2 (512876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0289_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to 4FAIRFAX (300139) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0290_P1 | 3 phase fault on PAWNSW4 (512749) 138 kV Bus a. Apply Fault at the PAWNSW4 (512749) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PAWNSW4 (512749) 138 kV Bus to GLENCOKM 4 (513095) 138 kV Bus CKT 1 b. 2. Trip branch from GLENCOKM 4 (513095) 138 kV Bus to 4STILWTR (300141) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLENCOKM 4 (513095) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0291_P1 | 3 phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply Fault at the T.NO.2-4 (509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.2-4 (509895) 138 kV Bus to T.NO.--4 (509817) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0292_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0293_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to DENV_WTAP4 (509896) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0294_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to OAKSWTP4 (509848) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0295_P1 | 3 phase fault on OPENSKY7 (515621) 345 kV Bus a. Apply Fault at the OPENSKY7 (515621) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from OPENSKY7 (515621) 345 kV Bus to G15-052T (560053) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0296_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to 72ELWOD4 (509888) 138 kV Bus CKT 1 b. 2. Trip branch from 72ELWOD4 (509888) 138 kV Bus to T.P.S.-4 (509788) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 72ELWOD4 (509888) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0297_P1 | 3 phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply Fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAPLPRD4 (509871) 138 kV Bus to JENKS--4 (509759) 138 kV Bus CKT 1 b. 2. Trip branch from JENKS--4 (509759) 138 kV Bus to 116JENK4 (509753) 138 kV Bus CKT 1 b. 3. Trip branch from 116JENK4 (509753) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 b. 4. Drop Load 1 at JENKS--4 (509759) 138 kV Bus b. 5. Drop Load 1 at 116JENK4 (509753) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0298_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to OTTER 4 (514708) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0299_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to FRMNTAP4 (514709) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0300_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to WAUKOTP4 (514711) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0301_P1 | 3 phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply Fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODRNG4 (514714) 138 kV Bus to MARSHL 4 (514733) 138 kV Bus CKT 1 b. 2. Trip branch from MARSHL 4 (514733) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 3. Trip branch from MARSHL 4 (514733) 138 kV Bus to MARSHAL4 (521006) 138 kV Bus CKT Z1 b. 4. Drop Load 1 at MARSHAL4 (521006) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0302_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0303_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST7 (514880) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0304_P1 | 3 phase fault on G15-066T (560056) 345 kV Bus a. Apply Fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G15-066T (560056) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0305_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to KINZEGR4 (512710) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0306_P1 | 3 phase fault on KINZE 4 (515008) 138 kV Bus a. Apply Fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZE 4 (515008) 138 kV Bus to FITZGRD4 (514830) 138 kV Bus CKT 1 b. 2. Trip branch from FITZGRD4 (514830) 138 kV Bus to PINE ST4 (514829) 138 kV Bus CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV Bus to CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Drop Load 1 at FITZGRD4 (514830) 138 kV Bus b. 5. Drop Load 1 at PINE ST4 (514829) 138 kV Bus b. 6. Drop Load 2 at PINE ST4 (514829) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0307_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to NORTHTP4 (512731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0308_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to 19TH ST4 (512712) 138 kV Bus CKT 1 b. 2. Trip branch from 19TH ST4 (512712) 138 kV Bus to 4RAMSEY (300844) 138 kV Bus CKT 1 b. 3. Drop Load 1 at 19TH ST4 (512712) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0309_P1 | 3 phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply Fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KINZEGR4 (512710) 138 kV Bus to KINZEGR2 (512713) 69 kV Bus CKT 1 b. 2. Trip branch from KINZEGR2 (512713) 69 kV Bus to ADMIRAL2 (512660) 69 kV Bus CKT 1 b. 3. Drop Shunt 1 at KINZEGR2 (512713) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0310_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to ARCADIA4 (514907) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0311_P1 | 3 phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply Fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV Bus to CRESENT4 (515377) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0312_P4 | a. Apply single phase fault at SOONER 4 (514802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SOONER 4 (514802) 138 kV to MORISNT4 (515447) 138 kV CKT 1 b. 2. Trip branch from SOONER 4 (514802) 138 kV to SNRPMPT4 (514798) 138 kV CKT 1 b. 3. Trip branch from SNRPMPT4 (514798) 138 kV to SNRPMP 4 (514799) 138 kV CKT 1 b. 4. Drop Load 1 SNRPMP 4 (514799) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0313_P4 | a. Apply single phase fault at T.NO.--4 (509817) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from T.NO.--4 (509817) 138 kV to T.NO.2-4 (509895) 138 kV CKT 1 b. 2. Trip branch from T.NO.--4 (509817) 138 kV to CDC-WT 4 (509842) 138 kV CKT 1 b. 3. Trip branch from CDC-WT 4 (509842) 138 kV to A.A.---4 (509784) 138 kV CKT 1 b. 4. Trip branch from CDC-WT 4 (509842) 138 kV to WHIRLPO4 (509840) 138 kV CKT 1 b. 5. Drop Load 1 WHIRLPO4 (509840) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0314_P4 | a. Apply single phase fault at MEMRIAL4 (514835) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MEMRIAL4 (514835) 138 kV to TENESTP4 (514837) 138 kV CKT 1 b. 2. Trip branch from MEMRIAL4 (514835) 138 kV to BRYANT 4 (514839) 138 kV CKT 1 b. 3. Trip branch from BRYANT 4 (514839) 138 kV to ACORN 4 (515459) 138 kV CKT 1 b. 4. Trip branch from ACORN 4 (515459) 138 kV to JONESSB4 (515480) 138 kV CKT 1 b. 5. Drop Load 1 BRYANT 4 (514839) 138 kV b. 6. Drop Load 1 ACORN 4 (515459) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0315_P4 | a. Apply single phase fault at S.S.---4 (509815) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S.S.---4 (509815) 138 kV to SHEFFD-4 (509812) 138 kV CKT 1 b. 2. Trip branch from SHEFFD-4 (509812) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 b. 3. Trip branch from S.S.---4 (509815) 138 kV to PRATTV-4 (509758) 138 kV CKT 1 b. 4. Trip branch from PRATTV-4 (509758) 138 kV to BLUEBEL4 (515242) 138 kV CKT 1 b. 5. Drop Load 1 PRATTV-4 (509758) 138 kV b. 6. Drop Load 1 SHEFFD-4 (509812) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0316_P4 | a. Apply single phase fault at R.S.S.-4 (509783) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from R.S.S.-4 (509783) 138 kV to ORU ETP4 (509849) 138 kV CKT 1 b. 2. Trip branch from ORU ETP4 (509849) 138 kV to WARNTAP4 (509858) 138 kV CKT 1 b. 3. Trip branch from ORU ETP4 (509849) 138 kV to ORU E4 (509738) 138 kV CKT 1 b. 4. Trip branch from R.S.S.-4 (509783) 138 kV to ORU-WTP4 (509853) 138 kV CKT 1 b. 5. Trip branch from ORU-WTP4 (509853) 138 kV to SHILETP4 (509813) 138 kV CKT 1 b. 6. Trip branch from ORU-WTP4 (509853) 138 kV to ORU W4 (509732) 138 kV CKT 1 b. 7. Drop Load 1 ORU W4 (509732) 138 kV b. 8. Drop Shunt 1 ORU W4 (509732) 138 kV b. 9. Drop Load 1 ORU E4 (509738) 138 kV b. 10. Drop Shunt 1 ORU E4 (509738) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0317_P4 | a. Apply single phase fault at DVISION4 (514853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DVISION4 (514853) 138 kV to LAKESID4 (514849) 138 kV CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV to HEFNER 4 (514848) 138 kV CKT 1 b. 3. Trip branch from DVISION4 (514853) 138 kV to SLVRLAK4 (514852) 138 kV CKT 1 b. 4. Drop Load 1 LAKESID4 (514849) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0318_P4 | a. Apply single phase fault at T.NO.--7 (509852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV to T.NO.2-4 (509895) kV to TNO2-1 (509894) 34.5 kV CKT1 b. 2. Trip branch from T.NO.2-4 (509895) 138 kV to T.NO.--4 (509817) 138 kV CKT 1 b. 3. Trip branch from T.NO.--7 (509852) 345 kV to N.E.S.-7 (510406) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0319_P4 | a. Apply single phase fault at WEKIWA-4 (509757) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WEKIWA-7 (509755) 345 kV to WEKIWA-4 (509757) kV to WEKIW1-1 (509879) 34.5 kV CKT1 b. 2. Trip branch from WEKIWA-4 (509757) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to 4SILVCTY (300140) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0320_P4 | a. Apply single phase fault at WOODRNG7 (514715) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WOODRNG7 (514715) 345 kV to WOODRNG4 (514714) kV to WOODRNG1 (515770) 13.8 kV CKT1 b. 2. Trip branch from WOODRNG7 (514715) 345 kV to PINTAIL7 (516010) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0321_P4 | a. Apply single phase fault at 4CLEVLND (300138) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4CLEVLND (300138) 138 kV to CLEVLND 4 (512729) 138 kV CKT Z1 b. 2. Trip three winding transformer from CLEVLND7 (512694) 345 kV to CLEVLND 4 (512729) kV to CLEVLND1 (512817) 13.8 kV CKT1 b. 3. Trip branch from 4CLEVLND (300138) 138 kV to PAWNSW4 (512749) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0322_P4 | a. Apply single phase fault at CTNWOOD4 (514827) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CTNWOOD4 (514827) 138 kV to ARCADIA4 (514907) 138 kV CKT 1 b. 2. Trip branch from CTNWOOD4 (514827) 138 kV to PINE ST4 (514829) 138 kV CKT 1 b. 3. Trip branch from PINE ST4 (514829) 138 kV to FITZGRD4 (514830) 138 kV CKT 1 b. 4. Trip branch from FITZGRD4 (514830) 138 kV to KINZE 4 (515008) 138 kV CKT 1 b. 5. Drop Load 1 PINE ST4 (514829) 138 kV b. 6. Drop Load 2 PINE ST4 (514829) 138 kV b. 7. Drop Load 1 FITZGRD4 (514830) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0324_P4 | a. Apply single phase fault at SAPLPRD4 (509871) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SAPLPRD4 (509871) 138 kV to SAPLPRD7 (509870) kV to SAPLPRD1 (509872) 13.8 kV CKT1 b. 2. Trip branch from SAPLPRD4 (509871) 138 kV to OAKSWTP4 (509848) 138 kV CKT 1 b. 3. Trip branch from OAKSWTP4 (509848) 138 kV to OAKS W4 (509727) 138 kV CKT 1 b. 4. Trip branch from OAKSWTP4 (509848) 138 kV to T.P.S.-4 (509788) 138 kV CKT 1 b. 5. Drop Load 1 OAKS W4 (509727) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0325_P4 | a. Apply single phase fault at ARCADIA4 (514907) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA4 (514907) 138 kV to RNDBARN4 (515461) 138 kV CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV to BURGETT4 (514510) 138 kV CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV to DANFRTH4 (514833) 138 kV CKT 1 b. 4. Trip three winding transformer from ARCADIA4 (514907) 138 kV to ARCADIA7 (514908) kV to ARCADI41 (515700) 13.8 kV CKT1 b. 5. Drop Load 1 BURGETT4 (514510) 138 kV b. 6. Drop Load 1 RNDBARN4 (515461) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0326_P4 | a. Apply single phase fault at BV-SE--4 (510391) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BV-SE--4 (510391) 138 kV to RICE CK4 (510385) 138 kV CKT 1 b. 2. Trip branch from RICE CK4 (510385) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 3. Trip branch from BV-SE--4 (510391) 138 kV to BV-COM-4 (510390) 138 kV CKT 1 b. 4. Drop Load M1 RICE CK4 (510385) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0327_P4 | a. Apply single phase fault at COFCTY2 (512735) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV to COFCTY2 (512735) kV to COFFEY1 (512740) 13.8 kV CKT1 b. 2. Trip three winding transformer from FARML 4 (512734) 138 kV to COFCTY2 (512735) kV to COFFEY2 (512741) 13.8 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0328_P4 | a. Apply single phase fault at NEOSHO 7 (532793) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV to G17-209-TAP (760921) 345 kV CKT 1 b. 2. Trip three winding transformer from NEOSHO 7 (532793) 345 kV to NEOSHO 5 (532937) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0329_P4 | a. Apply single phase fault at N.E.S.-4 (510396) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N.E.S.-4 (510396) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 2. Trip branch from OOLOGAHKM 4 (513124) 138 kV to CLARMR 4 (512707) 138 kV CKT 1 b. 3. Trip three winding transformer from CLARMR 4 (512707) 138 kV to CLARMR 5 (512651) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 4. Trip branch from N.E.S.-4 (510396) 138 kV to OWASO2_4 (509843) 138 kV CKT 1 b. 5. Trip branch from OWASO2_4 (509843) 138 kV to PCATSAT4 (509841) 138 kV CKT 1 b. 6. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0330_P4 | a. Apply single phase fault at NEOSHO 4 (533021) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHO 7 (532793) kV to N345 1 1 (532824) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 4 (533021) 138 kV to NEOSHON4 (533022) 138 kV CKT Z1 b. 3. Drop Shunt 1 N345 1 1 (532824) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0331_P4 | a. Apply single phase fault at NEOSHO 5 (532937) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV to NEOSHO 7 (532793) kV to N345 2 1 (532825) 13.8 kV CKT1 b. 2. Trip branch from NEOSHO 5 (532937) 161 kV to RIV4525 (547469) 161 kV CKT 1 b. 3. Drop Shunt 1 N345 2 1 (532825) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0332_P4 | a. Apply single phase fault at NEOSHOS2 (533778) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV to NEOSHOS2 (533778) kV to NSES 2X1 (532710) 13.2 kV CKT1 b. 2. Trip branch from NEOSHOS2 (533778) 69 kV to BAKER 2 (532926) 69 kV CKT 1 b. 3. Trip branch from BAKER 2 (532926) 69 kV to SOPITT 2 (533773) 69 kV CKT 1 b. 4. Drop Load 1 BAKER 2 (532926) 69 kV b. 5. Drop Load 2 BAKER 2 (532926) 69 kV b. 6. Drop Load 3 BAKER 2 (532926) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0333_P4 | a. Apply single phase fault at ALTOONA4 (533001) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ALTOONA4 (533001) 138 kV to G17-022-TAP (588664) 138 kV CKT 1 b. 2. Trip branch from ALTOONA4 (533001) 138 kV to TAYLOR 4 (533006) 138 kV CKT 1 b. 3. Trip branch from TAYLOR 4 (533006) 138 kV to MONTGOM4 (533004) 138 kV CKT 1 b. 4. Drop Load 1 TAYLOR 4 (533006) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0334_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to DELWARE4 (510379) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0335_P1 | 3 phase fault on N.E.S.-7 (510406) 345 kV Bus a. Apply Fault at the N.E.S.-7 (510406) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N.E.S.-7 (510406) 345 kV Bus to ONETA--7 (509807) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0336_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to 7BLACKBERRY (300739) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0337_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-009-TAP (532777) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0338_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 7 (532793) 345 kV Bus to G17-209-TAP (760921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0339_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 4 (533021) 138 kV Bus to N345 1 1 (532824) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 1 1 (532824) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0340_P1 | 3 phase fault on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 7 (532793) 345 kV Bus to NEOSHO 5 (532937) 161 kV Bus to N345 2 1 (532825) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at N345 2 1 (532825) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0341_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0342_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHON4 (533022) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0343_P1 | 3 phase fault on G18-079-TAP (763113) 138 kV Bus a. Apply Fault at the G18-079-TAP (763113) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G18-079-TAP (763113) 138 kV Bus to FARML 4 (512734) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0344_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS4 (533020) 138 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0345_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHO 4 (533021) 138 kV Bus to NEOSH4 1 (532958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0346_P1 | 3 phase fault on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 4 (533021) 138 kV Bus to NEOSHOS2 (533778) 69 kV Bus to NSES 2X1 (532710) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0347_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to MARMTNW5 (532935) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0348_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHO 5 (532937) 161 kV Bus to RIV4525 (547469) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0349_P1 | 3 phase fault on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHO 5 (532937) 161 kV Bus to NEOSHOS4 (533020) 138 kV Bus to NEOSH5 1 (532959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0350_P1 | 3 phase fault on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS4 (533020) 138 kV Bus to TV1MNDV4 (533008) 138 kV Bus CKT 1 b. 2. Trip branch from TV1MNDV4 (533008) 138 kV Bus to LIBERTY4 (533003) 138 kV Bus CKT 1 b. 3. Drop Load K1 at TV1MNDV4 (533008) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0351_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0352_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEOSHON4 (533022) 138 kV Bus to NEOSHON2 (533768) 69 kV Bus to NEC U3 (532711) 12 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0353_P1 | 3 phase fault on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHON4 (533022) 138 kV Bus to NEPARSN4 (533005) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0354_P1 | 3 phase fault on DELWARE4 (510379) 138 kV Bus a. Apply Fault at the DELWARE4 (510379) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DELWARE7 (510380) 345 kV Bus to DELWARE4 (510379) 138 kV Bus to DELAWAR1 (510370) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0355_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to NEOSHON2 (533768) 69 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0356_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to BAKER 2 (532926) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0357_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to CRAWFOR2 (533758) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0358_P1 | 3 phase fault on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEOSHOS2 (533778) 69 kV Bus to ORDNJCT2 (533703) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0359_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to DEARING4 (533002) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0360_P1 | 3 phase fault on COFFEYT4 (510422) 138 kV Bus a. Apply Fault at the COFFEYT4 (510422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COFFEYT4 (510422) 138 kV Bus to NBVILLE4 (510386) 138 kV Bus CKT 1 b. 2. Trip branch from NBVILLE4 (510386) 138 kV Bus to BV-SE--4 (510391) 138 kV Bus CKT 1 b. 3. Drop Load M1 at NBVILLE4 (510386) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0361_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0362_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0363_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0364_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ONETA--7 (509807) 345 kV Bus to OEC 7 (509836) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0365_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FARML 4 (512734) 138 kV Bus to SCOFCTY4 (510378) 138 kV Bus CKT 1 b. 2. Trip branch from SCOFCTY4 (510378) 138 kV Bus to SCOFFEYV4 (510420) 138 kV Bus CKT 1 b. 3. Trip branch from SCOFCTY4 (510378) 138 kV Bus to COFFEYT4 (510422) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SCOFFEYV4 (510420) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0366_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA1-1 (509881) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0367_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA2-1 (509868) 34.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0368_P1 | 3 phase fault on ONETA--7 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ONETA--7 (509807) 345 kV Bus to ONETA--4 (509806) 138 kV Bus to ONETA5-1 (509874) 34.5 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0369_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to WEKIWA-7 (509755) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0370_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to IGLOOV 7 (513596) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0371_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0372_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from T.NO.--7 (509852) 345 kV Bus to CLEVLND7 (512694) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0373_P1 | 3 phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from T.NO.--7 (509852) 345 kV Bus to T.NO.2-4 (509895) 138 kV Bus to TNO2-1 (509894) 34.5 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0374_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to WOLFCRK7 (532797) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0375_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7SPORTSMAN (300740) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0376_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY2 (512741) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0377_P1 | 3 phase fault on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7BLACKBERRY (300739) 345 kV Bus to 7JASPER (300949) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0378_P1 | 3 phase fault on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-209-TAP (760921) 345 kV Bus to LACYGNE7 (542981) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0379_P1 | 3 phase fault on CANEYRV7 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CANEYRV7 (532780) 345 kV Bus to LATHAMS7 (532800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0381_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARMTNW5 (532935) 161 kV Bus to MARMTNE5 (532934) 161 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0382_P1 | 3 phase fault on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARMTNW5 (532935) 161 kV Bus to MARMATN2 (533639) 69 kV Bus to MARMATN1 (532955) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0383_P1 | 3 phase fault on MARMTNE5 (532934) 161 kV Bus a. Apply Fault at the MARMTNE5 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFOR2 (533758) 69 kV Bus to SE1GREE2 (533772) 69 kV Bus CKT 1 b. 2. Trip branch from SE1GREE2 (533772) 69 kV Bus to GIR JCT2 (533762) 69 kV Bus CKT 1 b. 3. Drop Load K1 at CRAWFOR2 (533758) 69 kV Bus b. 4. Drop Load 1 at CRAWFOR2 (533758) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0384_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 5JASPER (300950) 161 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0385_P1 | 3 phase fault on 7JASPER (300949) 345 kV Bus a. Apply Fault at the 7JASPER (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7JASPER (300949) 345 kV Bus to 7MORGAN (300045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0387_P1 | 3 phase fault on FARML 4 (512734) 138 kV Bus a. Apply Fault at the FARML 4 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FARML 4 (512734) 138 kV Bus to COFCTY2 (512735) 69 kV Bus to COFFEY1 (512740) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0388_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to NEOSHO 7 (532793) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0389_P1 | 3 phase fault on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DELWARE7 (510380) 345 kV Bus to N.E.S.-7 (510406) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0390_P4 | a. Apply single phase fault at SUNNYSD7 (515136) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV to SUNNYSD4 (515135) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip branch from SUNNYSD7 (515136) 345 kV to TERRYRD7 (511568) 345 kV CKT 1 b. 3. Drop Shunt SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0391_P4 | a. Apply single phase fault at ARBUCKL4 (515117) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARBUCKL4 (515117) 138 kV to VANOSTP4 (515531) 138 kV CKT 1 b. 2. Trip branch from ARBUCKL4 (515117) 138 kV to SULPHR 4 (515559) 138 kV CKT 1 b. 3. Trip branch from SULPHR 4 (515559) 138 kV to JOLLYVL4 (515118) 138 kV CKT 1 b. 4. Trip branch from JOLLYVL4 (515118) 138 kV to PRICESF4 (514814) 138 kV CKT 1 b. 5. Trip branch from PRICESF4 (514814) 138 kV to HONEYCK4 (515643) 138 kV CKT 1 b. 6. Drop Load 1 SULPHR 4 (515559) 138 kV b. 7. Drop Load 1 JOLLYVL4 (515118) 138 kV b. 8. Drop Load 1 PRICESF4 (514814) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0392_P4 | a. Apply single phase fault at FTSMTHW5 (515301) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from FTSMTHW5 (515301) 161 kV to FTSMITH7 (515302) kV to FTSMTH51 (515728) 13.8 kV CKT5 b. 2. Trip branch from FTSMTHW5 (515301) 161 kV to ARKOMA 5 (515306) 161 kV CKT 1 b. 3. Trip branch from ARKOMA 5 (515306) 161 kV to 3RDST 5 (515308) 161 kV CKT 1 b. 4. Drop Shunt 1 ARKOMA 5 (515306) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0393_P4 | a. Apply single phase fault at PARKLN 4 (515178) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PARKLN 4 (515178) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to SEMINOL4 (515044) 138 kV CKT 1 b. 3. Trip branch from PARKLN 4 (515178) 138 kV to SOTHADA4 (515318) 138 kV CKT 1 b. 4. Trip branch from SOTHADA4 (515318) 138 kV to HARDEN 4 (515362) 138 kV CKT 1 b. 5. Trip branch from HARDEN 4 (515362) 138 kV to EFITSTP4 (515699) 138 kV CKT 1 b. 6. Trip branch from EFITSTP4 (515699) 138 kV to LULA 4 (515192) 138 kV CKT 1 b. 7. Trip branch from EFITSTP4 (515699) 138 kV to EFITTS 4 (515809) 138 kV CKT 1 b. 8. Drop Load 1 LKKONWA4 (515977) 138 kV b. 9. Drop Load 1 SOTHADA4 (515318) 138 kV b. 10. Drop Load 1 HARDEN 4 (515362) 138 kV b. 11. Drop Load 1 EFITTS 4 (515809) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0394_P4 | a. Apply single phase fault at LONEOAK4 (510897) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LONEOAK4 (510897) 138 kV to HARTSHN4 (520934) 138 kV CKT 1 b. 2. Trip branch from LONEOAK4 (510897) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 3. Trip branch from SMCALTP4 (510906) 138 kV to MCALEST4 (510908) 138 kV CKT 1 b. 4. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 5. Drop Load 1 S-MCALT4 (510865) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0395_P4 | a. Apply single phase fault at FTSMTHE5 (515300) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FTSMTHE5 (515300) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 2. Trip branch from QUANXTP5 (515310) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 4. Trip branch from BARLING5 (515311) 161 kV to MASSARD5 (515343) 161 kV CKT 1 b. 5. Trip branch from FTSMTHE5 (515300) 161 kV to COLONY 5 (515345) 161 kV CKT 1 b. 6. Trip branch from COLONY 5 (515345) 161 kV to BATTLEF5 (515349) 161 kV CKT 1 b. 7. Trip branch from BATTLEF5 (515349) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 8. Drop Load 1 BARLING5 (515311) 161 kV b. 9. Drop Load 1 QUANEXS5 (515474) 161 kV b. 10. Drop Load 1 COLONY 5 (515345) 161 kV b. 11. Drop Load 1 BATTLEF5 (515349) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0396_P4 | a. Apply single phase fault at WELETK4 (510902) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WELETK4 (510902) 138 kV to WELEETK4 (505592) 138 kV CKT 1 b. 2. Trip branch from WELETK4 (510902) 138 kV to EC.HEN-4 (510923) 138 kV CKT 1 b. 3. Trip branch from EC.HEN-4 (510923) 138 kV to OKMULGE4 (510898) 138 kV CKT 1 b. 4. Drop Load 1 EC.HEN-4 (510923) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0397_P4 | a. Apply single phase fault at MASSARD5 (515343) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MASSARD5 (515343) 161 kV to RYHLLTP5 (515523) 161 kV CKT 1 b. 2. Trip branch from MASSARD5 (515343) 161 kV to BARLING5 (515311) 161 kV CKT 1 b. 3. Trip branch from BARLING5 (515311) 161 kV to QUANXTP5 (515310) 161 kV CKT 1 b. 4. Trip branch from QUANXTP5 (515310) 161 kV to FTSMTHE5 (515300) 161 kV CKT 1 b. 5. Trip branch from QUANXTP5 (515310) 161 kV to QUANEXS5 (515474) 161 kV CKT 1 b. 6. Drop Load 1 BARLING5 (515311) 161 kV b. 7. Drop Load 1 QUANEXS5 (515474) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0398_P4 | a. Apply single phase fault at ARCADIA7 (514908) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARCADIA7 (514908) 345 kV to REDBUD 7 (514909) 345 kV CKT 1 b. 2. Trip branch from ARCADIA7 (514908) 345 kV to NORTWST7 (514880) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0399_P4 | a. Apply single phase fault at DRAPER 7 (514934) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV to DRAPER 4 (514933) kV to DRAPER41 (515721) 13.8 kV CKT1 b. 2. Trip branch from DRAPER 7 (514934) 345 kV to NSUB345 (555234) kV CKT 1 b. 3. Drop Shunt 1 DRAPER41 (515721) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0400_P4 | a. Apply single phase fault at MUSKOGE7 (515224) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV to FTSMITH7 (515302) 345 kV CKT 1 b. 2. Trip branch from MUSKOGE7 (515224) 345 kV to H_SPRNG-TAP (588839) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0401_P4 | a. Apply single phase fault at SEMINOL4 (515044) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOL4 (515044) 138 kV to LKKONWA4 (515977) 138 kV CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV to PARKLN 4 (515178) 138 kV CKT 1 b. 3. Trip branch from SEMINOL4 (515044) 138 kV to MAUD 4 (515055) 138 kV CKT 1 b. 4. Drop Load 1 LKKONWA4 (515977) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0402_P4 | a. Apply single phase fault at CHIKSAW4 (515171) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHIKSAW4 (515171) 138 kV to CARTER 4 (515138) 138 kV CKT 1 b. 2. Trip branch from CHIKSAW4 (515171) 138 kV to FNDTION4 (515162) 138 kV CKT 1 b. 3. Trip branch from FNDTION4 (515162) 138 kV to SPRNDAL4 (515172) 138 kV CKT 1 b. 4. Drop Load 1 FNDTION4 (515162) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0403_P4 | a. Apply single phase fault at SUNNYSD4 (515135) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNYSD 1 (515405) 13.8 kV CKT1 b. 2. Trip three winding transformer from SUNNYSD4 (515135) 138 kV to SUNNYSD7 (515136) kV to SUNNYSD1 (515762) 13.8 kV CKT1 b. 3. Drop Shunt 1 SUNYSD 1 (515405) 13.8 kV b. 4. Drop Shunt 1 SUNNYSD1 (515762) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0404_P4 | a. Apply single phase fault at MCALEST4 (510908) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MCALEST4 (510908) 138 kV to TALAWANDA 4 (510951) 138 kV CKT 1 b. 2. Trip branch from TALAWANDA 4 (510951) 138 kV to MCALESTIND 4 (510909) 138 kV CKT 1 b. 3. Trip branch from TALAWANDA 4 (510951) 138 kV to C-RIVER4 (510946) 138 kV CKT 1 b. 4. Trip branch from MCALEST4 (510908) 138 kV to SMCALTP4 (510906) 138 kV CKT 1 b. 5. Trip branch from SMCALTP4 (510906) 138 kV to LONEOAK4 (510897) 138 kV CKT 1 b. 6. Trip branch from SMCALTP4 (510906) 138 kV to S-MCALT4 (510865) 138 kV CKT 1 b. 7. Drop Load 1 S-MCALT4 (510865) 138 kV b. 8. Drop Load 1 MCALESTIND 4 (510909) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0405_P4 | a. Apply single phase fault at S BROWN4 (505602) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from S BROWN4 (505602) 138 kV to RUSSETT4 (521044) 138 kV CKT 1 b. 2. Trip branch from RUSSETT4 (521044) 138 kV to RUSSET-4 (515120) 138 kV CKT 1 b. 3. Trip branch from RUSSETT4 (521044) 138 kV to REAGAN 4 (520465) 138 kV CKT 1 b. 4. Trip branch from S BROWN4 (505602) 138 kV to COLBRTP4 (515159) 138 kV CKT 1 b. 5. Drop Load 1 RUSSETT4 (521044) 138 kV b. 6. Drop Load 1 REAGAN 4 (520465) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0406_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to C-RIVER7 (515422) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0407_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to HUGO 7 (521157) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0408_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN3-1 (510939) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0409_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT7 (510911) 345 kV Bus to VALIANT4 (510918) 138 kV Bus to VALN2-1 (510938) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0410_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 7 (514809) 345 kV Bus to SUNNYSD7 (515136) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0411_P1 | 3 phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply Fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from JOHNCO 7 (514809) 345 kV Bus to JOHNCO 4 (514808) 138 kV Bus to JOHNCO11 (514810) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at JOHNCO11 (514810) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0412_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to ARCADIA7 (514908) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0413_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0414_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0415_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0416_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to SEMINOL7 (515045) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0417_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO11 (515756) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO11 (515756) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0418_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOL7 (515045) 345 kV Bus to SEMINOL4 (515044) 138 kV Bus to SEMINO21 (515757) 14.4 kV Bus CKT 1 b. 2. Drop Shunt 1 at SEMINO21 (515757) 14.4 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0419_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from C-RIVER7 (515422) 345 kV Bus to C-RIVER4 (510946) 138 kV Bus to C-RIVER1 (510947) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0420_P1 | 3 phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply Fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER7 (515422) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0421_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from VALIANT4 (510918) 138 kV Bus to VALIANT2 (510910) 69 kV Bus to VALN1-1 (510937) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0422_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to V-WEYCO4 (510866) 138 kV Bus CKT 1 b. 2. Drop Shunt 1 at V-WEYCO4 (510866) 138 kV Bus1 b. 3. Drop Load 1 at V-WEYCO4 (510866) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0423_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to IDABEL-4 (510886) 138 kV Bus CKT 1 b. 2. Trip branch from IDABEL-4 (510886) 138 kV Bus to B.BOWTP4 (510888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IDABEL-4 (510886) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0424_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO---4 (510901) 138 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0425_P1 | 3 phase fault on VALIANT4 (510918) 138 kV Bus a. Apply Fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT4 (510918) 138 kV Bus to HUGO PP4 (520948) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0426_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to CANEYCK4 (515150) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0427_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to JOHNCO 7 (514809) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0428_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to RUSSET-4 (515120) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0429_P1 | 3 phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply Fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNCO 4 (514808) 138 kV Bus to SXMLCKT4 (515122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0430_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to VANOSTP4 (515531) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0431_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to PAOLI- 4 (515100) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0432_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to MAUD 4 (515055) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0433_P1 | 3 phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply Fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL4 (515044) 138 kV Bus to LKKONWA4 (515977) 138 kV Bus CKT 1 b. 2. Trip branch from LKKONWA4 (515977) 138 kV Bus to PARKLN 4 (515178) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0434_P1 | 3 phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply Fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from C-RIVER4 (510946) 138 kV Bus to TALAWANDA 4 (510951) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0435_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to WCITYTP2 (510870) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0436_P1 | 3 phase fault on VALIANT2 (510910) 69 kV Bus a. Apply Fault at the VALIANT2 (510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT2 (510910) 69 kV Bus to KIPUMPT2 (510876) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0437_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TURK 7 (507455) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0438_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0439_P1 | 3 phase fault on TURK 7 (507455) 345 kV Bus a. Apply Fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 7 (507455) 345 kV Bus to TURK 4 (507454) 138 kV Bus to TURK 1 (507457) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0440_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX1-1 (508100) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NWTEX1-1 (508100) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0441_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWTXARK7 (508072) 345 kV Bus to NWTXARK4 (508071) 138 kV Bus to NWTEX2-1 (508101) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at NWTEX2-1 (508101) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0442_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0443_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0444_P1 | 3 phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply Fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK7 (508072) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0445_P1 | 3 phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply Fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LYDIA 7 (508298) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0446_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO 7 (521157) 345 kV Bus to HUGOITC4 (520560) 138 kV Bus to HUGO TERTA (521189) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0447_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNNYSD1 (515762) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNNYSD1 (515762) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0448_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus to SUNNYSD4 (515135) 138 kV Bus to SUNYSD 1 (515405) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SUNYSD 1 (515405) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0449_P1 | 3 phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply Fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from PITTSB-7 (510907) 345 kV Bus to VALIANT7 (510911) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763134 [G18-082-GEN10.6900], 763137 [G18-082-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0450_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0451_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0452_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0453_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0454_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0455_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0456_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER21 (515792) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0457_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER41 (515721) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER41 (515721) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0458_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRAPER 7 (514934) 345 kV Bus to DRAPER 4 (514933) 138 kV Bus to DRAPER31 (515720) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DRAPER31 (515720) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0459_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0460_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to TURK 7 (507455) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0461_P1 | 3 phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply Fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 7 (514934) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0462_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to H_SPRNG-TAP (588839) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0463_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to CLARKSV7 (509745) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0464_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0465_P1 | 3 phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply Fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MUSKOGE7 (515224) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 760392 [G17-140-GEN10.6300], 760412 [G17-141-GEN10.6300]
04 - Southeast | 25W | Transfer | Group4_Fault_0466_P1 | 3 phase fault on HUGO---4 (510901) 138 kV Bus a. Apply Fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUGO---4 (510901) 138 kV Bus to HUGO---2 (510893) 69 kV Bus to HUGO4-1 (510859) 13.8 kV Bus CKT 1 b. 2. Drop Load 1 at HUGO---4 (510901) 138 kV Bus b. 3. Drop Load 1 at HUGO---2 (510893) 69 kV Bus b. 4. Drop Shunt 1 at HUGO---2 (510893) 69 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0467_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to HUGOITC4 (520560) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0468_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to VALLANT4 (521079) 138 kV Bus CKT 1 b. 2. Trip branch from VALLANT4 (521079) 138 kV Bus to GARVIN4 (520419) 138 kV Bus CKT 1 b. 3. Trip branch from GARVIN4 (520419) 138 kV Bus to IDABEL 4 (520953) 138 kV Bus CKT 1 b. 4. Drop Load 1 at VALLANT4 (521079) 138 kV Bus b. 5. Drop Load 1 at GARVIN4 (520419) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0469_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to FROGVIL4 (520918) 138 kV Bus CKT 1 b. 2. Trip branch from FROGVIL4 (520918) 138 kV Bus to WSBNKTP4 (521098) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0470_P1 | 3 phase fault on HUGO PP4 (520948) 138 kV Bus a. Apply Fault at the HUGO PP4 (520948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUGO PP4 (520948) 138 kV Bus to SAWYER4 (520411) 138 kV Bus CKT 1 b. 2. Trip branch from SAWYER4 (520411) 138 kV Bus to RATTAN 4 (521036) 138 kV Bus CKT 1 b. 3. Trip branch from RATTAN 4 (521036) 138 kV Bus to DARWIN 4 (520874) 138 kV Bus CKT 1 b. 4. Trip branch from DARWIN 4 (520874) 138 kV Bus to LANE 4 (520968) 138 kV Bus CKT 1 b. 5. Trip branch from LANE 4 (520968) 138 kV Bus to ATOKA--4 (510887) 138 kV Bus CKT 1 b. 6. Drop Load 1 at SAWYER4 (520411) 138 kV Bus b. 7. Drop Load 1 at RATTAN 4 (521036) 138 kV Bus b. 8. Drop Load 1 at DARWIN 4 (520874) 138 kV Bus b. 9. Drop Load 1 at LANE 4 (520968) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0471_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to NWTXARK7 (508072) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0472_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to RUSSETT4 (521044) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0473_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to GLASSES4 (515147) 138 kV Bus CKT 1 b. 2. Trip branch from GLASSES4 (515147) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASSES4 (515147) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0474_P1 | 3 phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply Fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RUSSET-4 (515120) 138 kV Bus to STIRLNG4 (515932) 138 kV Bus CKT 1 b. 2. Trip branch from STIRLNG4 (515932) 138 kV Bus to DRPSPRG4 (515873) 138 kV Bus CKT 1 b. 3. Trip branch from DRPSPRG4 (515873) 138 kV Bus to SPRNDAL4 (515172) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STIRLNG4 (515932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0475_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to HOWE 4 (521122) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0476_P1 | 3 phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply Fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SXMLCKT4 (515122) 138 kV Bus to MILLCKT4 (515121) 138 kV Bus CKT 1 b. 2. Trip branch from MILLCKT4 (515121) 138 kV Bus to MILLCRK4 (515196) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0477_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0478_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to TEXOMAJ4 (521067) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0479_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to LTLCITY4 (515151) 138 kV Bus CKT 1 b. 2. Trip branch from LTLCITY4 (515151) 138 kV Bus to BROWNTP4 (515152) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0480_P1 | 3 phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply Fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANEYCK4 (515150) 138 kV Bus to MADINDT4 (515149) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0481_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0482_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA7 (514908) 345 kV Bus to REDBUD 7 (514909) 345 kV Bus CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0483_P1 | 3 phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply Fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOL7 (515045) 345 kV Bus to DRAPER 7 (514934) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0484_P1 | 3 phase fault on VALIANT7 (510911) 345 kV Bus a. Apply Fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from VALIANT7 (510911) 345 kV Bus to LYDIA 7 (508298) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0485_P4 | a. Apply single phase fault at LYDIA 7 (508298) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LYDIA 7 (508298) 345 kV to WELSH 7 (508359) 345 kV CKT 1 b. 2. Trip branch from LYDIA 7 (508298) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0486_P4 | a. Apply single phase fault at DIANA 4 (508831) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from DIANA 4 (508831) 138 kV to DIANA 7 (508832) kV to DIANA-N1 (508845) 13.8 kV CKT3 b. 2. Trip branch from DIANA 4 (508831) 138 kV to PERDUE 4 (508351) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0487_P4 | a. Apply single phase fault at BANN 4 (508054) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BANN 4 (508054) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip branch from BANN 4 (508054) 138 kV to REDSPRG4 (508075) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0488_P4 | a. Apply single phase fault at LONGWD 4 (508808) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from LONGWD 4 (508808) 138 kV to LONGWD 7 (508809) kV to LONGW1-1 (508819) 13.2 kV CKT1 b. 2. Trip branch from LONGWD 4 (508808) 138 kV to LIEBERM4 (508806) 138 kV CKT 1 b. 3. Drop Shunt 1 LONGW1-1 (508819) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0489_P4 | a. Apply single phase fault at SW SHV 4 (507759) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from SW SHV 4 (507759) 138 kV to SW SHV 7 (507760) kV to SWSHV1-1 (507778) 13.8 kV CKT1 b. 2. Trip branch from SW SHV 4 (507759) 138 kV to LEASIDE 4 (507793) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0490_P4 | a. Apply single phase fault at PIRKEY 4 (508562) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV to EASTON 4 (509092) 138 kV CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV to BRANDYBR (508596) 138 kV CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV to KNOXLEE4 (508548) 138 kV CKT 1 b. 4. Trip branch from PIRKEY 4 (508562) 138 kV to HALLSVLS4 (508595) 138 kV CKT 1 b. 5. Trip branch from HALLSVLS4 (508595) 138 kV to WHITNEY4 (508575) 138 kV CKT 1 b. 6. Drop Load 1 EASTON 4 (509092) 138 kV b. 7. Drop Load 1 WHITNEY4 (508575) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0491_P4 | a. Apply single phase fault at NWTXARK7 (508072) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK7 (508072) 345 kV to TURK 7 (507455) 345 kV CKT 1 b. 2. Trip branch from NWTXARK7 (508072) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0492_P4 | a. Apply single phase fault at VALIANT7 (510911) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 1 b. 2. Trip branch from VALIANT7 (510911) 345 kV to PITTSB-7 (510907) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0493_P4 | a. Apply single phase fault at NWTXARK4 (508071) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NWTXARK4 (508071) 138 kV to NWT-BNT4 (508070) 138 kV CKT 1 b. 2. Trip three winding transformer from NWTXARK7 (508072) 345 kV to NWTXARK4 (508071) kV to NWTEX1-1 (508100) 13.8 kV CKT1 b. 3. Drop Shunt 1 NWTEX1-1 (508100) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0494_P4 | a. Apply single phase fault at PITTSB-7 (510907) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PITTSB-7 (510907) 345 kV to SEMINOL7 (515045) 345 kV CKT 1 b. 2. Trip branch from PITTSB-7 (510907) 345 kV to VALIANT7 (510911) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0495_P4 | a. Apply single phase fault at VALIANT4 (510918) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from VALIANT4 (510918) 138 kV to HUGO PP4 (520948) 138 kV CKT 1 b. 2. Trip branch from VALIANT4 (510918) 138 kV to IDABEL-4 (510886) 138 kV CKT 1 b. 3. Trip branch from IDABEL-4 (510886) 138 kV to B.BOWTP4 (510888) 138 kV CKT 1 b. 4. Trip branch from B.BOWTP4 (510888) 138 kV to CRAIGJT4 (510890) 138 kV CKT 1 b. 5. Trip branch from B.BOWTP4 (510888) 138 kV to B.BOW 4 (510864) 138 kV CKT 1 b. 6. Drop Load 1 IDABEL-4 (510886) 138 kV b. 7. Drop Load 1 B.BOW 4 (510864) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0496_P4 | a. Apply single phase fault at TURK 4 (507454) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV to TURK 7 (507455) kV to TURK 1 (507457) 13.8 kV CKT1 b. 2. Trip branch from TURK 4 (507454) 138 kV to MANDEVILTP4 (508105) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0497_P4 | a. Apply single phase fault at WILKES 4 (508840) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WILKES 4 (508840) 138 kV to WILKES 7 (508841) kV to WILKES-1 (508826) 13.2 kV CKT1 b. 2. Trip branch from WILKES 4 (508840) 138 kV to LSSOUTH4 (508297) 138 kV CKT 1 b. 3. Drop Shunt 1 WILKES-1 (508826) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0498_P4 | a. Apply single phase fault at PIRKEY 7 (508563) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PIRKEY 7 (508563) 345 kV to DIANA 7 (508832) 345 kV CKT 1 b. 2. Trip branch from PIRKEY 7 (508563) 345 kV to LEBROCK7 (508572) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0499_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-M1 (508843) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0500_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-N1 (508845) 13.8 kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0501_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0502_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TURK 4 (507454) 138 kV Bus to TURK 3 (507456) 115 kV Bus to TURK1 1 (507458) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0503_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to DIANA 7 (508832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0504_P1 | 3 phase fault on WELSH 7 (508359) 345 kV Bus a. Apply Fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WELSH 7 (508359) 345 kV Bus to SPPMAINBUS (5917) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0505_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0506_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DIANA 7 (508832) 345 kV Bus to DIANA 4 (508831) 138 kV Bus to DIANA-S1 (508844) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0507_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to WILKES 7 (508841) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0508_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY4 (508575) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0509_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT1-1 (508589) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0510_P1 | 3 phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply Fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHITNEY4 (508575) 138 kV Bus to WHITNEY2 (508574) 69 kV Bus to WHIT2-1 (508590) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0511_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to OAKPH 4 (508816) 138 kV Bus CKT 1 b. 2. Trip branch from OAKPH 4 (508816) 138 kV Bus to FLOURNY4 (507727) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OAKPH 4 (508816) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0512_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to NORAM 4 (507774) 138 kV Bus CKT 1 b. 2. Trip branch from NORAM 4 (507774) 138 kV Bus to RAINES 4 (507749) 138 kV Bus CKT 1 b. 3. Trip branch from RAINES 4 (507749) 138 kV Bus to ARSHILL4 (507711) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NORAM 4 (507774) 138 kV Bus b. 5. Drop Load 1 at RAINES 4 (507749) 138 kV Bus b. 6. Drop Shunt 1 at RAINES 4 (507749) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0513_P1 | 3 phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply Fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 4 (508808) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0514_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FLOURNY4 (507727) 138 kV Bus to FLOURNY2 (507726) 69 kV Bus to FLOURNY1 (507740) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0515_P1 | 3 phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply Fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY4 (507727) 138 kV Bus to GENMOTR4 (507732) 138 kV Bus CKT 1 b. 2. Trip branch from GENMOTR4 (507732) 138 kV Bus to SW SHV 4 (507759) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GENMOTR4 (507732) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0516_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WOOLWTP2 (507770) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0517_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to PINESRD2 (507747) 69 kV Bus CKT 1 b. 2. Trip branch from PINESRD2 (507747) 69 kV Bus to HARDY 2 (507734) 69 kV Bus CKT 1 b. 3. Drop Load 1 at PINESRD2 (507747) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0518_P1 | 3 phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply Fault at the FLOURNY2 (507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLOURNY2 (507726) 69 kV Bus to WASKOM 2 (508839) 69 kV Bus CKT 1 b. 2. Trip branch from WASKOM 2 (508839) 69 kV Bus to MVPIPET2 (508825) 69 kV Bus CKT 1 b. 3. Drop Load 1 at WASKOM 2 (508839) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0519_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to FTHUMBG4 (507731) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0520_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to MCWILLI4 (507742) 138 kV Bus CKT 1 b. 2. Trip branch from MCWILLI4 (507742) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MCWILLI4 (507742) 138 kV Bus b. 4. Drop Shunt 1 at MCWILLI4 (507742) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0521_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH1-1 (507712) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0522_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARSHILL4 (507711) 138 kV Bus to ARSHILL2 (507710) 69 kV Bus to ARSH2-1 (507714) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0523_P1 | 3 phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply Fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARSHILL4 (507711) 138 kV Bus to LIEBERM4 (508806) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0524_P1 | 3 phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply Fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIEBERM4 (508806) 138 kV Bus to IPCJEFF4 (508833) 138 kV Bus CKT 1 b. 2. Trip branch from IPCJEFF4 (508833) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IPCJEFF4 (508833) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0526_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0527_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to TENRUSK7 (508585) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0528_P1 | 3 phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply Fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TENRUSK7 (508585) 345 kV Bus to CROCKET7 (509241) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0529_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROCKET7 (509241) 345 kV Bus to 7GRIMES% (334028) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0530_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to LEASIDE 4 (507793) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0531_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to S SHV 4 (507755) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0532_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to POWELL 4 (507748) 138 kV Bus CKT 1 b. 2. Trip branch from POWELL 4 (507748) 138 kV Bus to LINWOOD4 (507738) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POWELL 4 (507748) 138 kV Bus b. 4. Drop Shunt 1 at POWELL 4 (507748) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0533_P1 | 3 phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply Fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW SHV 4 (507759) 138 kV Bus to SPRIDGE4 (507757) 138 kV Bus CKT 1 b. 2. Trip branch from SPRIDGE4 (507757) 138 kV Bus to WLNTSPRINGS4 (509103) 138 kV Bus CKT 1 b. 3. Trip branch from WLNTSPRINGS4 (509103) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SPRIDGE4 (507757) 138 kV Bus b. 5. Drop Load 2 at SPRIDGE4 (507757) 138 kV Bus b. 6. Drop Load 1 at WLNTSPRINGS4 (509103) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0534_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to CARROLL6 (500140) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0535_P1 | 3 phase fault on DOLHILL6 (500260) 230 kV Bus a. Apply Fault at the DOLHILL6 (500260) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DOLHILL6 (500260) 230 kV Bus to REDBAYOU_6 (500255) 230 kV Bus CKT 1 b. 2. Trip branch from REDBAYOU_6 (500255) 230 kV Bus to MANCOMP 6 (500525) 230 kV Bus CKT 1 b. 3. Trip branch from MANCOMP 6 (500525) 230 kV Bus to J1673 POI (46734) 230 kV Bus CKT 1 b. 4. Drop Load IN at REDBAYOU_6 (500255) 230 kV Bus b. 5. Drop Load IN at MANCOMP 6 (500525) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0536_P1 | 3 phase fault on J1673 POI (46734) 230 kV Bus a. Apply Fault at the J1673 POI (46734) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from J1673 POI (46734) 230 kV Bus to FISHER 6 (500310) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0537_P1 | 3 phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply Fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SUNNYSD7 (515136) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 588713 [G17-027-GEN10.6900], 588714 [G17-027-GEN20.6900], 588715 [G17-027-GEN30.6900], 588716 [G17-027-GEN40.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0538_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0539_P1 | 3 phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply Fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from B.BOWTP4 (510888) 138 kV Bus to B.BOW 4 (510864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at B.BOW 4 (510864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0540_P1 | 3 phase fault on SUGARHL4 (508080) 138 kV Bus a. Apply Fault at the SUGARHL4 (508080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUGARHL4 (508080) 138 kV Bus to SUGARHL2 (508079) 69 kV Bus to SHILL1-1 (508103) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0541_P1 | 3 phase fault on HOPE 3 (507453) 115 kV Bus a. Apply Fault at the HOPE 3 (507453) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOPE 3 (507453) 115 kV Bus to HOPESWI3 (507452) 115 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOPE 3 (507453) 115 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0542_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MANDEVILTP4 (508105) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0543_P1 | 3 phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply Fault at the MANDEVILTP4 (508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MANDEVILTP4 (508105) 138 kV Bus to NE-TEXARK2 (504363) 69 kV Bus to NE-TEXARK1 (504364) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0544_P1 | 3 phase fault on OKAY 4 (507428) 138 kV Bus a. Apply Fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAY 4 (507428) 138 kV Bus to OKAY 2 (507427) 69 kV Bus to OKAY1-1 (507442) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0545_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN1-1 (508097) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0546_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BANN 4 (508054) 138 kV Bus to BANN 2 (508053) 69 kV Bus to BANN2-1 (508096) 14.5 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0547_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to REDSPRG4 (508075) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0548_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to SETEXAR4 (508078) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0549_P1 | 3 phase fault on BANN 4 (508054) 138 kV Bus a. Apply Fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BANN 4 (508054) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0550_P1 | 3 phase fault on CROCKET7 (509241) 345 kV Bus a. Apply Fault at the CROCKET7 (509241) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CROCKET7 (509241) 345 kV Bus to CROCKET4 (509240) 138 kV Bus to CROCK-B1 (509243) 13.8 kV Bus CKT 1 b. 2. Trip branch from CROCKET4 (509240) 138 kV Bus to GRAPLND4 (509322) 138 kV Bus CKT 1 b. 3. Trip branch from GRAPLND4 (509322) 138 kV Bus to SLOCUM 4 (509326) 138 kV Bus CKT 1 b. 4. Trip branch from SLOCUM 4 (509326) 138 kV Bus to ALTO 4 (509320) 138 kV Bus CKT 1 b. 5. Trip branch from ALTO 4 (509320) 138 kV Bus to PINEGRV4 (509324) 138 kV Bus CKT 1 b. 6. Trip branch from PINEGRV4 (509324) 138 kV Bus to JACKSNV4 (509242) 138 kV Bus CKT 1 b. 7. Trip branch from JACKSNV4 (509242) 138 kV Bus to OVERTON4 (509080) 138 kV Bus CKT 1 b. 8. Drop Load 1 at GRAPLND4 (509322) 138 kV Bus b. 9. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 10. Drop Load 1 at SLOCUM 4 (509326) 138 kV Bus b. 11. Drop Load 1 at ALTO 4 (509320) 138 kV Bus b. 12. Drop Load 1 at PINEGRV4 (509324) 138 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0551_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 7ROCKYCRK% (334197) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0552_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_1 (334163) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at 1GRIMES_1 (334163) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0553_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from 7GRIMES% (334028) 345 kV Bus to 4GRIMES% (334026) 138 kV Bus to 1GRIMES_2 (334018) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at 1GRIMES_2 (334018) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0554_P1 | 3 phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply Fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7GRIMES% (334028) 345 kV Bus to 6GRIMES! (334027) 230 kV Bus CKT 1 b. 2. Trip branch from 6GRIMES! (334027) 230 kV Bus to 6PONDEROSA! (334088) 230 kV Bus CKT 1 b. 3. Trip three winding transformer from 6PONDEROSA! (334088) 230 kV Bus to 4PONDEROSA% (334087) 138 kV Bus to 1PONDEROSA (334094) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0555_P1 | 3 phase fault on 7ROCKYCRK% (334197) 345 kV Bus a. Apply Fault at the 7ROCKYCRK% (334197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from 7ROCKYCRK% (334197) 345 kV Bus to 6ROCKYCRK (334198) 230 kV Bus CKT 1 b. 2. Trip branch from 6ROCKYCRK (334198) 230 kV Bus to J1671 POI (46714) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0556_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LEASIDE 4 (507793) 138 kV Bus to LEASIDE 2 (507794) 69 kV Bus to LEASIDE 1-1 (507795) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0557_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to WESTELC4 (507767) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0558_P1 | 3 phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply Fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LEASIDE 4 (507793) 138 kV Bus to STONWAL4 (509052) 138 kV Bus CKT 1 b. 2. Trip branch from STONWAL4 (509052) 138 kV Bus to KEATCHI4 (509050) 138 kV Bus CKT 1 b. 3. Trip branch from KEATCHI4 (509050) 138 kV Bus to GEORPAC4 (509064) 138 kV Bus CKT 1 b. 4. Trip branch from GEORPAC4 (509064) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 b. 5. Drop Load 1 at STONWAL4 (509052) 138 kV Bus b. 6. Drop Load 1 at KEATCHI4 (509050) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0559_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to LSSOUTH4 (508297) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0560_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WELSHRE4 (508355) 138 kV Bus CKT 1 b. 2. Trip branch from WELSHRE4 (508355) 138 kV Bus to CHAPELH4 (508337) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WELSHRE4 (508355) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0561_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to SW SHV 7 (507760) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0562_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0563_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to WATLANT4 (508090) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0564_P1 | 3 phase fault on WILKES 4 (508840) 138 kV Bus a. Apply Fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 4 (508840) 138 kV Bus to MUNZCTY4 (508064) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0565_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP1 (5921) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0566_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP2 (5922) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0567_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-CAP3 (5923) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0568_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to SPP-REAC1 (5924) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0569_P1 | 3 phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply Fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPPMAINBUS (5917) 345 kV Bus to WELSHDC1 (5919) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0570_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LONGWD 7 (508809) 345 kV Bus to 7SAREPTA% (337376) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0571_P1 | 3 phase fault on DIANA 7 (508832) 345 kV Bus a. Apply Fault at the DIANA 7 (508832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 7 (508832) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0572_P1 | 3 phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply Fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LONGWD 7 (508809) 345 kV Bus to LONGWD 4 (508808) 138 kV Bus to LONGW1-1 (508819) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at LONGW1-1 (508819) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0573_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 2. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 3. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 b. 4. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 5. Drop Load 1 at NASH 4 (508049) 138 kV Bus b. 6. Drop Load 1 at ALUMAX 4 (508091) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault b. 12. Trip branch from NWTXARK4 (508071) 138 kV Bus to NASH 4 (508049) 138 kV Bus CKT 1 b. 13. Trip branch from NASH 4 (508049) 138 kV Bus to ALUMAX 4 (508091) 138 kV Bus CKT 1 b. 14. Trip branch from NASH 4 (508049) 138 kV Bus to BANN 4 (508054) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0574_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to PATTERS4 (507431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0575_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to NWT-BNT4 (508070) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0576_P1 | 3 phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply Fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWTXARK4 (508071) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0577_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to PITTSB_4 (508313) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0578_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LSSOUTH4 (508297) 138 kV Bus to DIANA 4 (508831) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0579_P1 | 3 phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply Fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LSSOUTH4 (508297) 138 kV Bus to LSSOUTH2 (508296) 69 kV Bus to LSS-1 (508325) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0580_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to PETTY 4 (508310) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0581_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WILKES 7 (508841) 345 kV Bus to WELSH 7 (508359) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0582_P1 | 3 phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply Fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAPELH4 (508337) 138 kV Bus to CHAPLHL4 (509664) 138 kV Bus CKT 1 b. 2. Trip branch from CHAPLHL4 (509664) 138 kV Bus to LIBERTH4 (509643) 138 kV Bus CKT 1 b. 3. Trip branch from LIBERTH4 (509643) 138 kV Bus to ARGO 4 (509665) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHAPLHL4 (509664) 138 kV Bus b. 5. Drop Load 1 at LIBERTH4 (509643) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0583_P1 | 3 phase fault on ARGO 4 (509665) 138 kV Bus a. Apply Fault at the ARGO 4 (509665) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARGO 4 (509665) 138 kV Bus to ARGO 2 (509642) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0584_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to PERDUE 4 (508351) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0585_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to NGPLTAP4 (508837) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0586_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to DIANASW4 (509639) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0587_P1 | 3 phase fault on DIANA 4 (508831) 138 kV Bus a. Apply Fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DIANA 4 (508831) 138 kV Bus to SPRHILL4 (508571) 138 kV Bus CKT 1 b. 2. Trip branch from SPRHILL4 (508571) 138 kV Bus to LLAMOND4 (508552) 138 kV Bus CKT 1 b. 3. Trip three winding transformer from LLAMOND4 (508552) 138 kV Bus to LLAMOND2 (508551) 69 kV Bus to LLAMON1- (508593) 13.8 kV Bus CKT 1 b. 4. Drop Load 1 at SPRHILL4 (508571) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0588_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY1-1 (508587) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0589_P1 | 3 phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply Fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PIRKEY 7 (508563) 345 kV Bus to PIRKEY 4 (508562) 138 kV Bus to PIRKY2-1 (508588) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0590_P1 | 3 phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply Fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LEBROCK7 (508572) 345 kV Bus to PIRKEY 7 (508563) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0591_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV1-1 (507778) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at SWSHV1-1 (507778) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0592_P1 | 3 phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply Fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SW SHV 7 (507760) 345 kV Bus to SW SHV 4 (507759) 138 kV Bus to SWSHV2-1 (507777) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at SWSHV2-1 (507777) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0593_P1 | 3 phase fault on HUGO 7 (521157) 345 kV Bus a. Apply Fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HUGO 7 (521157) 345 kV Bus to G16-063-TAP (560088) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0594_P1 | 3 phase fault on WILKES 7 (508841) 345 kV Bus a. Apply Fault at the WILKES 7 (508841) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WILKES 7 (508841) 345 kV Bus to WILKES 4 (508840) 138 kV Bus to WILKES-1 (508826) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at WILKES-1 (508826) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0595_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to SUGARHL4 (508080) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0596_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0597_P1 | 3 phase fault on TURK 4 (507454) 138 kV Bus a. Apply Fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TURK 4 (507454) 138 kV Bus to MANDEVILTP4 (508105) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0598_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWNR4 (507402) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWNR4 (507402) 138 kV Bus to OKAY 4 (507428) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWNR4 (507402) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0599_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PATTERS4 (507431) 138 kV Bus to ASHDWN_W 4 (504124) 138 kV Bus CKT 1 b. 2. Trip branch from ASHDWN_W 4 (504124) 138 kV Bus to CRAIGJT4 (510890) 138 kV Bus CKT 1 b. 3. Drop Load A1 at ASHDWN_W 4 (504124) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0600_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN1-1 (507443) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0601_P1 | 3 phase fault on PATTERS4 (507431) 138 kV Bus a. Apply Fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PATTERS4 (507431) 138 kV Bus to PATTERS2 (507429) 69 kV Bus to PATTN2-1 (507444) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0602_P1 | 3 phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply Fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWT-BNT4 (508070) 138 kV Bus to G18-003-TAP (762431) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0603_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PERDUE 4 (508351) 138 kV Bus to PERDUE 2 (508350) 69 kV Bus to PERDUE 1 (508356) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0604_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to EXXONM 4 (508369) 138 kV Bus CKT 1 b. 2. Trip branch from EXXONM 4 (508369) 138 kV Bus to LHAWKIN4 (508358) 138 kV Bus CKT 1 b. 3. Drop Load 1 at EXXONM 4 (508369) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0605_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to BIGSAND4 (509603) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0606_P1 | 3 phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply Fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PERDUE 4 (508351) 138 kV Bus to NEWGLAD4 (508560) 138 kV Bus CKT 1 b. 2. Trip branch from NEWGLAD4 (508560) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 b. 3. Drop Load 1 at NEWGLAD4 (508560) 138 kV Bus b. 4. Drop Shunt 1 at NEWGLAD4 (508560) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0607_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to NGPL 4 (508827) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NGPL 4 (508827) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0608_P1 | 3 phase fault on NGPLTAP4 (508837) 138 kV Bus a. Apply Fault at the NGPLTAP4 (508837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NGPLTAP4 (508837) 138 kV Bus to PLILER 4 (508564) 138 kV Bus CKT 1 b. 2. Trip branch from PLILER 4 (508564) 138 kV Bus to LONGVHT4 (508554) 138 kV Bus CKT 1 b. 3. Trip branch from LONGVHT4 (508554) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PLILER 4 (508564) 138 kV Bus b. 5. Drop Load 1 at LONGVHT4 (508554) 138 kV Bus b. 6. Drop Shunt 1 at LONGVHT4 (508554) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0609_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to MARSHL-4 (508557) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0610_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to SABMINT4 (508566) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0611_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to HALLSVLS4 (508595) 138 kV Bus CKT 1 b. 2. Trip branch from HALLSVLS4 (508595) 138 kV Bus to WHITNEY4 (508575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HALLSVLS4 (508595) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0612_P1 | 3 phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply Fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PIRKEY 4 (508562) 138 kV Bus to EASTON 4 (509092) 138 kV Bus CKT 1 b. 2. Trip branch from EASTON 4 (509092) 138 kV Bus to BRANDYBR (508596) 138 kV Bus CKT 1 b. 3. Trip branch from BRANDYBR (508596) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 4. Drop Load 1 at EASTON 4 (509092) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0613_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#11 (508591) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0614_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MARSHL-4 (508557) 138 kV Bus to MARAUTO2 (508576) 69 kV Bus to MRSH4#21 (508592) 12.47 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0615_P1 | 3 phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply Fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARSHL-4 (508557) 138 kV Bus to JEFFRSN4 (508835) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0616_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to CHEROKE4 (509059) 138 kV Bus CKT 1 b. 2. Trip branch from CHEROKE4 (509059) 138 kV Bus to TATUM 4 (509087) 138 kV Bus CKT 1 b. 3. Trip branch from TATUM 4 (509087) 138 kV Bus to ROKHILL4 (509083) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHEROKE4 (509059) 138 kV Bus b. 5. Drop Load 1 at TATUM 4 (509087) 138 kV Bus b. 6. Drop Load 2 at TATUM 4 (509087) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0617_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to OAK2HIL4 (509078) 138 kV Bus CKT 1 b. 2. Trip branch from OAK2HIL4 (509078) 138 kV Bus to OAK1HIL4 (509077) 138 kV Bus CKT 1 b. 3. Trip branch from OAK1HIL4 (509077) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 4. Drop Load 1 at OAK2HIL4 (509078) 138 kV Bus b. 5. Drop Load 1 at OAK1HIL4 (509077) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0618_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SABINEM4 (508577) 138 kV Bus CKT 1 b. 2. Drop Load 1 at SABINEM4 (508577) 138 kV Bus b. 3. Drop Load 2 at SABINEM4 (508577) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0619_P1 | 3 phase fault on SABMINT4 (508566) 138 kV Bus a. Apply Fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SABMINT4 (508566) 138 kV Bus to SEMRSHL4 (508569) 138 kV Bus CKT 1 b. 2. Trip branch from SEMRSHL4 (508569) 138 kV Bus to SCOTTSV4 (508567) 138 kV Bus CKT 1 b. 3. Trip branch from SCOTTSV4 (508567) 138 kV Bus to LONGWD 4 (508808) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SEMRSHL4 (508569) 138 kV Bus b. 5. Drop Load 1 at SCOTTSV4 (508567) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0620_P4 | a. Apply single phase fault at 3SAREPTA! (337363) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3SAREPTA! (337363) 115 kV to 7SAREPTA% (337376) 345 kV CKT 1 b. 2. Trip branch from 3SAREPTA! (337363) 115 kV to 3MINDEN_LA! (337361) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0621_P4 | a. Apply single phase fault at 3STERLING% (337415) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3STERLING% (337415) 115 kV to 8STERLING% (337420) kV to 1STERLING3 (337412) 13.8 kV CKT3 b. 2. Trip branch from 3STERLING% (337415) 115 kV to 8STERLING2% (337413) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0622_P4 | a. Apply single phase fault at 3STERL2% (337414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3STERL2% (337414) 115 kV to 3DREW_LA (337382) 115 kV CKT 1 b. 2. Trip branch from 3DREW_LA (337382) 115 kV to 3CHENIERE (337383) 115 kV CKT 1 b. 3. Trip branch from 3CHENIERE (337383) 115 kV to 3RISER (337384) 115 kV CKT 1 b. 4. Trip branch from 3RISER (337384) 115 kV to 3FROSTKRAFT! (337385) 115 kV CKT 1 b. 5. Trip branch from 3STERL2% (337414) 115 kV to 8STERLING2% (337413) 500 kV CKT 2 b. 6. Drop Load 1 3DREW_LA (337382) 115 kV b. 7. Drop Load 1 3CHENIERE (337383) 115 kV b. 8. Drop Load 1 3RISER (337384) 115 kV b. 9. Drop Shunt 1 3SHULER (337521) 115 kV b. 10. Drop Shunt 1 3RISER (337384) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0623_P4 | a. Apply single phase fault at 8EL DORADO% (337561) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8EL DORADO% (337561) 500 kV to 8MT_OLIVE% (337368) 500 kV CKT 1 b. 2. Trip branch from 8EL DORADO% (337561) 500 kV to 8STERLING% (337420) 500 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0624_P4 | a. Apply single phase fault at LIEBERM4 (508806) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LIEBERM4 (508806) 138 kV to LONGWD 4 (508808) 138 kV CKT 1 b. 2. Trip branch from LIEBERM4 (508806) 138 kV to G16-167-TAP (588404) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0625_P4 | a. Apply single phase fault at 3MINDEN_LA! (337361) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3SAREPTA! (337363) 115 kV CKT 1 b. 2. Trip branch from 3MINDEN_LA! (337361) 115 kV to 3MINDEN_LG (303302) 115 kV CKT 1 b. 3. Trip branch from 3MINDEN_LG (303302) 115 kV to 3ARCADIA (337367) 115 kV CKT 1 b. 4. Trip branch from 3ARCADIA (337367) 115 kV to 3REESE (337380) 115 kV CKT 1 b. 5. Trip branch from 3REESE (337380) 115 kV to 3TRUSSEL_CR (303310) 115 kV CKT 1 b. 6. Trip branch from 3TRUSSEL_CR (303310) 115 kV to 3VIENNA_LA! (337371) 115 kV CKT 1 b. 7. Drop Load 1 3MINDEN_LG (303302) 115 kV b. 8. Drop Load 1 3ARCADIA (337367) 115 kV b. 9. Drop Load LG 3ARCADIA (337367) 115 kV b. 10. Drop Load IN 3REESE (337380) 115 kV b. 11. Drop Load 1 3TRUSSEL_CR (303310) 115 kV b. 12. Drop Shunt 1 3MINDEN_LG (303302) 115 kV b. 13. Drop Load 1 3ARCADIA (337367) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0626_P4 | a. Apply single phase fault at 3EL DORADO! (337539) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from 3EL DORADO! (337539) 115 kV to 8EL DORADO% (337561) kV to 1EL DORADO1 (337564) 13.8 kV CKT1 b. 2. Trip branch from 3EL DORADO! (337539) 115 kV to 3ELDORADO.E! (337553) 115 kV CKT 1 b. 3. Drop Shunt 1 1EL DORADO1 (337564) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0627_P4 | a. Apply single phase fault at ARSHILL4 (507711) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ARSHILL4 (507711) 138 kV to FTHUMBG4 (507731) 138 kV CKT 1 b. 2. Trip three winding transformer from ARSHILL4 (507711) 138 kV to ARSHILL2 (507710) kV to ARSH1-1 (507712) 12.47 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0628_P4 | a. Apply single phase fault at 3MCNEIL! (337516) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 3MCNEIL! (337516) 115 kV to 8MCNEIL% (337515) 500 kV CKT 1 b. 2. Trip branch from 3MCNEIL! (337516) 115 kV to 3MAGNOLIA.W (337519) 115 kV CKT 1 b. 3. Trip branch from 3MAGNOLIA.W (337519) 115 kV to 3MAGNOLIA.S (337520) 115 kV CKT 1 b. 4. Trip branch from 3MAGNOLIA.S (337520) 115 kV to 3SHULER (337521) 115 kV CKT 1 b. 5. Trip branch from 3SHULER (337521) 115 kV to 3WYATT! (337544) 115 kV CKT 1 b. 6. Drop Load IN 3MAGNOLIA.W (337519) 115 kV b. 7. Drop Load 1 3MAGNOLIA.S (337520) 115 kV b. 8. Drop Load IN 3SHULER (337521) 115 kV b. 9. Drop Load 1 3SHULER (337521) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0629_P4 | a. Apply single phase fault at 8STERLING2% (337413) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8STERLING2% (337413) 500 kV to 8PERRYVILLE% (337427) 500 kV CKT 1 b. 2. Trip branch from 8STERLING2% (337413) 500 kV to 8STERLING% (337420) 500 kV CKT Z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0630_P4 | a. Apply single phase fault at 8PERRYVILLE% (337427) 500 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8BXTRWILSON% (336830) 500 kV CKT 1 b. 2. Trip branch from 8PERRYVILLE% (337427) 500 kV to 8STERLING% (337420) 500 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0631_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G16-091-TAP (587744) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0632_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0633_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0634_P1 | 3 phase fault on MINCO 7 (514801) 345 kV Bus a. Apply Fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MINCO 7 (514801) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 515439 [MNCOWNG3 0.6900], 515445 [MNCOWNG2 0.6900], 515551 [MINCO-WTG32 0.6900], 515907 [MNCOWNG1 0.6900], 599117 [MINCO-WTG31 0.6900], 599119 [MINCO-WTG33 0.6900], 599120 [MINCO-WTG34 0.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0635_P1 | 3 phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply Fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-037-TAP (560078) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0636_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0637_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0638_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0639_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 b. 2. Drop Shunt 1 at OKLAUN HVDC7 (511565) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0640_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0641_P1 | 3 phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply Fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-171-TAP (760938) 345 kV Bus to TERRYRD7 (511568) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0642_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to G18-015-TAP (762467) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0643_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0644_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV Bus to G17-171-TAP (760938) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0645_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0646_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from NSUB345 (555234) 345 kV Bus to CIMARON7 (514901) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0647_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750000) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0648_P1 | 3 phase fault on NSUB345 (555234) 345 kV Bus a. Apply Fault at the NSUB345 (555234) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NSUB345 (555234) 345 kV Bus to PLVALLY4 (514929) 138 kV Bus to NEWBUS13.8 (750001) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0649_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0650_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#4-1 (511414) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0651_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0652_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0653_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO11 (515714) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO11 (515714) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0654_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CIMARON7 (514901) 345 kV Bus to CIMARON4 (514898) 138 kV Bus to CIMARO21 (515715) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at CIMARO21 (515715) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0655_P1 | 3 phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply Fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-7 (511468) 345 kV Bus to L.E.S.-4 (511467) 138 kV Bus to LES#5-1 (511411) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at LES#4-1 (511414) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0656_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to FLETCHR4 (511422) 138 kV Bus CKT 1 b. 2. Drop Load 1 at FLETCHR4 (511422) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0657_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0658_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to L.E.S.-4 (511467) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0659_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to ELGINJT4 (511486) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0660_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to LWSTAP 4 (511439) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0661_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to SHERID4 (511474) 138 kV Bus CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV Bus to ARTVLTP4 (511537) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SHERID4 (511474) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0662_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV Bus to COMMTAP4 (511494) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0663_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#1-1 (511416) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0664_P1 | 3 phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply Fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV Bus to L.E.S.-2 (511466) 69 kV Bus to LES#2-1 (511415) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0665_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to WASHITA4 (521089) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0666_P1 | 3 phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply Fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G16-091-TAP (587744) 345 kV Bus to GRACMNT7 (515800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 587773 [G16-095-GEN10.6900], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0667_P1 | 3 phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply Fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT4 (515802) 138 kV Bus to ANADARK4 (520814) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 520522 [BCVI_WTG1 0.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0668_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to COMANC-4 (511437) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0669_P1 | 3 phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply Fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMMTAP4 (511494) 138 kV Bus to OMDUNCN4 (529304) 138 kV Bus CKT 1 b. 2. Trip branch from OMDUNCN4 (529304) 138 kV Bus to DUNCAN-4 (511453) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0670_P1 | 3 phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply Fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLE TAP4 (511423) 138 kV Bus to G16-097-TAP (587794) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0671_P1 | 3 phase fault on COMANC-4 (511437) 138 kV Bus a. Apply Fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COMANC-4 (511437) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0672_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to LWS S4 (511431) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LWS S4 (511431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0673_P1 | 3 phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply Fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LWSTAP 4 (511439) 138 kV Bus to RPPAPER4 (511512) 138 kV Bus CKT 1 b. 2. Trip branch from RPPAPER4 (511512) 138 kV Bus to 112GORE4 (511488) 138 kV Bus CKT 1 b. 3. Drop Load 1 at RPPAPER4 (511512) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0674_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELGINJT4 (511486) 138 kV Bus to ELSWORTH 4 (511563) 138 kV Bus CKT 1 b. 2. Trip branch from ELSWORTH 4 (511563) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ELSWORTH 4 (511563) 138 kV Bus b. 4. Drop Load 2 at ELSWORTH 4 (511563) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0675_P1 | 3 phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply Fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELGINJT4 (511486) 138 kV Bus to ELGINJT2 (511487) 69 kV Bus to ELGJT1-1 (511412) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0676_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to SEQUOYAHJ4 (520422) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0677_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to MINCO 7 (514801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0678_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CLVLDSW4 (520508) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0679_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to CHERRYRD 4 (521129) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0680_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to POCASET4 (521031) 138 kV Bus CKT 1 b. 2. Trip branch from POCASET4 (521031) 138 kV Bus to TUTLETP4 (521072) 138 kV Bus CKT 1 b. 3. Drop Load 1 at POCASET4 (521031) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0681_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANADARK4 (520814) 138 kV Bus to GEORGIA4 (520923) 138 kV Bus CKT 1 b. 2. Trip branch from GEORGIA4 (520923) 138 kV Bus to FLETCH-4 (520912) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GEORGIA4 (520923) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0682_P1 | 3 phase fault on ANADARK4 (520814) 138 kV Bus a. Apply Fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANADARK4 (520814) 138 kV Bus to ANADARK2 (520810) 69 kV Bus to ADRKTERT (521181) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0683_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to S.W.S.-4 (511477) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0685_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WASHITA4 (521089) 138 kV Bus to WASHITA2 (521088) 69 kV Bus to WASHTERT (521179) 7.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0686_P1 | 3 phase fault on WASHITA4 (521089) 138 kV Bus a. Apply Fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WASHITA4 (521089) 138 kV Bus to ONEY 4 (521017) 138 kV Bus CKT 1 b. 2. Trip branch from ONEY 4 (521017) 138 kV Bus to BINGERJ4 (520827) 138 kV Bus CKT 1 b. 3. Drop Load 1 at ONEY 4 (521017) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 599003 [BLUCAN2-WTG50.6900], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0687_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from GRACMNT7 (515800) 345 kV Bus to G16-037-TAP (560078) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0688_P1 | 3 phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply Fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRACMNT7 (515800) 345 kV Bus to GRACMNT4 (515802) 138 kV Bus to GRCMNT11 (515801) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at GRCMNT11 (515801) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587793 [G16-097-GEN10.6900], 761232 [G17-150GEN1 0.6600], 762903 [G18-055-GEN10.6600], 920001 [BLUCAN2-WTG10.6900], 920002 [BLUCAN2-WTG20.6900], 920003 [BLUCAN2-WTG30.6900], 920004 [BLUCAN2-WTG40.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0689_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 2. Trip branch from L.E.S.-4 (511467) 138 kV to COMMTAP4 (511494) 138 kV CKT 1 b. 3. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0690_P4 | a. Apply single phase fault at MINCO 7 (514801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MINCO 7 (514801) 345 kV to NSUB345 (555234) kV CKT 1 b. 2. Trip branch from MINCO 7 (514801) 345 kV to GRACMNT7 (515800) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0691_P4 | a. Apply single phase fault at GRACMNT4 (515802) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GRACMNT4 (515802) 138 kV to GRACMNT7 (515800) kV to GRCMNT11 (515801) 13.8 kV CKT2 b. 2. Trip branch from GRACMNT4 (515802) 138 kV to ANADARK4 (520814) 138 kV CKT 1 b. 3. Drop Shunt 1 GRCMNT11 (515801) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0692_P4 | a. Apply single phase fault at L.E.S.-2 (511466) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from L.E.S.-2 (511466) 69 kV to L.E.S.-4 (511467) kV to LES#1-1 (511416) 13.8 kV CKT1 b. 2. Trip branch from L.E.S.-2 (511466) 69 kV to LGORE-S2 (511470) 69 kV CKT 1 b. 3. Trip branch from LGORE-S2 (511470) 69 kV to LAW WC2 (511503) 69 kV CKT 1 b. 4. Drop Load 1 LGORE-S2 (511470) 69 kV b. 5. Drop Load 1 LAW WC2 (511503) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0693_P4 | a. Apply single phase fault at 112GORE4 (511488) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 112GORE4 (511488) 138 kV to COMANC-4 (511437) 138 kV CKT 1 b. 2. Trip branch from 112GORE4 (511488) 138 kV to LAIRGST4 (511510) 138 kV CKT 1 b. 3. Trip branch from LAIRGST4 (511510) 138 kV to CACHE4 (511500) 138 kV CKT 1 b. 4. Trip branch from LAIRGST4 (511510) 138 kV to L AIRGS4 (511429) 138 kV CKT 1 b. 5. Trip branch from CACHE4 (511500) 138 kV to G17-036_TAP (588779) 138 kV CKT 1 b. 6. Drop Load 1 CACHE4 (511500) 138 kV b. 7. Drop Load 1 L AIRGS4 (511429) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0694_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0696_P4 | a. Apply single phase fault at ELKCTY-4 (511458) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ELKCTY-4 (511458) 138 kV to CLINTJC4 (511485) 138 kV CKT 1 b. 2. Trip branch from ELKCTY-4 (511458) 138 kV to REDHLSW4 (521116) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0697_P4 | a. Apply single phase fault at WWRDEHV4 (515376) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from WWRDEHV4 (515376) 138 kV to WWRDEHV7 (515375) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 2. Trip branch from WWRDEHV4 (515376) 138 kV to IODINE-4 (514796) 138 kV CKT 1 b. 3. Trip branch from IODINE-4 (514796) 138 kV to REDCLFT4 (515533) 138 kV CKT 1 b. 4. Trip branch from REDCLFT4 (515533) 138 kV to DEWEY 4 (514787) 138 kV CKT 1 b. 5. Trip branch from REDCLFT4 (515533) 138 kV to REDCLF 4 (515863) 138 kV CKT 1 b. 6. Drop Load 1 IODINE-4 (514796) 138 kV b. 7. Drop Load 1 REDCLF 4 (515863) 138 kV b. 8. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0698_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TOLK 6 (525531) 230 kV to TOLK 7 (525549) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 2. Trip branch from TOLK 6 (525531) 230 kV to PLANT_X 6 (525481) 230 kV CKT 2 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0699_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0700_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0701_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0702_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WHEELER 6 (523777) 230 kV Bus to WHEELER 3 (523776) 115 kV Bus to WHEELER_TR11 (523774) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0703_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0704_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to GRAPEVINE 6 (523771) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0705_P1 | 3 phase fault on GRAPEVINE 6 (523771) 230 kV Bus a. Apply Fault at the GRAPEVINE 6 (523771) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GRAPEVINE 6 (523771) 230 kV Bus to GRAPEVINE 3 (523770) 115 kV Bus to GRAPEVN_TR11 (523769) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0706_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0707_P1 | 3 phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply Fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTTER_CO 7 (523961) 345 kV Bus to POTTER_CO 6 (523959) 230 kV Bus to POTTER_TR 1 (523957) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at POTTER_TR 1 (523957) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0708_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0709_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0710_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0711_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ELKCITY6 (511490) 230 kV Bus to CHISHOLM6 (511557) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0712_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0713_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0714_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0715_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0716_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0717_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0718_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0719_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF3 (525539) kV Bus CKT 3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0720_P1 | 3 phase fault on WHEELER 6 (523777) 230 kV Bus a. Apply Fault at the WHEELER 6 (523777) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 6 (523777) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0721_P4 | a. Apply single phase fault at CLARMR 5 (512651) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 4 (512707) kV to CLARMR4 (512813) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 4 (512707) 138 kV to OOLOGAHKM 4 (513124) 138 kV CKT 1 b. 3. Trip branch from OOLOGAHKM 4 (513124) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 4. Trip three winding transformer from CLARMR 5 (512651) 161 kV to CLARMR 2 (512679) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 5. Drop Load 1 OOLOGAHKM 4 (513124) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0722_P4 | a. Apply single phase fault at 4SILVCTY (300140) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 4SILVCTY (300140) 138 kV to 4BRISTOW (300137) 138 kV CKT 1 b. 2. Trip branch from 4SILVCTY (300140) 138 kV to SILVCTYGR4 (512726) 138 kV CKT 1 b. 3. Trip branch from SILVCTYGR4 (512726) 138 kV to WEKIWA-4 (509757) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0723_P4 | a. Apply single phase fault at GORE GR2 (512644) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from GORE GR2 (512644) 69 kV to GORE 5 (505552) kV to GORTER1 (512832) 13.8 kV CKT1 b. 2. Trip branch from GORE GR2 (512644) 69 kV to 2VIAN (300879) 69 kV CKT 1 b. 3. Drop Load 1 2VIAN (300879) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0724_P4 | a. Apply single phase fault at CATSAGR5 (512638) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATSAGR5 (512638) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to COLINS 5 (512627) 161 kV CKT 1 b. 3. Trip branch from CATSAGR5 (512638) 161 kV to MAID 5 (512648) 161 kV CKT 1 b. 4. Drop Load 1 5ELMCRK (300993) 161 kV b. 5. Drop Load 2 5ELMCRK (300993) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0725_P4 | a. Apply single phase fault at CLARMR 2 (512679) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CLARMR 2 (512679) 69 kV to CLARMR 5 (512651) kV to CLARMR1 (512814) 13.8 kV CKT1 b. 2. Trip branch from CLARMR 2 (512679) 69 kV to CLARCTY4 2 (513014) 69 kV CKT 1 b. 3. Trip branch from CLARCTY4 2 (513014) 69 kV to CLARCTY1 2 (513010) 69 kV CKT 1 b. 4. Drop Load 1 CLARCTY4 2 (513014) 69 kV b. 5. Drop Load 1 CLARCTY1 2 (513010) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0726_P4 | a. Apply single phase fault at CATOOSA4 (509790) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CATOOSA4 (509790) 138 kV to TERNITP4 (509835) 138 kV CKT 1 b. 2. Trip branch from TERNITP4 (509835) 138 kV to TER-NIT4 (509723) 138 kV CKT 1 b. 3. Trip branch from TERNITP4 (509835) 138 kV to VERDIGS4 (509854) 138 kV CKT 1 b. 4. Trip branch from VERDIGS4 (509854) 138 kV to CLARTOK4 (509864) 138 kV CKT 1 b. 5. Trip branch from CLARTOK4 (509864) 138 kV to N.E.S.-4 (510396) 138 kV CKT 1 b. 6. Trip branch from CATOOSA4 (509790) 138 kV to INOLATP4 (509752) 138 kV CKT 1 b. 7. Trip branch from INOLATP4 (509752) 138 kV to INOLA 4 (509736) 138 kV CKT 1 b. 8. Trip branch from INOLATP4 (509752) 138 kV to ROCKPT-4 (510437) 138 kV CKT 1 b. 9. Trip branch from ROCKPT-4 (510437) 138 kV to CHOUTEA4 (510373) 138 kV CKT 1 b. 10. Trip branch from CHOUTEA4 (510373) 138 kV to EXCLART4 (510401) 138 kV CKT 1 b. 11. Drop Load 1 TER-NIT4 (509723) 138 kV b. 12. Drop Shunt 1 TER-NIT4 (509723) 138 kV b. 13. Drop Load M1 VERDIGS4 (509854) 138 kV b. 14. Drop Load M2 VERDIGS4 (509854) 138 kV b. 15. Drop Load 1 CLARTOK4 (509864) 138 kV b. 16. Drop Load 1 INOLA 4 (509736) 138 kV b. 17. Drop Load 1 ROCKPT-4 (510437) 138 kV b. 18. Drop Load 1 CHOUTEA4 (510373) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0727_P4 | a. Apply single phase fault at COLINS 5 (512627) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from COLINS 5 (512627) 161 kV to 5ELMCRK (300993) 161 kV CKT 1 b. 2. Trip branch from 5ELMCRK (300993) 161 kV to CATSAGR5 (512638) 161 kV CKT 1 b. 3. Trip branch from COLINS 5 (512627) 161 kV to 5KETONVL (300997) 161 kV CKT 1 b. 4. Trip branch from 5KETONVL (300997) 161 kV to CLARMR 5 (512651) 161 kV CKT 1 b. 5. Drop Load 2 5ELMCRK (300993) 161 kV b. 6. Drop Load 1 5KETONVL (300997) 161 kV b. 7. Drop Load 2 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0728_P4 | a. Apply single phase fault at HUNT 2 (512671) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HUNT 2 (512671) 69 kV to MAIDTP2 (512625) 69 kV CKT 1 b. 2. Trip branch from MAIDTP2 (512625) 69 kV to GRDA1 2 (512727) 69 kV CKT 1 b. 3. Trip three winding transformer from GRDA1 2 (512727) 69 kV to GRDA1 5 (512656) kV to GRDA1 1 (512816) 13.8 kV CKT1 b. 4. Trip branch from HUNT 2 (512671) 69 kV to PRY0RC22 (512639) 69 kV CKT 1 b. 5. Trip branch from PRY0RC22 (512639) 69 kV to PRYORC32 (512622) 69 kV CKT 1 b. 6. Trip branch from PRYORC32 (512622) 69 kV to PRYORC12 (512810) 69 kV CKT 1 b. 7. Drop Load 1 PRY0RC22 (512639) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0729_P4 | a. Apply single phase fault at COLNSGR2 (512870) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from COLNSGR2 (512870) 69 kV to COLINS 5 (512627) kV to COLLIN3 1 (512840) 13.8 kV CKT2 b. 2. Trip branch from COLNSGR2 (512870) 69 kV to PARKMEDTP (512703) 69 kV CKT 1 b. 3. Trip branch from PARKMEDTP (512703) 69 kV to 2PARKMDWS (301999) 69 kV CKT 1 b. 4. Trip branch from PARKMEDTP (512703) 69 kV to SKIATTP2 (512871) 69 kV CKT 1 b. 5. Drop Load 1 2PARKMDWS (301999) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0730_P4 | a. Apply single phase fault at SPRGFLD5 (505492) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SPRGFLD5 (505492) 161 kV to BROOKLINE 5 (549969) 161 kV CKT 1 b. 2. Trip branch from SPRGFLD5 (505492) 161 kV to CLAY 5 (549970) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0731_P4 | a. Apply single phase fault at JTEC 5 (549954) 161 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JTEC 5 (549954) 161 kV to SW DISP PLT5 (549960) 161 kV CKT 1 b. 2. Trip branch from SW DISP PLT5 (549960) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 b. 3. Trip branch from JTEC 5 (549954) 161 kV to 5BTLFD (300348) 161 kV CKT 1 b. 4. Trip branch from 5BTLFD (300348) 161 kV to 5JAMESV (300089) 161 kV CKT 1 b. 5. Drop Load W SW DISP PLT5 (549960) 161 kV b. 6. Drop Load E SW DISP PLT5 (549960) 161 kV b. 7. Drop Load E 5KETONVL (300997) 161 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0732_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to 2CDRCRST (301345) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0733_P1 | 3 phase fault on SHIPERD7 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 (506979) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SHIPERD7 (506979) 345 kV Bus to SHIPERD5 (506980) 161 kV Bus to SHIPERD1 (506981) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0734_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to BENTON 7 (532791) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0735_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0736_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WOLFCRK7 (532797) 345 kV Bus to W.GRDNR7 (542965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0737_P1 | 3 phase fault on WOLFCRK7 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFCRK7 (532797) 345 kV Bus to WOLFCRK2 (533653) 69 kV Bus to WOLFCRK1 (532962) 17 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0738_P1 | 3 phase fault on LACYGNE7 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LACYGNE7 (542981) 345 kV Bus to WAVERLY7 (532799) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0739_P1 | 3 phase fault on G17-009-TAP (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-009-TAP (532777) 345 kV Bus to CANEYRV7 (532780) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0740_P1 | 3 phase fault on CLARMR 5 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLARMR 5 (512651) 161 kV Bus to CLARMR 4 (512707) 138 kV Bus to CLARMR4 (512813) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0741_P1 | 3 phase fault on FT GIB 5 (505560) 161 kV Bus a. Apply Fault at the FT GIB 5 (505560) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FT GIB 5 (505560) 161 kV Bus to OKAYGR 5 (512640) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0742_P1 | 3 phase fault on OKAYGR 5 (512640) 161 kV Bus a. Apply Fault at the OKAYGR 5 (512640) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OKAYGR 5 (512640) 161 kV Bus to OKAYGR 2 (512646) 69 kV Bus to OKAY1 (512848) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0743_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENSA 5 (512654) 161 kV Bus to KETCHUM5 (512669) 161 kV Bus CKT 1 b. 2. Trip branch from KETCHUM5 (512669) 161 kV Bus to AFTON 5 (512632) 161 kV Bus CKT 1 b. 3. Drop Load 1 at KETCHUM5 (512669) 161 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0744_P1 | 3 phase fault on PENSA 5 (512654) 161 kV Bus a. Apply Fault at the PENSA 5 (512654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENSA 5 (512654) 161 kV Bus to PENSA 2 (512628) 69 kV Bus to PENSA 1 (512841) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0745_P1 | 3 phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply Fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 5CDRCRST (301344) 161 kV Bus to TAHLQH 5 (512655) 161 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0746_P4 | a. Apply single phase fault at TATONGA7 (515407) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TATONGA7 (515407) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from TATONGA7 (515407) 345 kV to WWRDEHV7 (515375) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0747_P4 | a. Apply single phase fault at HARPER 4 (539668) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HARPER 4 (539668) 138 kV to FLATRDG4 (539638) 138 kV CKT 1 b. 2. Trip branch from HARPER 4 (539668) 138 kV to MILANTP4 (539675) 138 kV CKT 1 b. 3. Trip branch from MILANTP4 (539675) 138 kV to CONWAY (539009) 138 kV CKT 1 b. 4. Trip branch from CONWAY (539009) 138 kV to VIOLA 4 (533075) 138 kV CKT 1 b. 5. Drop Load 1 CONWAY (539009) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0748_P4 | a. Apply single phase fault at DGRASSE7 (515852) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE7 (515852) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from DGRASSE7 (515852) 345 kV to WWRDEHV7 (515375) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0749_P4 | a. Apply single phase fault at MATHWSN7 (515497) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MATHWSN7 (515497) 345 kV to CIMARON7 (514901) 345 kV CKT 2 b. 2. Trip branch from MATHWSN7 (515497) 345 kV to TATONGA7 (515407) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0750_P4 | a. Apply single phase fault at BADGER 7 (515677) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 1 b. 2. Trip branch from BADGER 7 (515677) 345 kV to BOBCAT 7 (516106) kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0751_P4 | a. Apply single phase fault at THISTLE7 (539801) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from THISTLE7 (539801) 345 kV to CLARKCOUNTY7 (539800) 345 kV CKT 1 b. 2. Trip branch from THISTLE7 (539801) 345 kV to BUFFALO7 (532782) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0752_P4 | a. Apply single phase fault at DGRASSE4 (515853) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DGRASSE4 (515853) 138 kV to KNOBHIL4 (514795) 138 kV CKT 1 b. 2. Trip branch from DGRASSE4 (515853) 138 kV to ROSEVLY4 (520436) 138 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0753_P4 | a. Apply single phase fault at CIMARON7 (514901) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CIMARON7 (514901) 345 kV to MATHWSN7 (515497) 345 kV CKT 2 b. 2. Trip branch from CIMARON7 (514901) 345 kV to NSUB345 (555234) kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0754_P4 | a. Apply single phase fault at CLARKCOUNTY7 (539800) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV to THISTLE7 (539801) 345 kV CKT 1 b. 2. Trip branch from CLARKCOUNTY7 (539800) 345 kV to SPERVIL7 (531469) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0755_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to WWDBORDT (755000) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0756_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV21 (515799) 13.8 kV Bus CKT 2 b. 2. Drop Shunt 1 at WWDEHV21 (515799) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0758_P1 | 3 phase fault on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from FINNEY 7 (523853) 345 kV Bus to HOLCOMB7 (531449) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0761_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TR 1 (525537) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TOLK_TR 1 (525537) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0762_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TOLK 7 (525549) 345 kV Bus to TOLK 6 (525531) 230 kV Bus to TOLK_TF2 (525538) kV Bus CKT 2 b. 2. Drop Shunt 1 at TOLK_TF2 (525538) kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0763_P1 | 3 phase fault on OCHILTREE 6 (523155) 230 kV Bus a. Apply Fault at the OCHILTREE 6 (523155) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OCHILTREE 6 (523155) 230 kV Bus to OCHILTREE 3 (523154) 115 kV Bus to OCHLTRE_TR11 (523151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0764_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to HARPER 4 (539668) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0765_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0766_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WWRDEHV7 (515375) 345 kV Bus to WWRDEHV4 (515376) 138 kV Bus to WWDEHV31 (515795) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at WWDEHV31 (515795) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0767_P1 | 3 phase fault on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FLATRDG4 (539638) 138 kV Bus to BARBER 4 (539674) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0768_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to SETAB 7 (531465) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0769_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOLCOMB7 (531449) 345 kV Bus to HOLCOMB3 (531448) 115 kV Bus to HOLCTER1 (531450) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at HOLCTER1 (531450) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0770_P1 | 3 phase fault on HOLCOMB7 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus to BUCKNER7 (531501) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0771_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0772_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to CIM-PLT3 (539654) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0773_P1 | 3 phase fault on WALKMYR3 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WALKMYR3 (531405) 115 kV Bus to HUGOTON3 (531481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0774_P1 | 3 phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply Fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from REDCLFT4 (515533) 138 kV Bus to REDCLF 4 (515863) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0775_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI31 (515704) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI31 (515704) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0776_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI21 (515703) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0777_P1 | 3 phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply Fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ARCADIA7 (514908) 345 kV Bus to ARCADIA4 (514907) 138 kV Bus to ARCADI41 (515700) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at ARCADI21 (515703) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0778_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0779_P1 | 3 phase fault on SPERVIL7 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from SPERVIL7 (531469) 345 kV Bus to IRONWOOD7 (539803) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0780_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to LAMB_CNTY 6 (525637) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_TR3 1 (525633) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0781_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0782_P1 | 3 phase fault on OCHILTREE 3 (523154) 115 kV Bus a. Apply Fault at the OCHILTREE 3 (523154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OCHILTREE 3 (523154) 115 kV Bus to PERRYTON 3 (523158) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0783_P1 | 3 phase fault on CIM-PLT3 (539654) 115 kV Bus a. Apply Fault at the CIM-PLT3 (539654) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIM-PLT3 (539654) 115 kV Bus to N-CIMRN3 (539749) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0784_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0785_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0786_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to CHISHOLM7 (511553) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0787_P1 | 3 phase fault on WWDBORDT (755000) 345 kV Bus a. Apply Fault at the WWDBORDT (755000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus to BORDER 7 (515458) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0788_P1 | 3 phase fault on BORDER 7 (515458) 345 kV Bus a. Apply Fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BORDER 7 (515458) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0789_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0790_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0791_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0792_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM7 (511553) 345 kV Bus to GRAPEVINE (560035) 345 kV Bus CKT 1 b. 2. Trip branch from GRAPEVINE (560035) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0793_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0794_P1 | 3 phase fault on TATONGA7 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TATONGA7 (515407) 345 kV Bus to MATHWSN7 (515497) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0796_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to REDNGTN7 (515875) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0797_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0798_P1 | 3 phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply Fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from MATHWSN7 (515497) 345 kV Bus to NORTWST7 (514880) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0799_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS41 (514885) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS41 (514885) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0800_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS31 (515743) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS31 (515743) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0801_P1 | 3 phase fault on NORTWST7 (514880) 345 kV Bus a. Apply Fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTWST7 (514880) 345 kV Bus to NORTWST4 (514879) 138 kV Bus to NORTWS21 (515742) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at NORTWS21 (515742) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0802_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0803_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to BVRCNTY7 (515554) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0804_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to BADGER 7 (515677) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0805_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0806_P1 | 3 phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus to HITCHLAND 7 (523097) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0807_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0808_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE7 (515852) 345 kV Bus to THISTLE7 (539801) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0809_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0810_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to BUFFALO7 (532782) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0811_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to TATONGA7 (515407) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0812_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from THISTLE7 (539801) 345 kV Bus to THISTLE4 (539804) 138 kV Bus to THISTLE T1 (539802) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0813_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0814_P1 | 3 phase fault on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE7 (539801) 345 kV Bus to CLARKCOUNTY7 (539800) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0815_P1 | 3 phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DGRASSE7 (515852) 345 kV Bus to DGRASSE4 (515853) 138 kV Bus to DGRASSE1 (515854) 13.8 kV Bus CKT 1 b. 2. Drop Shunt 1 at DGRASSE1 (515854) 13.8 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0816_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0817_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0818_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0819_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0820_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR21 (523094) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0821_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 7 (523097) 345 kV Bus to HITCHLAND 6 (523095) 230 kV Bus to HITCHLD_TR01 (523091) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0822_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0823_P1 | 3 phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHISHOLM7 (511553) 345 kV Bus to CHISHOLM6 (511557) 230 kV Bus to CHISHOLM1 (511558) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at CHISHOLM1 (511558) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0824_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to ELKCITY6 (511490) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0825_P1 | 3 phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 (511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHISHOLM6 (511557) 230 kV Bus to SWEETWT6 (511541) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0826_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to FINNEY 7 (523853) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0827_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 b. 2. Trip three winding transformer from HARBNGR7 (531512) 345 kV Bus to HARBNGR3 (531510) 115 kV Bus to HARBNGR-T (531511) 13.8 kV Bus CKT 1 b. 3. Trip branch from HARBNGR3 (531510) 115 kV Bus to WALKMYR3 (531405) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0828_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0829_P1 | 3 phase fault on CIMARON7 (514901) 345 kV Bus a. Apply Fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON7 (514901) 345 kV Bus to NSUB345 (555234) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 587953 [G16-119-GEN10.6900], 587958 [G16-119-GEN20.6900], 761232 [G17-150GEN1 0.6600], 763841 [G19-052-GEN20.6000], 763959 [G19-067-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0830_P1 | 3 phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV Bus to DGRASSE7 (515852) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0831_P1 | 3 phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply Fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDNGTN7 (515875) 345 kV Bus to WOODRNG7 (514715) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0832_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to OCHILTREE 6 (523155) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0833_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 6 (523095) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0834_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR11 (523092) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0835_P1 | 3 phase fault on HITCHLAND 6 (523095) 230 kV Bus a. Apply Fault at the HITCHLAND 6 (523095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV Bus to HITCHLAND 3 (523093) 115 kV Bus to HITCHLD_TR41 (523098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0836_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0837_P1 | 3 phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from BUFFALO7 (532782) 345 kV Bus to WICHITA7 (532796) 345 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0839_P1 | 3 phase fault on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from THISTLE4 (539804) 138 kV Bus to FLATRDG4 (539638) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0840_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORLND4 (520999) 138 kV Bus to MOORLND2 (520995) 69 kV Bus to MLNDTERT (521180) 2.4 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0841_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to IODINE 4 (520957) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE 4 (520957) 138 kV Bus to FTSUPLY4 (520920) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE 4 (520957) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0842_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to SEILING4 (520553) 138 kV Bus CKT 1 b. 2. Trip branch from SEILING4 (520553) 138 kV Bus to TALOGA 4 (521065) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SEILING4 (520553) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0843_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to ASPEN 4 (520462) 138 kV Bus CKT 1 b. 2. Trip branch from ASPEN 4 (520462) 138 kV Bus to BEARCAT4 (520500) 138 kV Bus CKT 1 b. 3. Trip branch from BEARCAT4 (520500) 138 kV Bus to NINMLTP4 (521128) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ASPEN 4 (520462) 138 kV Bus b. 5. Drop Load 1 at BEARCAT4 (520500) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0844_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to PIC4 (520425) 138 kV Bus CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV Bus to CDRDLTP4 (520848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at PIC4 (520425) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0845_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0846_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0847_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0848_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_0849_P1 | 3 phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply Fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ELKCITY6 (511490) 230 kV Bus to ELKCTY-4 (511458) 138 kV Bus to ELKC2-1 (511482) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0850_P1 | 3 phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply Fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWEETWT6 (511541) 230 kV Bus to STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 2. Trip branch from STLN-DEMARC6 (523779) 230 kV Bus to WHEELER 6 (523777) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763346 [G18-117-GEN20.6000], 763541 [G19-013-GEN10.7200], 763948 [G19-066-GEN10.7200]
04 - Southeast | 25W | Transfer | Group4_Fault_0854_P1 | 3 phase fault on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from LAMAR7 (599950) 345 kV Bus to G18-030-TAP (762662) 345 kV Bus CKT 1 b. 2. Drop Load 1 at LAMAR7 (599950) 345 kV Bus b. 3. Drop Shunt 1 at LAMAR7 (599950) 345 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0855_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to COBRN_CREEK3 (523772) 115 kV Bus CKT 1 b. 2. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus b. 3. Drop Load 1 at COBRN_CREEK3 (523772) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0856_P1 | 3 phase fault on WHEELER 3 (523776) 115 kV Bus a. Apply Fault at the WHEELER 3 (523776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHEELER 3 (523776) 115 kV Bus to HOWARD 3 (523797) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0857_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR11 (524041) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0858_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV Bus to NICHOLS 3 (524043) 115 kV Bus to NICHOLS_TR21 (524042) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0859_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HUTCHISON 6 (523551) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0860_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0861_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0862_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0863_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to BOWERS 3 (523748) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0864_P1 | 3 phase fault on GRAPEVINE 3 (523770) 115 kV Bus a. Apply Fault at the GRAPEVINE 3 (523770) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GRAPEVINE 3 (523770) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0865_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_N 3 (523544) 115 kV Bus to HUTCH_TR1N 1 (523540) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0866_P1 | 3 phase fault on HUTCHISON 6 (523551) 230 kV Bus a. Apply Fault at the HUTCHISON 6 (523551) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HUTCHISON 6 (523551) 230 kV Bus to HUTCH_S 3 (523546) 115 kV Bus to HUTCH_TR2S 1 (523541) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0867_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0868_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to EAST_PLANT 6 (524163) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0869_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0870_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0871_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0872_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0873_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0874_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to NEWHART 6 (525461) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0875_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0876_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0877_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0878_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to FAIN 3 (523339) 115 kV Bus CKT 1 b. 2. Trip branch from FAIN 3 (523339) 115 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FAIN 3 (523339) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0879_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO 3 (524016) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ASARCO 3 (524016) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0880_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to ASARCO_TP 3 (524018) 115 kV Bus CKT 1 b. 2. Trip branch from ASARCO_TP 3 (524018) 115 kV Bus to HIGHLAND_TP3 (523931) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0881_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 5. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 6. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0882_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to CAMX/AGR TP3 (523485) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0883_P1 | 3 phase fault on HUTCH_N 3 (523544) 115 kV Bus a. Apply Fault at the HUTCH_N 3 (523544) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HUTCH_N 3 (523544) 115 kV Bus to HUTCH_S 3 (523546) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0884_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0885_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0886_P1 | 3 phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply Fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAN+TASCOS6 (523869) 230 kV Bus to XIT_INTG 6 (523221) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from XIT_INTG 6 (523221) 230 kV Bus to XIT_INTG 3 (523220) 115 kV Bus to XIT_INTG TR1 (523219) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0887_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to CAMEX/AGRM 3 (523486) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CAMEX/AGRM 3 (523486) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0888_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0889_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0890_P1 | 3 phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WWRDEHV4 (515376) 138 kV Bus to IODINE-4 (514796) 138 kV Bus CKT 1 b. 2. Trip branch from IODINE-4 (514796) 138 kV Bus to REDCLFT4 (515533) 138 kV Bus CKT 1 b. 3. Drop Load 1 at IODINE-4 (514796) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0891_P4 | a. Apply single phase fault at MOORLND4 (520999) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from MOORLND4 (520999) 138 kV to PIC4 (520425) 138 kV CKT 1 b. 2. Trip branch from PIC4 (520425) 138 kV to CDRDLTP4 (520848) 138 kV CKT 1 b. 3. Trip branch from CDRDLTP4 (520848) 138 kV to CEDRDAL4 (520507) 138 kV CKT 1 b. 4. Trip branch from CDRDLTP4 (520848) 138 kV to OKEENE 4 (521016) 138 kV CKT 1 b. 5. Trip branch from MOORLND4 (520999) 138 kV to ASPEN 4 (520462) 138 kV CKT 1 b. 6. Trip branch from ASPEN 4 (520462) 138 kV to BEARCAT4 (520500) 138 kV CKT 1 b. 7. Trip branch from BEARCAT4 (520500) 138 kV to NINMLTP4 (521128) 138 kV CKT 1 b. 8. Trip branch from NINMLTP4 (521128) 138 kV to NINMILE4 (520492) 138 kV CKT 1 b. 9. Trip branch from NINMLTP4 (521128) 138 kV to MORWODS4 (521001) 138 kV CKT 1 b. 10. Drop Load 1 CEDRDAL4 (520507) 138 kV b. 11. Drop Load 1 PIC4 (520425) 138 kV b. 12. Drop Load 1 ASPEN 4 (520462) 138 kV b. 13. Drop Load 1 BEARCAT4 (520500) 138 kV b. 14. Drop Load 1 NINMILE4 (520492) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0892_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0893_P1 | 3 phase fault on ROSEVLY4 (520436) 138 kV Bus a. Apply Fault at the ROSEVLY4 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROSEVLY4 (520436) 138 kV Bus to AVARD 4 (520601) 138 kV Bus CKT 1 b. 2. Drop Load 1 at AVARD 4 (520601) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0894_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0895_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to GLASMTN4 (514788) 138 kV Bus CKT 1 b. 2. Trip branch from GLASMTN4 (514788) 138 kV Bus to CLEOCOR4 (514778) 138 kV Bus CKT 1 b. 3. Drop Load 1 at GLASMTN4 (514788) 138 kV Bus b. 4. Drop Load 2 at GLASMTN4 (514788) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0896_P1 | 3 phase fault on MOORLND4 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND4 (520999) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0897_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0898_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD4 (514785) 138 kV Bus to WINDFRM4 (515785) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0899_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to ALVAOGE2 (514792) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0900_P1 | 3 phase fault on KNOBHIL2 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 (514794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOBHIL2 (514794) 69 kV Bus to CZYCRVT2 (515560) 69 kV Bus CKT 1 b. 2. Trip branch from CZYCRVT2 (515560) 69 kV Bus to SALINE 2 (514716) 69 kV Bus CKT 1 b. 3. Trip branch from SALINE 2 (514716) 69 kV Bus to HELENAT2 (515371) 69 kV Bus CKT 1 b. 4. Drop Load 1 at CZYCRVT2 (515560) 69 kV Bus b. 5. Drop Shunt 1 at CZYCRVT2 (515560) 69 kV Bus1 b. 6. Drop Load 1 at SALINE 2 (514716) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0901_P1 | 3 phase fault on MOORLND2 (520995) 69 kV Bus a. Apply Fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MOORLND2 (520995) 69 kV Bus to CRTSJCT2 (521197) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0902_P1 | 3 phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DGRASSE4 (515853) 138 kV Bus to MOORLND4 (520999) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0903_P1 | 3 phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOODWRD4 (514785) 138 kV Bus to WODWRD 2 (514782) 69 kV Bus to WOODWR21 (515771) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0904_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to MORWODS4 (521001) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0905_P1 | 3 phase fault on NINMLTP4 (521128) 138 kV Bus a. Apply Fault at the NINMLTP4 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NINMLTP4 (521128) 138 kV Bus to NINMILE4 (520492) 138 kV Bus CKT 1 b. 2. Drop Load 1 at NINMILE4 (520492) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0906_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0907_P1 | 3 phase fault on CRTSJCT2 (521197) 69 kV Bus a. Apply Fault at the CRTSJCT2 (521197) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRTSJCT2 (521197) 69 kV Bus to CURTIS 2 (520480) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CURTIS 2 (520480) 69 kV Bus b. 3. Drop Load 2 at CURTIS 2 (520480) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0908_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALVA 2 (520806) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0909_P1 | 3 phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply Fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALVAOGE2 (514792) 69 kV Bus to ALINETP2 (515803) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0910_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0911_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOCOR4 (514778) 138 kV Bus to CLEOPLT4 (515562) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0912_P1 | 3 phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply Fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CLEOCOR4 (514778) 138 kV Bus to CLEOCOR2 (514777) 69 kV Bus to CLEOCOR1 (515716) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0913_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to OKEENE 4 (521016) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0914_P1 | 3 phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply Fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CDRDLTP4 (520848) 138 kV Bus to CEDRDAL4 (520507) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CEDRDAL4 (520507) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0915_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TALOGA 4 (521065) 138 kV Bus to TALOGA 2 (521064) 69 kV Bus to TLGTERT (521178) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0916_P1 | 3 phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply Fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TALOGA 4 (521065) 138 kV Bus to DEWEY 4 (514787) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0917_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERT (521170) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0918_P1 | 3 phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply Fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from FTSUPLY4 (520920) 138 kV Bus to FTSUPLY2 (520919) 69 kV Bus to FTSUPTERTB (521182) 13.8 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0919_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to KNOBHIL4 (514795) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0920_P1 | 3 phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOBHIL4 (514795) 138 kV Bus to KNOBHIL2 (514794) 69 kV Bus to KNOBHIL1 (515732) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0921_P1 | 3 phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CLARKCOUNTY7 (539800) 345 kV Bus to SPERVIL7 (531469) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763895 [G19-058-GEN20.6000]
04 - Southeast | 25W | Transfer | Group4_Fault_0922_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to NEWGRTP2 (514776) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0923_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to WOODWRD2 (521096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0924_P1 | 3 phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply Fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WODWRD 2 (514782) 69 kV Bus to CEDARAV2 (514781) 69 kV Bus CKT 1 b. 2. Trip branch from CEDARAV2 (514781) 69 kV Bus to TANGRTP2 (514775) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CEDARAV2 (514781) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0925_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to SALTPLN4 (520437) 138 kV Bus CKT 1 b. 2. Trip branch from SALTPLN4 (520437) 138 kV Bus to CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 3. Trip branch from CHRKCTY4 (520431) 138 kV Bus to DRIFTWD4 (521200) 138 kV Bus CKT 1 b. 4. Drop Load 1 at SALTPLN4 (520437) 138 kV Bus b. 5. Drop Load 2 at SALTPLN4 (520437) 138 kV Bus b. 6. Drop Load 1 at CHRKCTY4 (520431) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0926_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to MORWOOD4 (521002) 138 kV Bus CKT 1 b. 2. Trip branch from MORWOOD4 (521002) 138 kV Bus to BRANTLEY4 (520832) 138 kV Bus CKT 1 b. 3. Trip branch from BRANTLEY4 (520832) 138 kV Bus to DURHAM 4 (520885) 138 kV Bus CKT 1 b. 4. Trip branch from DURHAM 4 (520885) 138 kV Bus to SWEETWR4 (521060) 138 kV Bus CKT 1 b. 5. Trip branch from SWEETWR4 (521060) 138 kV Bus to BULOJ4 (520402) 138 kV Bus CKT 1 b. 6. Trip branch from BULOJ4 (520402) 138 kV Bus to ERICK 4 (520903) 138 kV Bus CKT 1 b. 7. Trip branch from ERICK 4 (520903) 138 kV Bus to SAYRE--4 (511504) 138 kV Bus CKT 1 b. 8. Trip branch from SAYRE--4 (511504) 138 kV Bus to FALCNRD4 (511511) 138 kV Bus CKT 1 b. 9. Trip branch from FALCNRD4 (511511) 138 kV Bus to ELKCTY-4 (511458) 138 kV Bus CKT 1 b. 10. Drop Load 1 at BRANTLEY4 (520832) 138 kV Bus b. 11. Drop Load 1 at DURHAM 4 (520885) 138 kV Bus b. 12. Drop Load 1 at SWEETWR4 (521060) 138 kV Bus b. 13. Drop Load 1 at BULOJ4 (520402) 138 kV Bus b. 14. Drop Load 1 at ERICK 4 (520903) 138 kV Bus b. 15. Drop Load 1 at SAYRE--4 (511504) 138 kV Bus b. 16. Drop Load 1 at FALCNRD4 (511511) 138 kV Bus b. 17. Drop Shunt 1 at SAYRE--4 (511504) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0927_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MORWODS4 (521001) 138 kV Bus to ELLIS 4 (511561) 138 kV Bus CKT 1 b. 2. Trip branch from ELLIS 4 (511561) 138 kV Bus to CUSTER 4 (520459) 138 kV Bus CKT 1 b. 3. Trip branch from CUSTER 4 (520459) 138 kV Bus to REDHLSW4 (521116) 138 kV Bus CKT 1 b. 4. Drop Load 1 at ELLIS 4 (511561) 138 kV Bus b. 5. Drop Load 1 at CUSTER 4 (520459) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0928_P1 | 3 phase fault on MORWODS4 (521001) 138 kV Bus a. Apply Fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MORWODS4 (521001) 138 kV Bus to MORWODS2 (521000) 69 kV Bus to MRWDTERT (521172) 13.8 kV Bus CKT 1 b. 2. Trip branch from MORWODS2 (521000) 69 kV Bus to BTLRJCT2 (520457) 69 kV Bus CKT 1 b. 3. Trip branch from BTLRJCT2 (520457) 69 kV Bus to BUTLER 2 (520458) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0929_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to FARGOJCT2 (521196) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0930_P1 | 3 phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply Fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOODWRD2 (521096) 69 kV Bus to VICI 2 (521082) 69 kV Bus CKT 1 b. 2. Trip branch from VICI 2 (521082) 69 kV Bus to TALOGA 2 (521064) 69 kV Bus CKT 1 b. 3. Drop Load 1 at VICI 2 (521082) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0931_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DRIFTWD4 (521200) 138 kV Bus to DRIFTWD2 (521201) 69 kV Bus to DRFTWDTERT (521185) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0932_P1 | 3 phase fault on DRIFTWD4 (521200) 138 kV Bus a. Apply Fault at the DRIFTWD4 (521200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD4 (521200) 138 kV Bus to BYRONTP4 (520432) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0933_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to CLEO PL4 (515553) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO PL4 (515553) 138 kV Bus b. 3. Drop Shunt 1 at CLEO PL4 (515553) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0934_P1 | 3 phase fault on CLEOPLT4 (515562) 138 kV Bus a. Apply Fault at the CLEOPLT4 (515562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOPLT4 (515562) 138 kV Bus to MENOTAP4 (514789) 138 kV Bus CKT 1 b. 2. Trip branch from MENOTAP4 (514789) 138 kV Bus to IMO 4 (514790) 138 kV Bus CKT 1 b. 3. Drop Load 1 at MENOTAP4 (514789) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 516022 [SUNDCG11 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0935_P1 | 3 phase fault on NOELSW 4 (520430) 138 kV Bus a. Apply Fault at the NOELSW 4 (520430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NOELSW 4 (520430) 138 kV Bus to ROSEVLY4 (520436) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0936_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to ALINE 2 (514793) 69 kV Bus CKT 1 b. 2. Drop Load 1 at ALINE 2 (514793) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0937_P1 | 3 phase fault on ALINETP2 (515803) 69 kV Bus a. Apply Fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALINETP2 (515803) 69 kV Bus to CLEOTP 2 (515804) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0938_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEOCOR2 (514777) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0939_P1 | 3 phase fault on CLEOTP 2 (515804) 69 kV Bus a. Apply Fault at the CLEOTP 2 (515804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CLEOTP 2 (515804) 69 kV Bus to CLEO 2 (514791) 69 kV Bus CKT 1 b. 2. Drop Load 1 at CLEO 2 (514791) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0940_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTBJ2 (521202) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTBJ2 (521202) 69 kV Bus to MEDLDGE2 (522396) 69 kV Bus CKT 1 b. 3. Trip branch from MEDLDGE2 (522396) 69 kV Bus to HAZELTN2 (520937) 69 kV Bus CKT 1 b. 4. Drop Load 1 at MEDLDGE2 (522396) 69 kV Bus b. 5. Drop Load 1 at HAZELTN2 (520937) 69 kV Bus b. 6. Drop Shunt 1 at HAZELTN2 (520937) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0941_P1 | 3 phase fault on DRIFTWD2 (521201) 69 kV Bus a. Apply Fault at the DRIFTWD2 (521201) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRIFTWD2 (521201) 69 kV Bus to HAZLTAJ2 (520938) 69 kV Bus CKT 1 b. 2. Trip branch from HAZLTAJ2 (520938) 69 kV Bus to BRLNGTN2 (520833) 69 kV Bus CKT 1 b. 3. Trip branch from BRLNGTN2 (520833) 69 kV Bus to CHEROKS2 (520851) 69 kV Bus CKT 1 b. 4. Drop Load 1 at BRLNGTN2 (520833) 69 kV Bus b. 5. Drop Load 2K at BRLNGTN2 (520833) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0942_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to WILKINS4 (514950) 138 kV Bus CKT 1 b. 2. Trip branch from WILKINS4 (514950) 138 kV Bus to OAKTRET4 (514930) 138 kV Bus CKT 1 b. 3. Trip branch from OAKTRET4 (514930) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Drop Load 1 at WILKINS4 (514950) 138 kV Bus b. 5. Drop Load 1 at OAKTRET4 (514930) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0943_P1 | 3 phase fault on OU TAP 4 (514931) 138 kV Bus a. Apply Fault at the OU TAP 4 (514931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OU TAP 4 (514931) 138 kV Bus to OUBROOK4 (514903) 138 kV Bus CKT 1 b. 2. Drop Load 1 at OUBROOK4 (514903) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0944_P1 | 3 phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply Fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from QUAILCK4 (514851) 138 kV Bus to SKYLINE4 (514850) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0945_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to WRAIRPT4 (514889) 138 kV Bus CKT 1 b. 2. Trip branch from WRAIRPT4 (514889) 138 kV Bus to 36&MER 4 (514888) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WRAIRPT4 (514889) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0946_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PENN 4 (514925) 138 kV Bus to SANTAFE4 (514926) 138 kV Bus CKT 1 b. 2. Trip branch from SANTAFE4 (514926) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SANTAFE4 (514926) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0947_P1 | 3 phase fault on PENN 4 (514925) 138 kV Bus a. Apply Fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PENN 4 (514925) 138 kV Bus to PENN 2 (514924) 69 kV Bus to PENN 1 (515751) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0948_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to TUTCONT4 (511425) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0949_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to EL-RENO4 (514819) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0950_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0951_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to HAYMAKR4 (514863) 138 kV Bus CKT 1 b. 2. Trip branch from HAYMAKR4 (514863) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 3. Drop Load 1 at HAYMAKR4 (514863) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0952_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to SARA 4 (514895) 138 kV Bus CKT 1 b. 2. Trip branch from SARA 4 (514895) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SARA 4 (514895) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0953_P1 | 3 phase fault on CIMARON4 (514898) 138 kV Bus a. Apply Fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CIMARON4 (514898) 138 kV Bus to CZECHAL4 (514894) 138 kV Bus CKT 1 b. 2. Trip branch from CZECHAL4 (514894) 138 kV Bus to XEROX 4 (514893) 138 kV Bus CKT 1 b. 3. Trip branch from XEROX 4 (514893) 138 kV Bus to MORGAN 4 (514896) 138 kV Bus CKT 1 b. 4. Trip branch from MORGAN 4 (514896) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 b. 5. Drop Load 1 at CZECHAL4 (514894) 138 kV Bus b. 6. Drop Load 1 at XEROX 4 (514893) 138 kV Bus b. 7. Drop Load 1 at MORGAN 4 (514896) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0954_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to BRADEN 4 (514854) 138 kV Bus CKT 1 b. 2. Trip branch from BRADEN 4 (514854) 138 kV Bus to SLVRLAK4 (514852) 138 kV Bus CKT 1 b. 3. Drop Load 1 at BRADEN 4 (514854) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0955_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to PIEDMNT4 (514864) 138 kV Bus CKT 1 b. 2. Trip branch from PIEDMNT4 (514864) 138 kV Bus to RICHRDS4 (514862) 138 kV Bus CKT 1 b. 3. Trip branch from RICHRDS4 (514862) 138 kV Bus to DVISION4 (514853) 138 kV Bus CKT 1 b. 4. Drop Load 1 at PIEDMNT4 (514864) 138 kV Bus b. 5. Drop Load 1 at RICHRDS4 (514862) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0956_P1 | 3 phase fault on NORTWST4 (514879) 138 kV Bus a. Apply Fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTWST4 (514879) 138 kV Bus to LNEOAK 4 (514873) 138 kV Bus CKT 1 b. 2. Trip branch from LNEOAK 4 (514873) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LNEOAK 4 (514873) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0957_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to HOLLYWD4 (514953) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0958_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to MCCLAIN4 (514902) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0959_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to TURNER 4 (514992) 138 kV Bus CKT 1 b. 2. Trip branch from TURNER 4 (514992) 138 kV Bus to SOGATE 4 (514928) 138 kV Bus CKT 1 b. 3. Trip branch from SOGATE 4 (514928) 138 kV Bus to SW134TP4 (514876) 138 kV Bus CKT 1 b. 4. Drop Load 1 at TURNER 4 (514992) 138 kV Bus b. 5. Drop Load 1 at SOGATE 4 (514928) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0960_P1 | 3 phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply Fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLVALLY4 (514929) 138 kV Bus to CHERYCK4 (514957) 138 kV Bus CKT 1 b. 2. Trip branch from CHERYCK4 (514957) 138 kV Bus to BOYD 4 (514958) 138 kV Bus CKT 1 b. 3. Trip branch from BOYD 4 (514958) 138 kV Bus to CEDARLN4 (514948) 138 kV Bus CKT 1 b. 4. Drop Load 1 at CHERYCK4 (514957) 138 kV Bus b. 5. Drop Load 1 at BOYD 4 (514958) 138 kV Bus b. 6. Drop Shunt 1 at BOYD 4 (514958) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0961_P1 | 3 phase fault on REDBUD 7 (514909) 345 kV Bus a. Apply Fault at the REDBUD 7 (514909) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from REDBUD 7 (514909) 345 kV Bus to R.S.S.-7 (509782) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0962_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0963_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to INDNHIL4 (514954) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0964_P1 | 3 phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply Fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOLLYWD4 (514953) 138 kV Bus to STUBMAN4 (514952) 138 kV Bus CKT 1 b. 2. Trip branch from STUBMAN4 (514952) 138 kV Bus to MLENIUM4 (514932) 138 kV Bus CKT 1 b. 3. Trip branch from MLENIUM4 (514932) 138 kV Bus to OU TAP 4 (514931) 138 kV Bus CKT 1 b. 4. Drop Load 1 at STUBMAN4 (514952) 138 kV Bus b. 5. Drop Load 1 at MLENIUM4 (514932) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0965_P1 | 3 phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply Fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SLVRLAK4 (514852) 138 kV Bus to QUAILCK4 (514851) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0966_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to WESTHSE4 (514904) 138 kV Bus CKT 1 b. 2. Drop Load 1 at WESTHSE4 (514904) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0967_P1 | 3 phase fault on INDNHIL4 (514954) 138 kV Bus a. Apply Fault at the INDNHIL4 (514954) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INDNHIL4 (514954) 138 kV Bus to INDIANH4 (515380) 138 kV Bus CKT 1 b. 2. Trip branch from INDIANH4 (515380) 138 kV Bus to MOORE 4 (514955) 138 kV Bus CKT 1 b. 3. Trip branch from MOORE 4 (514955) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 4. Drop Load 1 at INDIANH4 (515380) 138 kV Bus b. 5. Drop Load 1 at MOORE 4 (514955) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0968_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to MUSTANG4 (514861) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0969_P1 | 3 phase fault on DVISION4 (514853) 138 kV Bus a. Apply Fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DVISION4 (514853) 138 kV Bus to LAKESID4 (514849) 138 kV Bus CKT 1 b. 2. Trip branch from LAKESID4 (514849) 138 kV Bus to HEFNER 4 (514848) 138 kV Bus CKT 1 b. 3. Drop Load 1 at LAKESID4 (514849) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0970_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to G17-152_TAP (914902) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0971_P1 | 3 phase fault on SW134TP4 (514876) 138 kV Bus a. Apply Fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SW134TP4 (514876) 138 kV Bus to WESTMOR4 (514887) 138 kV Bus CKT 1 b. 2. Trip branch from WESTMOR4 (514887) 138 kV Bus to PENN 4 (514925) 138 kV Bus CKT 1 b. 3. Drop Load 1 at WESTMOR4 (514887) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0972_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to TUTTLE4 (511501) 138 kV Bus CKT 1 b. 2. Trip branch from TUTTLE4 (511501) 138 kV Bus to LEONARD4 (511575) 138 kV Bus CKT 1 b. 3. Drop Load 1 at TUTTLE4 (511501) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0973_P1 | 3 phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply Fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUTCONT4 (511425) 138 kV Bus to CEMRD_TP4 (511576) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511974 [REDBDPLNW0 0.6900]
04 - Southeast | 25W | Transfer | Group4_Fault_0974_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to T-CONCO4 (511424) 138 kV Bus CKT 1 b. 2. Drop Load 1 at T-CONCO4 (511424) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0975_P1 | 3 phase fault on CEMRD_TP4 (511576) 138 kV Bus a. Apply Fault at the CEMRD_TP4 (511576) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CEMRD_TP4 (511576) 138 kV Bus to CMTRYRD4 (515864) 138 kV Bus CKT 1 b. 2. Drop Load 1 at CMTRYRD4 (515864) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0976_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to JENSENT4 (514820) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0977_P1 | 3 phase fault on JENSENT4 (514820) 138 kV Bus a. Apply Fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JENSENT4 (514820) 138 kV Bus to JENSEN 4 (514821) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0978_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EL-RENO4 (514819) 138 kV Bus to OMEGA 4 (515962) 138 kV Bus CKT 1 b. 2. Trip branch from OMEGA 4 (515962) 138 kV Bus to ROMNOSE4 (514823) 138 kV Bus CKT 1 b. 3. Drop Load 1 at OMEGA 4 (515962) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0979_P1 | 3 phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply Fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EL-RENO4 (514819) 138 kV Bus to ELRENO 2 (514818) 69 kV Bus to EL RENO1 (515722) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0980_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to JNSKAMO4 (514906) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0981_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to RNDBARN4 (515461) 138 kV Bus CKT 1 b. 2. Trip branch from RNDBARN4 (515461) 138 kV Bus to BURGETT4 (514510) 138 kV Bus CKT 1 b. 3. Trip branch from BURGETT4 (514510) 138 kV Bus to DANFRTH4 (514833) 138 kV Bus CKT 1 b. 4. Drop Load 1 at RNDBARN4 (515461) 138 kV Bus b. 5. Drop Load 1 at BURGETT4 (514510) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0982_P1 | 3 phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply Fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ARCADIA4 (514907) 138 kV Bus to LGARBER4 (515465) 138 kV Bus CKT 1 b. 2. Trip branch from LGARBER4 (515465) 138 kV Bus to CHTWOOD4 (514842) 138 kV Bus CKT 1 b. 3. Trip branch from CHTWOOD4 (514842) 138 kV Bus to JONESSB4 (515480) 138 kV Bus CKT 1 b. 4. Drop Load 1 at LGARBER4 (515465) 138 kV Bus b. 5. Drop Load 1 at CHTWOOD4 (514842) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0983_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to BARNES 4 (515003) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0984_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to SOONRTP4 (514949) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0985_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0986_P1 | 3 phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply Fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRAPER 4 (514933) 138 kV Bus to GM 4 (514961) 138 kV Bus CKT 1 b. 2. Trip branch from GM 4 (514961) 138 kV Bus to AIRDEPT4 (515457) 138 kV Bus CKT 1 b. 3. Trip branch from AIRDEPT4 (515457) 138 kV Bus to WILDMRY4 (514984) 138 kV Bus CKT 1 b. 4. Trip branch from WILDMRY4 (514984) 138 kV Bus to OAKCRK 4 (514960) 138 kV Bus CKT 1 b. 5. Drop Load 1 at GM 4 (514961) 138 kV Bus b. 6. Drop Load 1 at AIRDEPT4 (515457) 138 kV Bus b. 7. Drop Load 1 at WILDMRY4 (514984) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0987_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from R.S.S.-7 (509782) 345 kV Bus to PECANCK7 (515235) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0989_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T1 4 (509773) 138 kV Bus to RSST1 T1 (509882) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T1 4 (509773) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0990_P1 | 3 phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from R.S.S.-7 (509782) 345 kV Bus to RSS T2 4 (509875) 138 kV Bus to RSST2 T1 (509876) 13.8 kV Bus CKT 1 b. 2. Trip branch from RSS T2 4 (509875) 138 kV Bus to R.S.S.-4 (509783) 138 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0991_P1 | 3 phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply Fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FRNKLNS4 (520917) 138 kV Bus to MIDWEST4 (514946) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_0992_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to DAYTON 4 (514892) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0993_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to SW 5TH 4 (514920) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0994_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MUSTANG4 (514861) 138 kV Bus to COUNCIL4 (514865) 138 kV Bus CKT 1 b. 2. Trip branch from COUNCIL4 (514865) 138 kV Bus to WESTOAK4 (514866) 138 kV Bus CKT 1 b. 3. Trip branch from WESTOAK4 (514866) 138 kV Bus to MERIDAN4 (514867) 138 kV Bus CKT 1 b. 4. Trip branch from MERIDAN4 (514867) 138 kV Bus to DOUGLTP4 (514868) 138 kV Bus CKT 1 b. 5. Drop Load 1 at COUNCIL4 (514865) 138 kV Bus b. 6. Drop Load 1 at WESTOAK4 (514866) 138 kV Bus b. 7. Drop Load 1 at MERIDAN4 (514867) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0995_P1 | 3 phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply Fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MUSTANG4 (514861) 138 kV Bus to MSTANG 2 (514860) 69 kV Bus to MUSTANG1 (515740) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0996_P1 | 3 phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply Fault at the MARAUTO2 (508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MARAUTO2 (508576) 69 kV Bus to MARSHAL2 (508556) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0997_P1 | 3 phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply Fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JEFFRSN4 (508835) 138 kV Bus to LAKEPIN4 (509624) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0998_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to HARRISN4 (508544) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_0999_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to NMINEOL4 (508349) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1000_P1 | 3 phase fault on LHAWKIN4 (508358) 138 kV Bus a. Apply Fault at the LHAWKIN4 (508358) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LHAWKIN4 (508358) 138 kV Bus to REDSPRW4 (508366) 138 kV Bus CKT 1 b. 2. Trip branch from REDSPRW4 (508366) 138 kV Bus to PECANHL4 (508365) 138 kV Bus CKT 1 b. 3. Trip branch from PECANHL4 (508365) 138 kV Bus to GARDVAL4 (508364) 138 kV Bus CKT 1 b. 4. Trip branch from GARDVAL4 (508364) 138 kV Bus to KENSULI4 (508363) 138 kV Bus CKT 1 b. 5. Trip branch from KENSULI4 (508363) 138 kV Bus to BENWHEL4 (508362) 138 kV Bus CKT 1 b. 6. Trip branch from BENWHEL4 (508362) 138 kV Bus to STARR 4 (508361) 138 kV Bus CKT 1 b. 7. Trip branch from STARR 4 (508361) 138 kV Bus to EBURGES4 (508360) 138 kV Bus CKT 1 b. 8. Trip branch from EBURGES4 (508360) 138 kV Bus to BURGEST4 (508357) 138 kV Bus CKT 1 b. 9. Drop Load 1 at REDSPRW4 (508366) 138 kV Bus b. 10. Drop Load 1 at PECANHL4 (508365) 138 kV Bus b. 11. Drop Load 1 at GARDVAL4 (508364) 138 kV Bus b. 12. Drop Load 1 at KENSULI4 (508363) 138 kV Bus b. 13. Drop Load 1 at BENWHEL4 (508362) 138 kV Bus b. 14. Drop Load 1 at STARR 4 (508361) 138 kV Bus b. 15. Drop Load 1 at EBURGES4 (508360) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1001_P1 | 3 phase fault on BURGEST4 (508357) 138 kV Bus a. Apply Fault at the BURGEST4 (508357) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BURGEST4 (508357) 138 kV Bus to MORTONST 4 (508373) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1002_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to (763010) kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1003_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KNOXLEE4 (508548) 138 kV Bus to SOTXEST4 (508570) 138 kV Bus CKT 1 b. 2. Trip branch from SOTXEST4 (508570) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 b. 3. Drop Load 1 at SOTXEST4 (508570) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1004_P1 | 3 phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply Fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KNOXLEE4 (508548) 138 kV Bus to KNOXLEE2 (508547) 69 kV Bus to KXLEE-1 (508584) 12.47 kV Bus CKT 1 b. 2. Trip branch from KNOXLEE2 (508547) 69 kV Bus to SELONGV2 (508568) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1005_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN1-1 (509095) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1006_P1 | 3 phase fault on NWHENDR4 (509076) 138 kV Bus a. Apply Fault at the NWHENDR4 (509076) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NWHENDR4 (509076) 138 kV Bus to NWHENDR2 (509075) 69 kV Bus to NWHEN2-1 (509096) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1007_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to MONROCR2 (508558) 69 kV Bus CKT 1 b. 2. Trip branch from MONROCR2 (508558) 69 kV Bus to WHITNEY2 (508574) 69 kV Bus CKT 1 b. 3. Drop Load 1 at MONROCR2 (508558) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1008_P1 | 3 phase fault on KILGORE2 (508546) 69 kV Bus a. Apply Fault at the KILGORE2 (508546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KILGORE2 (508546) 69 kV Bus to HOWELL 2 (508545) 69 kV Bus CKT 1 b. 2. Trip branch from HOWELL 2 (508545) 69 kV Bus to SABINE 2 (508565) 69 kV Bus CKT 1 b. 3. Trip branch from SABINE 2 (508565) 69 kV Bus to SPIPETP2 (508573) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HOWELL 2 (508545) 69 kV Bus b. 5. Drop Load 1 at SABINE 2 (508565) 69 kV Bus b. 6. Drop Shunt 1 at HOWELL 2 (508545) 69 kV Bus1 b. 7. Drop Shunt 1 at SABINE 2 (508565) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1009_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON1-1 (509097) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1010_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to SVCPIPE2 (508578) 69 kV Bus CKT 1 b. 2. Drop Load 1 at SVCPIPE2 (508578) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1011_P1 | 3 phase fault on SPIPETP2 (508573) 69 kV Bus a. Apply Fault at the SPIPETP2 (508573) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SPIPETP2 (508573) 69 kV Bus to CLARKSV2 (508540) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1012_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to EASTEX 4 (508582) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1013_P1 | 3 phase fault on HARRISN4 (508544) 138 kV Bus a. Apply Fault at the HARRISN4 (508544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRISN4 (508544) 138 kV Bus to LIBCYTP4 (508550) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1014_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OVERTON4 (509080) 138 kV Bus to OVERTON2 (509079) 69 kV Bus to OVTON2-1 (509098) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1015_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1016_P1 | 3 phase fault on EASTEX 4 (508582) 138 kV Bus a. Apply Fault at the EASTEX 4 (508582) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EASTEX 4 (508582) 138 kV Bus to NTXEAST4 (508561) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1017_P1 | 3 phase fault on LIBCYTP4 (508550) 138 kV Bus a. Apply Fault at the LIBCYTP4 (508550) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LIBCYTP4 (508550) 138 kV Bus to LIBCITY4 (508535) 138 kV Bus CKT 1 b. 2. Drop Load 1 at LIBCITY4 (508535) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1018_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL1-1 (509090) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1019_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROKHILL4 (509083) 138 kV Bus to ROKHILL2 (509082) 69 kV Bus to RKHIL2-1 (509091) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1020_P1 | 3 phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply Fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL4 (509083) 138 kV Bus to NEWPROS4 (509102) 138 kV Bus CKT 1 b. 2. Trip branch from NEWPROS4 (509102) 138 kV Bus to CARTPOD4 (509057) 138 kV Bus CKT 1 b. 3. Trip branch from CARTPOD4 (509057) 138 kV Bus to HULLTAP4 (509099) 138 kV Bus CKT 1 b. 4. Trip branch from HULLTAP4 (509099) 138 kV Bus to CARTHGT4 (509060) 138 kV Bus CKT 1 b. 5. Drop Load 1 at NEWPROS4 (509102) 138 kV Bus b. 6. Drop Load 1 at CARTPOD4 (509057) 138 kV Bus b. 7. Drop Load 1 at HULLTAP4 (509099) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1021_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to BIG3TAP2 (508539) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1022_P1 | 3 phase fault on SELONGV2 (508568) 69 kV Bus a. Apply Fault at the SELONGV2 (508568) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SELONGV2 (508568) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1023_P1 | 3 phase fault on G19-065-TAP (763010) kV Bus a. Apply Fault at the G19-065-TAP (763010) kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G19-065-TAP (763010) kV Bus to LONDON 4 (509072) 138 kV Bus CKT 1 b. 2. Trip branch from LONDON 4 (509072) 138 kV Bus to FRIARSW4 (509062) 138 kV Bus CKT 1 b. 3. Trip branch from FRIARSW4 (509062) 138 kV Bus to FRIRSWR4 (509063) 138 kV Bus CKT 1 b. 4. Trip branch from FRIRSWR4 (509063) 138 kV Bus to NWHENDR4 (509076) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LONDON 4 (509072) 138 kV Bus b. 6. Drop Load 1 at FRIARSW4 (509062) 138 kV Bus b. 7. Drop Load 1 at FRIRSWR4 (509063) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1024_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to EVENSID2 (509061) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1025_P1 | 3 phase fault on NWHENDR2 (509075) 69 kV Bus a. Apply Fault at the NWHENDR2 (509075) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NWHENDR2 (509075) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1026_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LETOURT2 (508549) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1027_P1 | 3 phase fault on OVERTON4 (509080) 138 kV Bus a. Apply Fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON4 (509080) 138 kV Bus to LEVERET4 (509069) 138 kV Bus CKT 1 b. 2. Trip branch from LEVERET4 (509069) 138 kV Bus to KILGORR4 (509067) 138 kV Bus CKT 1 b. 3. Trip branch from KILGORR4 (509067) 138 kV Bus to MONROER4 (509073) 138 kV Bus CKT 1 b. 4. Trip branch from MONROER4 (509073) 138 kV Bus to KNOXLEE4 (508548) 138 kV Bus CKT 1 b. 5. Drop Load 1 at LEVERET4 (509069) 138 kV Bus b. 6. Drop Load 1 at KILGORR4 (509067) 138 kV Bus b. 7. Drop Load 1 at MONROER4 (509073) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1028_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1029_P1 | 3 phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply Fault at the WHITNEY2 (508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WHITNEY2 (508574) 69 kV Bus to LONGVUE2 (508555) 69 kV Bus CKT 1 b. 2. Trip branch from LONGVUE2 (508555) 69 kV Bus to GATES 2 (508541) 69 kV Bus CKT 1 b. 3. Trip branch from GATES 2 (508541) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 b. 4. Drop Load 1 at LONGVUE2 (508555) 69 kV Bus b. 5. Drop Shunt 1 at LONGVUE2 (508555) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1030_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to KILGORE2 (508546) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1031_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1032_P1 | 3 phase fault on NTXEAST4 (508561) 138 kV Bus a. Apply Fault at the NTXEAST4 (508561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NTXEAST4 (508561) 138 kV Bus to ESTGEN4 (508583) 138 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1033_P1 | 3 phase fault on OVERTON2 (509079) 69 kV Bus a. Apply Fault at the OVERTON2 (509079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OVERTON2 (509079) 69 kV Bus to TURNERT2 (509089) 69 kV Bus CKT 1 b. 2. Drop Load 1 at TURNERT2 (509089) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1034_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to MURVAULTP (509048) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1035_P1 | 3 phase fault on CARTHGT4 (509060) 138 kV Bus a. Apply Fault at the CARTHGT4 (509060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARTHGT4 (509060) 138 kV Bus to LOGANSP4 (509071) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1036_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1037_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to ROSBORO2 (509085) 69 kV Bus CKT 1 b. 2. Trip branch from ROSBORO2 (509085) 69 kV Bus to BLOCKRT2 (509055) 69 kV Bus CKT 1 b. 3. Drop Load 1 at ROSBORO2 (509085) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1038_P1 | 3 phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply Fault at the ROKHILL2 (509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROKHILL2 (509082) 69 kV Bus to CARTHAG2 (509056) 69 kV Bus CKT 1 b. 2. Trip branch from CARTHAG2 (509056) 69 kV Bus to LAPACIF2 (509068) 69 kV Bus CKT 1 b. 3. Drop Load 1 at CARTHAG2 (509056) 69 kV Bus b. 4. Drop Load 2 at CARTHAG2 (509056) 69 kV Bus b. 5. Drop Load 1 at LAPACIF2 (509068) 69 kV Bus b. 6. Drop Shunt 1 at CARTHAG2 (509056) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1039_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to BIG 3 2 (508537) 69 kV Bus CKT 1 b. 2. Drop Load 1 at BIG 3 2 (508537) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1040_P1 | 3 phase fault on BIG3TAP2 (508539) 69 kV Bus a. Apply Fault at the BIG3TAP2 (508539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BIG3TAP2 (508539) 69 kV Bus to LLAMOND2 (508551) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1041_P1 | 3 phase fault on LETOURT2 (508549) 69 kV Bus a. Apply Fault at the LETOURT2 (508549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LETOURT2 (508549) 69 kV Bus to LETOURN2 (508581) 69 kV Bus CKT 1 b. 2. Trip branch from LETOURN2 (508581) 69 kV Bus to LETRNST2 (508536) 69 kV Bus CKT 1 b. 3. Drop Load 1 at LETOURN2 (508581) 69 kV Bus b. 4. Drop Load 1 at LETRNST2 (508536) 69 kV Bus b. 5. Drop Shunt 1 at LETOURN2 (508581) 69 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1042_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to FEARSCO2 (509086) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1043_P1 | 3 phase fault on EVENSID2 (509061) 69 kV Bus a. Apply Fault at the EVENSID2 (509061) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EVENSID2 (509061) 69 kV Bus to POYNTER2 (509081) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1044_P1 | 3 phase fault on POYNTER2 (509081) 69 kV Bus a. Apply Fault at the POYNTER2 (509081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POYNTER2 (509081) 69 kV Bus to HNDRSNR2 (509065) 69 kV Bus CKT 1 b. 2. Trip branch from HNDRSNR2 (509065) 69 kV Bus to BEARCATTP 2 (509127) 69 kV Bus CKT 1 b. 3. Trip branch from BEARCATTP 2 (509127) 69 kV Bus to BECKVIL2 (509054) 69 kV Bus CKT 1 b. 4. Drop Load 1 at HNDRSNR2 (509065) 69 kV Bus b. 5. Drop Load 1 at BEARCATTP 2 (509127) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1045_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4COLSTTA% (334021) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1046_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MT.ZION (334060) 138 kV Bus CKT 1 b. 2. Trip branch from 4MT.ZION (334060) 138 kV Bus to 4L558T485 (334058) 138 kV Bus CKT 1 b. 3. Drop Load BZ at 4MT.ZION (334060) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1047_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4MAG AND (334025) 138 kV Bus CKT 1 b. 2. Trip branch from 4MAG AND (334025) 138 kV Bus to 4SOTA 1 (334024) 138 kV Bus CKT 1 b. 3. Trip branch from 4SOTA 1 (334024) 138 kV Bus to 4NAVSSPLT! (334019) 138 kV Bus CKT 1 b. 4. Drop Load BZ at 4SOTA 1 (334024) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1048_P1 | 3 phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply Fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4GRIMES% (334026) 138 kV Bus to 4BENTWATER! (334039) 138 kV Bus CKT 1 b. 2. Trip branch from 4BENTWATER! (334039) 138 kV Bus to 4WALDEN (334040) 138 kV Bus CKT 1 b. 3. Trip branch from 4WALDEN (334040) 138 kV Bus to 4APRILTX (334041) 138 kV Bus CKT 1 b. 4. Trip branch from 4APRILTX (334041) 138 kV Bus to 4LFOREST (334042) 138 kV Bus CKT 1 b. 5. Trip branch from 4LFOREST (334042) 138 kV Bus to 4RABONCHAPEL (334049) 138 kV Bus CKT 1 b. 6. Trip branch from 4RABONCHAPEL (334049) 138 kV Bus to 4WDHAVN (334105) 138 kV Bus CKT 1 b. 7. Trip branch from 4WDHAVN (334105) 138 kV Bus to 4PONDEROSA% (334087) 138 kV Bus CKT 1 b. 8. Drop Load 1 at 4BENTWATER! (334039) 138 kV Bus b. 9. Drop Load 1 at 4WALDEN (334040) 138 kV Bus b. 10. Drop Load 1 at 4APRILTX (334041) 138 kV Bus b. 11. Drop Load BZ at 4LFOREST (334042) 138 kV Bus b. 12. Drop Load BZ at 4RABONCHAPEL (334049) 138 kV Bus b. 13. Drop Load BZ at 4WDHAVN (334105) 138 kV Bus b. 14. Drop Shunt 1 at 4BENTWATER! (334039) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1049_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4FISHCRK (334045) 138 kV Bus CKT 1 b. 2. Trip branch from 4FISHCRK (334045) 138 kV Bus to 4DEERLAKE (334048) 138 kV Bus CKT 1 b. 3. Trip branch from 4DEERLAKE (334048) 138 kV Bus to 4SPRINGBRNCH (334046) 138 kV Bus CKT 1 b. 4. Trip branch from 4SPRINGBRNCH (334046) 138 kV Bus to 4DOBBIN! (334044) 138 kV Bus CKT 1 b. 5. Trip branch from 4DOBBIN! (334044) 138 kV Bus to 4TUBULAR (334043) 138 kV Bus CKT 1 b. 6. Drop Load BZ at 4FISHCRK (334045) 138 kV Bus b. 7. Drop Load BZ at 4DEERLAKE (334048) 138 kV Bus b. 8. Drop Load BZ at 4SPRINGBRNCH (334046) 138 kV Bus b. 9. Drop Load 1 at 4DOBBIN! (334044) 138 kV Bus b. 10. Drop Load BZ at 4DOBBIN! (334044) 138 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1050_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4LONGMIR! (334075) 138 kV Bus CKT 1 b. 2. Trip branch from 4LONGMIR! (334075) 138 kV Bus to 4PANORAM (334074) 138 kV Bus CKT 1 b. 3. Trip branch from 4PANORAM (334074) 138 kV Bus to 4EGYPT (334073) 138 kV Bus CKT 1 b. 4. Trip branch from 4EGYPT (334073) 138 kV Bus to 4LEWIS% (334072) 138 kV Bus CKT 1 b. 5. Drop Load 1 at 4LONGMIR! (334075) 138 kV Bus b. 6. Drop Load 1 at 4PANORAM (334074) 138 kV Bus b. 7. Drop Load 1 at 4EGYPT (334073) 138 kV Bus b. 8. Drop Shunt 1 at 4LONGMIR! (334075) 138 kV Bus1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1051_P1 | 3 phase fault on 4PONDEROSA% (334087) 138 kV Bus a. Apply Fault at the 4PONDEROSA% (334087) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 4PONDEROSA% (334087) 138 kV Bus to 4CONROE1! (334104) 138 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1052_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to GREGGTN2 (508542) 69 kV Bus CKT 1 b. 2. Trip branch from GREGGTN2 (508542) 69 kV Bus to NETTLTP2 (508559) 69 kV Bus CKT 1 b. 3. Drop Load 1 at GREGGTN2 (508542) 69 kV Bus b. 4. Drop Load 2 at GREGGTN2 (508542) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1053_P1 | 3 phase fault on LLAMOND2 (508551) 69 kV Bus a. Apply Fault at the LLAMOND2 (508551) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LLAMOND2 (508551) 69 kV Bus to AIRLINE2 (508538) 69 kV Bus CKT 1 b. 2. Trip branch from AIRLINE2 (508538) 69 kV Bus to LONGVHT2 (508553) 69 kV Bus CKT 1 b. 3. Drop Load 1 at AIRLINE2 (508538) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1054_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO GREC TAP5 (512865) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1055_P4 | a. Apply single-phase fault on 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch 7SPORTSMAN (300740) 345 kV Bus TO GRDA1 7 (512650) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1056_P4 | a. Apply single-phase fault on GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 3. Disconnect BUS 512821 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1060_P4 | a. Apply single-phase fault on T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch T.NO.--7 (509852) 345 kV Bus TO IGLOOV 7 (513596) 345 kV Bus CKT 1 b. 3. Disconnect BUS 513592 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1061_P4 | a. Apply single-phase fault on CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch CLARMR 5 (512651) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Disconnect BUS 512700 b. 4. Disconnect BUS 512818 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1062_P4 | a. Apply single-phase fault on MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 1. Clear fault after 15 cycles: b. 2. Trip branch MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 3. Trip branch GRDA1 5 (512656) 161 kV Bus TO WMAIN ST5 (512742) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1063_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Trip branch from CLEVLND7 (512694) 345 kV Bus TO G15-066T (560056) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1064_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from T.NO.--7 (509852) 345 kV Bus TO CLEVLND7 (512694) 345 kV Bus CKT 1 b. 2. Clear fault at CLEVLND7 (512694) 345 kV Bus b. 3. Disconnect bus CLEVLND1 (512817) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1065_P4 | a. Apply single-phase fault at CLEVLND7 (512694) 345 kV Bus b. 1. Run for 15 cycles: b. 2. Trip branch from CLEVLND7 (512694) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Trip three winding from CLEVLND7 (512694) 345 kV Bus TO CLEVLND 4 (512729) 138 kV Bus TO CLEVLND1 (512817) 13.8 kV CKT 1 b. 4. Clear fault at CLEVLND7 (512694) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1066_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1067_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1068_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1069_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1070_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Disconnect bus MAITER1 1 (512836) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1071_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from 5CHOTEAU1 (300069) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GERALDGAY5 (512760) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1072_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from CATSAGR5 (512638) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1073_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1074_P4 | a. Apply single-phase fault at MAID 5 (512648) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 1 b. 2. Clear fault at MAID 5 (512648) 161 kV Bus b. 3. Trip branch from MAID 5 (512648) 161 kV Bus TO GRDA1 5 (512656) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1076_P4 | a. Apply single-phase fault at KERR GR5 (512635) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO MAID 5 (512648) 161 kV Bus CKT 1 b. 2. Clear fault at KERR GR5 (512635) 161 kV Bus b. 3. Trip branch from KERR GR5 ( 512635 ) 161 kV Bus TO MAID 5 ( 512648 ) 161 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1078_P4 | a. Apply single-phase fault at KETCHUM5 (512669) 161 kV Bus b. 1. Run for 15 cycles, Disconnect Bus 512632 b. 2. Clear fault at KETCHUM5 (512669) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 b. 4. Drop Load 1 Bus 512669 b. 5. Disconnect Bus 512669 b. 6. Disconnect Bus 512845 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1079_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1080_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from KERR GR5 (512635) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Disconnect bus PENSA 1 (512841) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1081_P4 | a. Apply single-phase fault at PENSA 5 (512654) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from DRYGULCH5 (512629) 161 kV Bus TO PENSA 5 (512654) 161 kV Bus CKT 1 b. 2. Clear fault at PENSA 5 (512654) 161 kV Bus b. 3. Trip branch from PENSA 5 (512654) 161 kV Bus TO KETCHUM5 (512669) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1084_P4 | a. Apply single-phase fault at TONECE5 (512751) 161 kV Bus b. 1. Run for 15 cycles, Trip branch from SILMCTY5 (512643) 161 kV Bus TO TONECE5 (512751) 161 kV Bus CKT 1 b. 2. Clear fault at TONECE5 (512751) 161 kV Bus b. 3. Disconnect Bus 512754 b. 4. Drop Load 1 Bus 512745 b. 5. Drop Load 1 Bus 512746 b. 6. Disconnect Bus 512728 b. 7. Disconnect Bus 512745 b. 8. Disconnect Bus 512746 b. 9. Disconnect Bus 512747 b. 10. Disconnect Bus 512756 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763002 [G18-064-GEN10.5500]
04 - Southeast | 25W | Transfer | Group4_Fault_1085_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from FLINTCR7 (506935) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1086_P4 | a. Apply single-phase fault at TONECE7 (512750) 345 kV Bus b. 1. Run for 15 cycles, Trip branch from GRDA1 7 (512650) 345 kV Bus TO TONECE7 (512750) 345 kV Bus CKT 1 b. 2. Clear fault at TONECE7 (512750) 345 kV Bus b. 3. Disconnect Bus 512752 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1087_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1088_P4 | a. Apply single-phase fault at WINDFRM4 (515785) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WINDFRM4 (515785) 138 kV Bus TO MOORLND4 (520999) 138 kV Bus CKT 1 b. 3. Trip branch from WOODWRD4 (514785) 138 kV Bus TO WINDFRM4 (515785) 138 kV Bus CKT 1 b. 4. Clear fault at WINDFRM4 (515785) 138 kV Bus b. 5. Drop Generator 1 Bus 515895 b. 6. Drop Load S1 Bus 515787 b. 7. Disconnect Bus 515785 b. 8. Disconnect Bus 515786 b. 9. Disconnect Bus 515787 b. 10. Disconnect Bus 515790 b. 11. Disconnect Bus 515895 b. 12. Disconnect Bus 515896 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1089_P4 | a. Apply single-phase fault at SUNNYSD7 (515136) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip three winding transformer from SUNNYSD7 (515136) 345 kV Bus TO SUNNYSD4 (515135) 138 kV TO SUNYSD 1 (515405) 13.8 kV CKT 1 b. 3. Disconnect Bus SUNYSD 1 (515405) 13.8 kV CKT 1 b. 4. Trip branch from SUNNYSD7 (515136) 345 kV Bus TO G16-063-TAP (560088) 138 kV Bus CKT 1 b. 5. Clear fault at SUNNYSD7 (515136) 345 kV Bus b. 6. Drop Shunt 1 Bus SUNYSD 1 (515405) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1090_P4 | a. Apply single-phase fault at DRAPER 4 (514933) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus 514946 b. 3. Trip branch from DRAPER 4 (514933) 138 kV Bus TO SOONRTP4 (514949) 138 kV Bus CKT 1 b. 4. Clear fault at DRAPER 4 (514933) 138 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1091_P4 | a. Apply single-phase fault at WAUKOTP4 (514711) 138 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 3. Trip branch from WAUKOTP4 (514711) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 4. Run for 10 cycles: b. 5. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO FAIRMON4 (514712) 138 kV Bus CKT 1 b. 6. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO WOODRNG4 (514714) 138 kV Bus CKT 1 b. 7. Trip branch from FRMNTAP4 (514709) 138 kV Bus TO SO4TH 4 (514731) 138 kV Bus CKT 1 b. 8. Clear fault at WAUKOTP4 (514711) 138 kV Bus b. 9. Disconnect Bus WAUKOTP4 (514711) 138 kV b. 10. Disconnect Bus FRMNTAP4 (514709) 138 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1092_P4 | a. Apply single-phase fault at JOHNCO 7 (514809) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO JOHNCO 7 (514809) 345 kV Bus CKT 1 b. 3. Trip branch from JOHNCO 7 (514809) 345 kV Bus TO SUNNYSD7 (515136) 345 kV Bus CKT 1 b. 4. Clear fault at JOHNCO 7 (514809) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1093_P4 | a. Apply single-phase fault at GRACMNT7 (515800) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G16-091-TAP (587744) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 3. Trip branch from MINCO 7 (514801) 345 kV Bus TO GRACMNT7 (515800) 345 kV Bus CKT 1 b. 4. Clear fault at GRACMNT7 (515800) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1095_P4 | a. Apply single-phase fault at PECANCK7 (515235) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO PECANCK7 (515235) 345 kV Bus CKT 1 b. 3. Disconnect Bus PECANC21 (515759) 13.8 kV b. 4. Clear fault at PECANCK7 (515235) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1097_P4 | a. Apply single-phase fault at REDBUD 7 (514909) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from ARCADIA7 (514908) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 2 b. 3. Trip branch from R.S.S.-7 (509782) 345 kV Bus TO REDBUD 7 (514909) 345 kV Bus CKT 1 b. 4. Clear fault at REDBUD 7 (514909) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1098_P4 | a. Apply single-phase fault at FTSMITH8 (515305) 500 kV Bus b. 1. Run for 16 cycles: b. 2. Disconnect Bus FTSMTH31 (515727) 13.8 kV b. 3. Trip branch from 8ANO% (337909) 500 kV Bus TO FTSMITH8 (515305) 500 kV Bus CKT 1 b. 4. Clear fault at FTSMITH8 (515305) 500 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1099_P4 | a. Apply single-phase fault at SEMINOL7 (515045) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from PITTSB-7 (510907) 345 kV Bus TO SEMINOL7 (515045) 345 kV Bus CKT 1 b. 3. Disconnect Bus SEMINO21 (515757) 14.4 kV b. 4. Clear fault at SEMINOL7 (515045) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1100_P4 | a. Apply single-phase fault at SOONER 7 (514803) 345 kV Bus b. 1. Run for 16 cycles: b. 2. Trip branch from G15-066T (560056) 345 kV Bus TO SOONER 7 (514803) 345 kV Bus CKT 1 b. 3. Disconnect Bus SOONER 1 (515760) 13.8 kV b. 4. Clear fault at SOONER 7 (514803) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1101_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1102_P4 | a. Apply single-phase fault at VBI 5 (515339) 161 kV Bus b. 1. Run for 23.52 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 2. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 3. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 4. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 5. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 6. Run for 11.28 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 7. Run for 2.1 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 8. Run for 1.2 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 9. Run for 1.5 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 10. Run for 3.9 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 11. Run for 1.62 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 12. Run for 9.18 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 13. Run for 4.02 cycles, Trip branch from VAN BUR5 (505522) 161 kV Bus TO VBI 5 (515339) 161 kV Bus KT Z1 b. 14. Run for 4.2 cycles, Trip branch from OAKPARK5 (515315) 161 kV Bus TO GERBRTP5 (515326) 161 kV Bus CKT 1 b. 15. Run for 2.4 cycles, Trip branch from MASSARD5 (515343) 161 kV Bus TO WHITESD5 (515341) 161 kV Bus CKT 1 b. 16. Run for 0.18 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 17. Run for 2.82 cycles, Trip branch from HELBERG5 (515327) 161 kV Bus TO PUDDIN 5 (515346) 161 kV Bus CKT 1 b. 18. Run for 6.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 19. Run for 1.44 cycles, Trip branch from BRANCH 5 (515316) 161 kV Bus TO GRNDPRT5 (515524) 161 kV Bus CKT 1 b. 20. Run for 19.38 cycles, Disconnect Bus VBI 1 (515769) 13.8 kV b. 21. Run for 23.82 cycles, Trip branch from ROLANRD2 (515257) 69 kV Bus TO ROLANTP2 (515277) 69 kV Bus CKT 1 b. 22. Run for 18.36 cycles, Trip branch from TAHLQH 5 (512655) 161 kV Bus TO HWY59TP5 (515527) 161 kV Bus CKT 1 b. 23. Clear fault at bus VBI 5 (515339) 161 kV Bus b. 24. Drop Load A1 Bus 504191 b. 25. Drop Load A1 Bus 504192 b. 26. Drop Load 1 Bus 515332 b. 27. Drop Load A1 Bus 515332 b. 28. Drop Load A1 Bus 515333 b. 29. Drop Load 1 Bus 515334 b. 30. Drop Load A1 Bus 515337 b. 31. Drop Load A1 Bus 515340 b. 32. Drop Load 1 Bus 515341 b. 33. Drop Load A1 Bus 515346 b. 34. Drop Load 1 Bus 515350 b. 35. Drop Load 1 Bus 515351 b. 36. Drop Load 1 Bus 515360 b. 37. Drop Load 1 Bus 515406 b. 38. Disconnect Bus 504191 b. 39. Disconnect Bus 504192 b. 40. Disconnect Bus 515326 b. 41. Disconnect Bus 515329 b. 42. Disconnect Bus 515332 b. 43. Disconnect Bus 515333 b. 44. Disconnect Bus 515334 b. 45. Disconnect Bus 515337 b. 46. Disconnect Bus 515340 b. 47. Disconnect Bus 515341 b. 48. Disconnect Bus 515346 b. 49. Disconnect Bus 515348 b. 50. Disconnect Bus 515350 b. 51. Disconnect Bus 515351 b. 52. Disconnect Bus 515360 b. 53. Disconnect Bus 515406 b. 54. Disconnect Bus 515524 b. 55. Disconnect Bus 515527 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1103_P4 | a. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus b. 1. Run for 56.88 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 2. Run for 19.22 cycles, Disconnect Bus WOODWR21 (515771) 13.2 kV b. 3. Run for 0.66 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 4. Run for 49.74 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 b. 5. Run for 7.14 cycles, Trip WINDFRM4 (515785) 138 kV Bus TO WOODWRD4 (514785) 138 kV Bus CKT 1 b. 6. Clear fault at WODWRD 2 (514782) 69 kV Bus c. 1. Apply single-phase fault at WODWRD 2 (514782) 69 kV Bus c. 2. Run for 12.84 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 3. Run for 126.6 cycles, Trip WODWRD 2 (514782) 69 kV Bus TO CEDARAV2 (514781) 69 kV Bus CKT 1 c. 4. Clear fault at WODWRD 2 (514782) 69 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1104_P4 | a. Apply single-phase fault at CTNWOOD4 (514827) 138 kV Bus b. 1. Run for 22 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 2. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 3. Run for 0.3 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 4. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 5. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 6. Run for 10.38 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 7. Run for 3.3 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 8. Run for 3.96 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 9. Run for 0.3 cycles, Trip CRESENT4 515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 10. Run for 1.74 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 11. Run for 0.3 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 12. Run for 9.3 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 13. Run for 1.08 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 14. Run for 5.34 cycles, Trip MCELROY4 (515009) 138 kV Bus TO UNVRSTY4 (515181) 138 kV Bus CKT 1 b. 15. Run for 7.92 cycles, Trip KETCH 4 (514834) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 16. Run for 0.6 cycles, Trip CRESENT4 (515377) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 17. Run for 3.48 cycles, Trip KINZE 4 (515008) 138 kV Bus TO KINZEGR4 (512710) 138 kV Bus CKT 1 b. 18. Run for 0.6 cycles, Trip WOODRNG4 (514714) 138 kV Bus TO MARSHL 4 (514733) 138 kV Bus CKT 1 b. 19. Run for 0.96 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 20. Run for 19.8 cycles, Trip ARCADIA4 (514907) 138 kV Bus TO CTNWOOD4 (514827) 138 kV Bus CKT 1 b. 21. Run for 37.8 cycles, Trip NORTWST4 (514879) 138 kV Bus TO KETCHTP4 (514828) 138 kV Bus CKT 1 b. 22. Clear fault at CTNWOOD4 ( 514827 ) 138 kV Bus b. 23. Drop Load 1 Bus 514827 b. 24. Drop Load 1 Bus 514829 b. 25. Drop Load 2 Bus 514829 b. 26. Drop Load 1 Bus 514830 b. 27. Drop Load 1 Bus 514831 b. 28. Drop Load 1 Bus 515181 b. 29. Drop Load 1 Bus 515373 b. 30. Drop Load 1 Bus 515466 b. 31. Drop Load 1 Bus 515467 b. 32. Drop Load 1 Bus 521006 b. 33. Disconnect Bus 514733 b. 34. Disconnect Bus 514827 b. 35. Disconnect Bus 514828 b. 36. Disconnect Bus 514829 b. 37. Disconnect Bus 514830 b. 38. Disconnect Bus 514831 b. 39. Disconnect Bus 515008 b. 40. Disconnect Bus 515181 b. 41. Disconnect Bus 515373 b. 42. Disconnect Bus 515466 b. 43. Disconnect Bus 515467 b. 44. Disconnect Bus 521006 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1105_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV CB OR335 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1106_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip branch from RSVLT_CC_E 7 (527655) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1107_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB 4R00 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1108_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1109_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB J24 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1110_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 4. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1111_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV CB OR70 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1112_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R15 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1113_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R30 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt 1 HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1114_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV CB 1R75 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1115_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV CB 4R240 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1117_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_1118_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1119_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 584862 [G15-045-GEN10.4800], 762903 [G18-055-GEN10.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1120_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S105 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 3. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1121_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S110 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 4. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1122_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV CB 4S120 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from KIOWA 7 (527965) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1123_P4 | a. Apply single phase fault at BATTLEFIELD5 (549959) 161 kV CB 111 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from GOLDEN 2 (549911) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 2. Trip branch from DAYTON 2 (549913) 69 kV to BATTLEFIELD2 (549979) 69 kV CKT 1 b. 3. Trip branch from MAIN STREET5 (549958) 161 kV to BATTLEFIELD5 (549959) 161 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1124_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1125_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV CB 2R05 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus BUFF_DUNES23 (523061) 0.69 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1126_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV CB PRE19S Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1127_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1128_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR05 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1129_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV CB NR20 Stuck b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from CRAWFISH_DR (560022) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1130_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J17 Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 3. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1131_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1132_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB J18_2 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1133_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV CB TF Stuck b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 4. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 5. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 6. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1134_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV Bus TO 5SOUTHLAND# (338814) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338125 b. 8. Drop Load A1 Bus 338813 b. 9. Drop Load A1 Bus 338814 b. 10. Disconnect Bus 338125 b. 11. Disconnect Bus 338606 b. 12. Disconnect Bus 338607 b. 13. Disconnect Bus 338608 b. 14. Disconnect Bus 338609 b. 15. Disconnect Bus 338813 b. 16. Disconnect Bus 338814 b. 17. Disconnect Bus 505462 b. 18. Disconnect Bus 505464 b. 19. Disconnect Bus 505466 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1135_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 Cycles, Trip branch from Bus 5HARRISON.E! (338104) 161 kV To Bus 5SUMMIT (338121) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Drop Load 1 Bus 338121 b. 8. Drop Load 1 Bus 338122 b. 9. Drop Load 1 Bus 338124 b. 10. Disconnect Bus 338121 b. 11. Disconnect Bus 338122 b. 12. Disconnect Bus 338123 b. 13. Disconnect Bus 338124 b. 14. Disconnect Bus 505462 b. 15. Disconnect Bus 505464 b. 16. Disconnect Bus 505466 b. 17. Drop Load A1 Bus 338813 b. 18. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1136_P4 | a. Apply single-phase fault at BULL SH5 (505460) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus 5MANSFDMN (300095) 161 kV To Bus 5GAINES (300081) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH5 (505460) 161 kV b. 3. Drop Generator 1 Bus 505462 b. 4. Drop Generator 2 Bus 505464 b. 5. Drop Generator 3 Bus 505466 b. 6. Drop Generator 4 Bus 505466 b. 7. Disconnect Bus 505462 b. 8. Disconnect Bus 505464 b. 9. Disconnect Bus 505466 b. 10. Drop Load A1 Bus 338813 b. 11. Disconnect Bus 338813 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1137_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip branch from Bus BULL SH W5 (505461) 161 kV To Bus 5S.LEAD HILL (338120) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505473 b. 12. Disconnect Bus 505475 b. 13. Disconnect Bus 505476 b. 14. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1138_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus 5RENOHLWTP (300130) 161 kV To Bus 5RIVERSIDE (300805) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1139_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV Run For 5.0 Cycles, Open Line From Bus 5GRANDVIEW% (338099) 161 kV To Bus TABLE R5 (505472) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1140_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run For 5.0 Cycles, Open Line From Bus NIXA 5 (505496) 161 kV To Bus TABLE R5 (505472) 161 CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1141_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Open Line From Bus RVS438 5 (547497) 161 kV To TABLE R5 (505472) 161 kV Bus CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus TABLE R5 (505472) 161 kV b. 3. Drop Generator 1 Bus 505476 b. 4. Drop Generator 2 Bus 505476 b. 5. Drop Generator 3 Bus 505478 b. 6. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 8. Disconnect Bus 505475 b. 9. Disconnect Bus 505476 b. 10. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1142_P4 | a. Apply single-phase fault at TABLE R5 (505472) 161 kV b. 1. Run for 5 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X1 1 (505473) 13.8 kV CKT 1 b. 2. Run For 12.0 cycles, Trip Three winding transformer from TABLE R5 (505472) 161 kV To Bus TABLE R2 (505474) 69 kV To Bus TBR X2 1 (505475) 13.8 kV CKT 1 b. 3. Clear fault at TABLE R5 (505472) 161 kV b. 4. Disconnect Bus TBR X1 1 (505473) 13.8 kV b. 5. Drop Generator 1 Bus 505476 b. 6. Drop Generator 2 Bus 505476 b. 7. Drop Generator 3 Bus 505478 b. 8. Drop Generator 4 Bus 505478 b. 7. Disconnect Bus 505473 b. 9. Disconnect Bus 505475 b. 10. Disconnect Bus 505476 b. 11. Disconnect Bus 505478 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1143_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus TABLE R5 (505472) 161 kV To Bus 5CLEVCOV (300718) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load 1 Bus 300718 b. 8. Drop Load 1 Bus 338120 b. 9. Disconnect Bus 300718 b. 10. Disconnect Bus 338120 b. 11. Disconnect Bus 505468 b. 12. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1144_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus b. 1. Run for 5 cycles, Trip branch from Bus NORFORK5 (505448) 161 kV To Bus BUFORD 5 (504440) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Drop Load A1 Bus 504440 b. 8. Disconnect Bus 504440 b. 9. Disconnect Bus 505468 b. 10. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1145_P4 | a. Apply single-phase fault at BULL SH W5 (505461) 161 kV Bus Run For 5 Cycles, Trip branch from Bus 5HILLTOP% (338110) 161 kV To Bus BULL SH W5 (505461) 161 kV CKT 1 b. 2. Clear fault and run for 12 cycles, Disconnect Bus BULL SH W5 (505461) 161 kV b. 3. Drop Generator 5 Bus 505468 b. 4. Drop Generator 6 Bus 505468 b. 5. Drop Generator 7 Bus 505470 b. 6. Drop Generator 8 Bus 505470 b. 7. Disconnect Bus 505468 b. 8. Disconnect Bus 505470 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1146_P4 | a. Apply single-phase fault at BATTLEFIELD2 (549979) 69 kV b. 1. Run for 8 cycles: b. 2. Trip branch from GOLDEN 2 (549911) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 3. Trip branch from DAYTON 2 (549913) 69 kV Bus TO BATTLEFIELD2 (549979) 69 kV Bus CKT 1 b. 4. Clear fault and run for 10 cycles, Trip branch from MAIN STREET5 (549958) 161 kV Bus TO BATTLEFIELD5 (549959) 161 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1147_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1148_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1150_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1151_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1152_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1153_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1154_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1155_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1156_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1157_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1158_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1159_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1160_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1161_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1162_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1163_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1164_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1165_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1167_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1168_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1169_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1170_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1171_P4 | a. Apply single-phase fault at WHEELER 6 (523777) 230 kV Bus b. 1. Run for 21.0 Cycles: b. 2. WHEELER 6 (523777) 230 kV Bus TO STLN-DEMARC6 (523779) 230 kV Bus CKT 1 b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1172_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1173_P4 | a. Apply fault at bus HITCHLAND 7 (523097) 345 kV b. 1. Run for 5.0 cycles, Disconnect bus 523091 b. 2. Run for 11.0 cycles, Disconnect bus 523091 b. 3. Clear fault bus 523097 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1174_P4 | a. Apply Fault at Bus WHEELER 6 (523777) 230 kV b. 1. Run for 5 cycles, Disconnect Bus 523774 b. 2. Run for 11 cycles: b. 3. Disconnect Bus 523777 b. 4. Disconnect Bus 523774 b. 5. Clear Fault Bus 523777 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1175_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1176_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus 524267 b. 4. Disconnect bus 524285 b. 5. Disconnect bus 524287 b. 6. Clear fault at bus 524267 b. 7. Disconnect Bus 524263 b. 8. Disconnect Bus 524275 b. 9. Disconnect Bus 524276 b. 10. Disconnect Bus 524289 b. 11. Disconnect Bus 524290 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1177_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1178_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Run for 11 cycles: b. 3. Disconnect bus TUCO_TR3 1 (525819) 13.2 kV b. 4. Clear fault at bus TUCO_INT 6 (525830) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
04 - Southeast | 25W | Transfer | Group4_Fault_1179_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1182_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1184_P4 | a. Apply single-phase fault at 531449 b. 1. Run For 12.0 Cycles, Open Line From Bus 531449 To Bus 531465 CKT 1 b. 2. Clear Fault Bus 531449 b. 3. Open Line From Bus 523853 To Bus 531449 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1185_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520864 To Bus 520900 CKT 1 b. 3. Open Line From Bus 520912 To Bus 520900 CKT 1 b. 4. Open Line From Bus 520923 To Bus 520912 CKT 1 b. 5. Run For 9.0 Cycles b. 6. Open Line From Bus 520814 To Bus 520422 CKT 1 b. 7. Open Line From Bus 520422 To Bus 520473 CKT 1 b. 8. Open Line From Bus 520473 To Bus 520867 CKT 1 b. 9. Open Line From Bus 520888 To Bus 520510 CKT 1 b. 10. Open Line From Bus 520867 To Bus 520510 CKT 1 b. 11. Clear Fault Bus 520814 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1187_P4 | a. Apply single-phase fault at 520814 b. 1. Run For 6.0 Cycles, Open Line From Bus 520814 To Bus 521129 CKT 1 b. 1. Clear fault and run For 9.0 Cycles, Open Line From Bus 511477 To Bus 520814 CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
04 - Southeast | 25W | Transfer | Group4_Fault_1188_P4 | a. Apply single-phase fault at 520917 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520400 To Bus 520842 CKT 1 b. 3. Run For 9.0 Cycles b. 4. Disconnect Bus 514946 b. 5. Open Line From Bus 520917 To Bus 520975 CKT 1 b. 6. Clear Fault Bus 520917 b. 7. Drop Load 1 Bus 520400 b. 8. Drop Load 1 Bus 520975 b. 9. Disconnect Bus 520400 b. 10. Disconnect Bus 520975 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1189_P4 | a. Apply single-phase fault at 520920 b. 1. Run For 6.0 Cycles b. 2. Open Line From Bus 520920 To Bus 520922 CKT 1 b. 3. Drop Generator 1 Bus 521145 b. 4. Disconnect Bus 520922 b. 5. Disconnect Bus 521141 b. 6. Disconnect Bus 521144 b. 7. Disconnect Bus 521145 b. 8. Disconnect Bus 521151 b. 9. Run For 9.0 Cycles Print 0 Plot 3 Crtplt 0 b. 10. Open Line From Bus 520957 To Bus 520999 CKT 1 b. 11. Clear Fault Bus 520920 b. 12. Open Line From Bus 520920 To Bus 520957 CKT 1 b. 13. Drop Load 1 Bus 520957 b. 14. Disconnect Bus 520957 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1190_P4 | a. Apply single-phase fault at 520948 b. 1. Run For 6.0 Cycles, Open Line From Bus 510887 To Bus 520968 CKT 1 b. 2. Run For 9.0 Cycles b. 3. Open Line From Bus 520948 To Bus 520918 CKT 1 b. 4. Open Line From Bus 505602 To Bus 521049 CKT 1 b. 5. Clear Fault Bus 520948 b. 6. Drop Load 1 Bus 515370 b. 7. Drop Load 1 Bus 515568 b. 8. Drop Load 1 Bus 520463 b. 9. Drop Load 1 Bus 520483 b. 10. Drop Load 1 Bus 520497 b. 11. Drop Load 1 Bus 520918 b. 12. Drop Load 1 Bus 521077 b. 13. Drop Load 1 Bus 521115 b. 14. Disconnect Bus 515370 b. 15. Disconnect Bus 515568 b. 16. Disconnect Bus 520463 b. 17. Disconnect Bus 520483 b. 18. Disconnect Bus 520497 b. 19. Disconnect Bus 520826 b. 20. Disconnect Bus 520884 b. 21. Disconnect Bus 520918 b. 22. Disconnect Bus 521049 b. 23. Disconnect Bus 521077 b. 24. Disconnect Bus 521098 b. 25. Disconnect Bus 521115 b. 26. Drop Load 1 Bus 520411 b. 27. Drop Load 1 Bus 520874 b. 28. Drop Load 1 Bus 520968 b. 29. Drop Load 1 Bus 521036 b. 30. Disconnect Bus 520411 b. 31. Disconnect Bus 520874 b. 32. Disconnect Bus 520968 b. 33. Disconnect Bus 521036 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1192_P4 | a. Apply single-phase fault at MARIETA4 (520988) 138 kV CB 472 Stuck b. 1. Run for 6 cycles, Trip branch from CANEYCK4 (515150) 138 kV To Bus 521067 CKT 1 b. 2 Run For 9 cycles: b. 3. Trip branch from 5MARIETA4 (520988) 138 kV To Bus TEXOMAJ4 (521061)138 kV CKT 1 b. 4. Trip branch from 520981 To Bus 520939 CKT 1 b. 5. Clear Fault Bus 520988 b. 6. Drop Load 1 Bus 520455 b. 7. Drop Load 1 Bus 520487 b. 8. Drop Load 1 Bus 520488 b. 9. Drop Load 1 Bus 520511 b. 10. Drop Load 1 Bus 520901 b. 11. Drop Load 1 Bus 521038 b. 12. Drop Load 1 Bus 521061 b. 13. Drop Load 1 Bus 521066 b. 14. Disconnect Bus 520455 b. 15. Disconnect Bus 520467 b. 16. Disconnect Bus 520487 b. 17. Disconnect Bus 520488 b. 18. Disconnect Bus 520511 b. 19. Disconnect Bus 520901 b. 20. Disconnect Bus 520939 b. 21. Disconnect Bus 520972 b. 22. Disconnect Bus 521038 b. 23. Disconnect Bus 521061 b. 24. Disconnect Bus 521066 b. 25. Disconnect Bus 521067 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1193_P4 | a. Apply single-phase fault at NOELSW 4 (520430) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DRIFTWD4 (521200) 138 kV Bus TO CHRKCTY4 (520431) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch from ROSEVLY4 (520436) 138 kV Bus TO NOELSW 4 (520430) 138 kV Bus CKT 1 b. 4. Trip branch from NOELSW 4 (520430) 138 kV Bus TO SALTPLN4 (520437) 138 kV Bus CKT 1 b. 5. Clear fault at NOELSW 4 (520430) 138 kV Bus b. 6. Drop Load 1 Bus 520431 b. 7. Drop Load 1 Bus 520437 b. 8. Drop Load 2 Bus 520437 b. 9. Disconnect Bus 520431 b. 10. Disconnect Bus 520437 b. 11. Drop Load 1 Bus 520436 b. 12. Drop Load 1 Bus 520601 b. 13. Disconnect Bus 520436 b. 14. Disconnect Bus 520601 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1194_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from DOVERSW4 (520882) 138 kV Bus TO OKEENE 4 (521016) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch MOORLND4 (520999) 138 kV Bus TO PIC4 (520425) 138 kV Bus CKT 1 Bus CKT 1 b. 3. Drop Load 1 Bus 520425 b. 4. Drop Load 1 Bus 520507 b. 5. Disconnect Bus 520425 b. 6. Disconnect Bus 520848 b. 7. Disconnect Bus 520507 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1195_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1196_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch CLINTJC4 (511485) 138 kV Bus TO CLINTON4 (520856) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 3. Trip branch ONEY 4 (521017) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 4. Clear fault at WASHITA4 (521089) 138 kV Bus b. 5. Drop Load 1 Bus 520468 b. 6. Drop Load 1 Bus 520503 b. 7. Drop Load 1 Bus 520856 b. 8. Drop Load 1 Bus 520950 b. 9. Drop Load 1 Bus 521010 b. 10. Drop Load 2 Bus 521010 b. 11. Drop Load 1 Bus 521017 b. 12. Drop Load 1 Bus 521050 b. 13. Drop Load 1 Bus 521092 b. 14. Disconnect Bus 520468 b. 15. Disconnect Bus 520503 b. 16. Disconnect Bus 520827 b. 17. Disconnect Bus 520856 b. 18. Disconnect Bus 520950 b. 19. Disconnect Bus 521010 b. 20. Disconnect Bus 521017 b. 21. Disconnect Bus 521050 b. 22. Disconnect Bus 521092 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1197_P4 | a. Apply single-phase fault at WASHITA4 (521089) 138 kV Bus b. 1. Run for 6 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 1 b. 2. Clear fault and run for 9 cycles, Trip branch GRACMNT4 (515802) 138 kV Bus TO WASHITA4 (521089) 138 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1198_P4 | a. Apply single-phase fault at ANADARK4 (520814) 138 kV Bus b. 1. Run for 6 cycles: b. 2. Trip branch from COMANCH4 (520864) 138 kV Bus TO EMPIRE 4 (520900) kV 138 kV Bus CKT 1 b. 3. Trip Three winding transformer from FLETCH-4 (520912) 138 kV TO FLETCHR2 (520911) 69 kV TO FLCHTERT (521168) 13.8 kV CKT 1 b. 4. Run for 9 cycles: b. 5. Trip branch from SEQUOYAHJ4 (520422) 138 kV Bus TO ANADARK4 (520814) kV 138 kV Bus CKT 1 b. 6. Trip branch from PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) kV 138 kV Bus CKT 1 b. 7. Trip branch from CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 8. Clear fault at ANADARK4 (520814) 138 kV Bus b. 9. Drop Load 1 Bus 520547 b. 10. Drop Load 2 Bus 520547 b. 11. Drop Load 1a Bus 520604 b. 12. Disconnect Bus 520422 b. 13. Disconnect Bus 520510 b. 14. Disconnect Bus 520604 b. 15. Disconnect Bus 520867 b. 16. Disconnect Bus 520547 b. 17. Drop Load 1 Bus 520900 b. 18. Drop Load 1 Bus 520923 b. 19. Disconnect Bus 520900 b. 20. Disconnect Bus 520923 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | Group4_Fault_1199_P4 | a. Apply single-phase fault at PAYNESW4 (520888) 138 kV Bus b. 1. Run for 6 cycles, Trip branch from OU SW 4 (521104) 138 kV Bus TO COLE 4 (520861) 138 kV Bus CKT 1 b. 2. Run for 9 cycles: b. 3. Trip PAYNESW4 (520888) 138 kV Bus TO NAPLSTP4 (520510) 138 kV Bus CKT 1 b. 4. Trip PAYNESW4 (520888) 138 kV Bus TO CRINER 4 (520868) 138 kV Bus CKT 1 b. 5. Trip CORNVIL4 (511449) 138 kV Bus TO CORN TP4 (520867) 138 kV Bus CKT 1 b. 6. Trip ANADARK4 (520814) 138 kV Bus TO CLVLDSW4 (520508) 138 kV Bus CKT 1 b. 7. Clear fault at PAYNESW4 (520888) 138 kV Bus Drop Load 1 at 520547 Drop Load 2 at 520547 Drop Load 1A at 520604 Disconnect Bus 520422 Disconnect Bus 520510 Disconnect Bus 520604 Disconnect Bus 520867 Disconnect Bus 520547 Drop Load 1 Bus 520861 Drop Load 1 Bus 520868 Disconnect Bus 520861 Disconnect Bus 520868 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0001_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to PLANT_X 6 (525481) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0002_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0003_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0004_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0005_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to G17-146-TAP (760498) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0006_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR1 1 (525479) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0007_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR2 (525478) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0008_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0009_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763189 [G18-089-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0010_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR11 (525459) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0011_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR21 (525458) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0012_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0013_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to NEEDMORE 6 (525586) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0014_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0015_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763257 [G18-099-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0016_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0017_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0018_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNDOWN 6 (526435) 230 kV Bus to SUNDOWN 3 (526434) 115 kV Bus to SUNDOWN_TR11 (526432) 13.8 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0019_P1 | 3 phase fault on G17-146-TAP (760498) 230 kV Bus a. Apply Fault at the G17-146-TAP (760498) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G17-146-TAP (760498) 230 kV Bus to DEAFSMITH 6 (524623) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0020_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to MULSHVLY_TP3 (525019) 115 kV Bus CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to MULESHVALLY3 (525018) 115 kV Bus CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MULESHVALLY3 (525018) 115 kV Bus b. 5. Drop Load 2 at MULESHVALLY3 (525018) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0021_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to RKYFORD_TP 3 (525446) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0022_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0023_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0024_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to BC-EARTH 3 (525056) 115 kV Bus CKT 1 b. 2. Trip branch from BC-EARTH 3 (525056) 115 kV Bus to BC-KELLEY +3 (525050) 115 kV Bus CKT 1 b. 3. Trip branch from BC-KELLEY +3 (525050) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 b. 4. Drop Load 1 at BC-EARTH 3 (525056) 115 kV Bus b. 5. Drop Load 1 at BC-KELLEY +3 (525050) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0025_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0026_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0027_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SWISHER 6 (525213) 230 kV Bus to SWISHER 3 (525212) 115 kV Bus to SWISHER_TR11 (525211) 13.2 kV Bus CKT 1 b. 2. Trip branch from SWISHER 3 (525212) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0028_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0029_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0030_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to HART_INDUST3 (525124) 115 kV Bus CKT 1 b. 2. Trip branch from HART_INDUST3 (525124) 115 kV Bus to LAMTON 3 (525414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HART_INDUST3 (525124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0031_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0032_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PNM-DC6 (599955) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0033_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROOSEVELT 6 (524909) 230 kV Bus to ROOSEVELT 3 (524908) 115 kV Bus to ROSEVLT_TR11 (524907) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0034_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PLSNT_HILL 6 (524770) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0035_P1 | 3 phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply Fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE 6 (525586) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0036_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0037_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0038_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR4 1 (525821) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0039_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR3 1 (525819) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0040_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0041_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFFORTH 6 (526525) 230 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus to WOLFRTH_TR11 (526522) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0042_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0043_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to AMOCO_TP 3 (526445) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0044_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to LC-OPDYKE 3 (526036) 115 kV Bus CKT 1 b. 2. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LC-OPDYKE 3 (526036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0045_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to PACIFIC 3 (526424) 115 kV Bus CKT 1 b. 2. Trip branch from PACIFIC 3 (526424) 115 kV Bus to COCHRAN 3 (526361) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PACIFIC 3 (526424) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0046_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEAFSMITH 6 (524623) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0047_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_EST 3 (524619) 115 kV Bus to DEFSMTH_TR21 (524621) 13.8 kV Bus CKT 2 b. 2. Trip branch from DFSMTH_EST 3 (524619) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0048_P1 | 3 phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply Fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0049_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to AMOCO_CRYO 3 (526452) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AMOCO_CRYO 3 (526452) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0050_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0051_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0052_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0053_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0054_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to MURPHY 3 (526192) 115 kV Bus CKT 1 b. 2. Trip branch from MURPHY 3 (526192) 115 kV Bus to QUINCY 3 (526195) 115 kV Bus CKT 1 b. 3. Trip branch from QUINCY 3 (526195) 115 kV Bus to SP-MILWAUKEE (526196) 115 kV Bus CKT 1 b. 4. Trip branch from SP-MILWAUKEE (526196) 115 kV Bus to SP-UPLAND (526198) 115 kV Bus CKT 1 b. 5. Drop Load 1 at MURPHY 3 (526192) 115 kV Bus b. 6. Drop Load D2 at MURPHY 3 (526192) 115 kV Bus b. 7. Drop Load 1 at SP-MILWAUKEE (526196) 115 kV Bus b. 8. Drop Load 1 at SP-UPLAND (526198) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0055_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0056_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0057_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0058_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0059_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0060_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6 (523323) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0061_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MCDWL_CREEK6 (523323) 230 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus to MCDWL_CRKTR1 (523321) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0062_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0063_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from PRINGLE 6 (523267) 230 kV Bus to PRINGLE 3 (523266) 115 kV Bus to PRINGLE_TR 1 (523265) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0064_P1 | 3 phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply Fault at the ROLLHILLS 6 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROLLHILLS 6 (524010) 230 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus to ROLHILLS_TR1 (524008) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0065_P1 | 3 phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply Fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BUSHLAND 6 (524267) 230 kV Bus to BUSHLAND 3 (524266) 115 kV Bus to BSHLND_TR1 1 (524263) 13.2 kV Bus CKT 1 b. 2. Trip branch from BUSHLAND 3 (524266) 115 kV Bus to OUTPOST 3 (524243) 115 kV Bus CKT 1 b. 3. Trip branch from OUTPOST 3 (524243) 115 kV Bus to ARNOT 3 (524560) 115 kV Bus CKT 1 b. 4. Trip branch from ARNOT 3 (524560) 115 kV Bus to HILLSIDE 3 (524300) 115 kV Bus CKT 1 b. 5. Trip branch from HILLSIDE 3 (524300) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 b. 6. Drop Load 1 at OUTPOST 3 (524243) 115 kV Bus b. 7. Drop Load 1 at ARNOT 3 (524560) 115 kV Bus b. 8. Drop Load 1 at HILLSIDE 3 (524300) 115 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0066_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0067_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 6 (524365) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0068_P1 | 3 phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from AMA_SOUTH 6 (524415) 230 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus to AMA_SO_TR1 1 (524410) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0069_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0070_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0071_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0072_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0073_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0074_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to NICHOLS 6 (524044) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0075_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#22 3 (524694) 115 kV Bus CKT 1 b. 2. Drop Load 1 at DS-#22 3 (524694) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0076_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR1 1 (524744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0077_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR2 1 (524743) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0078_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#21 3 (524734) 115 kV Bus CKT 1 b. 2. Trip branch from DS-#21 3 (524734) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 3. Drop Load 1 at DS-#21 3 (524734) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0079_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to KRS_RURL_TP3 (525226) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0080_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV Bus to KRESS_INT 2 (525191) 69 kV Bus to KRESS_TR1 1 (525190) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0081_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0082_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0083_P1 | 3 phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORE_CNTY 6 (523309) 230 kV Bus to MOORE_E 3 (523308) 115 kV Bus to MOORE_TR1 1 (523302) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0084_P1 | 3 phase fault on MCDWL_CREEK3 (523322) 115 kV Bus a. Apply Fault at the MCDWL_CREEK3 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK3 (523322) 115 kV Bus to EXELL_TP 3 (523332) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0085_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV Bus to PLSNT_HILL 3 (524768) 115 kV Bus to PLSNHIL_TR11 (524767) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0086_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 6 (524770) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0087_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OASIS 6 (524875) 230 kV Bus to OASIS 3 (524874) 115 kV Bus to OASIS_TR1 113.200 (524872) kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0088_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 6 (524875) 230 kV Bus to SN_JUAN_TAP6 (524885) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0089_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0090_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0091_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0092_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0093_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0094_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0095_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0096_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0097_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to GRASSLAND 6 (526677) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0098_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_EST 6 (526299) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LUBBCK_EST 6 (526299) 230 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus to LBB_EST TR11 (526294) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0099_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0100_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0101_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to NORTON 3 (524502) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0102_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to E_CLOVIS 3 (524773) 115 kV Bus CKT 1 b. 2. Trip branch from E_CLOVIS 3 (524773) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 3. Drop Load 1 at E_CLOVIS 3 (524773) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0103_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to N_CLOVIS_TP3 (524776) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0104_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to FE-HOLLAND 3 (524831) 115 kV Bus CKT 1 b. 2. Trip branch from FE-HOLLAND 3 (524831) 115 kV Bus to FE-CLOVIS2+3 (524838) 115 kV Bus CKT 1 b. 3. Trip branch from FE-CLOVIS2+3 (524838) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 4. Drop Load 1 at FE-HOLLAND 3 (524831) 115 kV Bus b. 5. Drop Load 1 at FE-CLOVIS2+3 (524838) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0105_P1 | 3 phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply Fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6 (524885) 230 kV Bus to CHAVES_CNTY6 (527483) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0106_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0107_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PERIMETER 3 (524797) 115 kV Bus CKT 1 b. 2. Trip branch from PERIMETER 3 (524797) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PERIMETER 3 (524797) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0108_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to FE-CHZPLT 3 (524863) 115 kV Bus CKT 1 b. 2. Trip branch from FE-CHZPLT 3 (524863) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FE-CHZPLT 3 (524863) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0109_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0110_P1 | 3 phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply Fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORRIS_TP 3 (524764) 115 kV Bus to NORRIS 3 (524801) 115 kV Bus CKT 1 b. 2. Drop Load 1 at NORRIS 3 (524801) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0111_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR1 1 (524819) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0112_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR2 1 (524820) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0113_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0114_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR11 (524921) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0115_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR21 (524922) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0116_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_WST 3 (524622) 115 kV Bus to DEFSMTH_TR11 (524620) 13.2 kV Bus CKT 1 b. 2. Trip branch from DFSMTH_WST 3 (524622) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0117_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0118_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR11 (526017) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0119_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR21 (526018) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0120_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to FE-CLVS_INT3 (524808) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0121_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to N_CLOVIS 3 (524777) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_CLOVIS 3 (524777) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0122_P1 | 3 phase fault on NORTON 3 (524502) 115 kV Bus a. Apply Fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTON 3 (524502) 115 kV Bus to FE-TUCMCARI3 (524509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0123_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY6 (527483) 230 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0124_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR1 1 (527478) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0125_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR2 1 (527479) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0126_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0127_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_TR 1 (527796) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at EDDY_TR 1 (527796) 13.2 kV Bus | P1 | Yes | Yes | Yes | No | No | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0128_P1 | 3 phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply Fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FE-CLVS_INT3 (524808) 115 kV Bus to W_CLOVIS 3 (524784) 115 kV Bus CKT 1 b. 2. Trip branch from W_CLOVIS 3 (524784) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at W_CLOVIS 3 (524784) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0129_P1 | 3 phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply Fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANNON_TP 3 (524790) 115 kV Bus to CANNONAFB 3 (524794) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANNONAFB 3 (524794) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0130_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0131_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0132_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to PRICE_TAP 3 (527509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0133_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to URTON 3 (527501) 115 kV Bus CKT 1 b. 2. Trip branch from URTON 3 (527501) 115 kV Bus to ROSWELL_CTY3 (527522) 115 kV Bus CKT 1 b. 3. Drop Load 1 at URTON 3 (527501) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0134_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to SAMSON 3 (527546) 115 kV Bus CKT 1 b. 2. Trip branch from SAMSON 3 (527546) 115 kV Bus to ROSWLL_INT 3 (527564) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SAMSON 3 (527546) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0135_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0136_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0137_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to LP-DOUD 3 (526176) 115 kV Bus CKT 1 b. 2. Drop Load 1 at LP-DOUD 3 (526176) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0138_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0139_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to YUMA_INT 3 (526475) 115 kV Bus CKT 1 b. 2. Trip branch from YUMA_INT 3 (526475) 115 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus CKT 1 b. 3. Drop Load 1 at YUMA_INT 3 (526475) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0140_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to SP-WOLFORTH3 (526483) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SP-WOLFORTH3 (526483) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0141_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to GEORGIA 3 (524322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0142_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to PALO_DURO 3 (524530) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0143_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to CANYON_E_TP3 (524522) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0144_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to SOUTHEAST 3 (524338) 115 kV Bus CKT 1 b. 2. Trip branch from SOUTHEAST 3 (524338) 115 kV Bus to PULLMAN 3 (524331) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SOUTHEAST 3 (524338) 115 kV Bus b. 4. Drop Load 1 at PULLMAN 3 (524331) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0145_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to MANHATTAN 3 (524224) 115 kV Bus CKT 1 b. 2. Trip branch from MANHATTAN 3 (524224) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MANHATTAN 3 (524224) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0146_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR1 1 (524361) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0147_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR2 1 (524360) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0148_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to WESTERN 3 (524325) 115 kV Bus CKT 1 b. 2. Trip branch from WESTERN 3 (524325) 115 kV Bus to 34TH_ST_TP 3 (524281) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WESTERN 3 (524325) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0149_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GEORGIA 3 (524322) 115 kV Bus to GEORGIA 2 (524321) 69 kV Bus to GEORGIA_TR11 (524320) 13.2 kV Bus CKT 1 b. 2. Trip branch from GEORGIA 2 (524321) 69 kV Bus to LAWRENPRK1 2 (524209) 69 kV Bus CKT 1 b. 3. Trip branch from LAWRENPRK1 2 (524209) 69 kV Bus to LAWRENPRK2 2 (524216) 69 kV Bus CKT @1 b. 4. Trip branch from LAWRENPRK2 2 (524216) 69 kV Bus to SONCY 2 (524200) 69 kV Bus CKT 1 b. 5. Trip branch from SONCY 2 (524200) 69 kV Bus to SONCY_TP 2 (524251) 69 kV Bus CKT 1 b. 6. Drop Load 1 at LAWRENPRK1 2 (524209) 69 kV Bus b. 7. Drop Load 1 at LAWRENPRK2 2 (524216) 69 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0150_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to CRSE_HINDTP3 (524387) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0151_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to HUNSLEY 3 (524520) 115 kV Bus CKT 1 b. 2. Trip branch from HUNSLEY 3 (524520) 115 kV Bus to CANYON_WEST3 (524516) 115 kV Bus CKT 1 b. 3. Trip branch from CANYON_WEST3 (524516) 115 kV Bus to DAWN 3 (524590) 115 kV Bus CKT 1 b. 4. Trip branch from DAWN 3 (524590) 115 kV Bus to PANDAHFD 3 (524597) 115 kV Bus CKT 1 b. 5. Trip branch from PANDAHFD 3 (524597) 115 kV Bus to DS-#25+ 3 (524575) 115 kV Bus CKT 1 b. 6. Trip branch from DS-#25+ 3 (524575) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 7. Drop Load 1 at HUNSLEY 3 (524520) 115 kV Bus b. 8. Drop Load 1 at CANYON_WEST3 (524516) 115 kV Bus b. 9. Drop Load 1 at DAWN 3 (524590) 115 kV Bus b. 10. Drop Load 1 at PANDAHFD 3 (524597) 115 kV Bus b. 11. Drop Load 1 at DS-#25+ 3 (524575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0152_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to CANYON_EAST3 (524523) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANYON_EAST3 (524523) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0153_P1 | 3 phase fault on PALO_DURO 3 (524530) 115 kV Bus a. Apply Fault at the PALO_DURO 3 (524530) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PALO_DURO 3 (524530) 115 kV Bus to HAPPY_INT 3 (525154) 115 kV Bus CKT 1 b. 2. Drop Load 1 at PALO_DURO 3 (524530) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0154_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to CROUSE_HIND3 (524388) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CROUSE_HIND3 (524388) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0155_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to FARMERS 3 (524377) 115 kV Bus CKT 1 b. 2. Trip branch from FARMERS 3 (524377) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FARMERS 3 (524377) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0156_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to 34TH_ST 3 (524282) 115 kV Bus CKT 1 b. 2. Drop Load 1 at 34TH_ST 3 (524282) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0157_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0158_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to ESTACADO_TP3 (524425) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0159_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COULTER 3 (524306) 115 kV Bus to COULTER 2 (524305) 69 kV Bus to COLTER_TR1 1 (524304) 13.2 kV Bus CKT 1 b. 2. Trip branch from COULTER 2 (524305) 69 kV Bus to WATERFL_TP 2 (524234) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0160_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to PUCKETT 3 (524256) 115 kV Bus CKT 1 b. 2. Trip branch from PUCKETT 3 (524256) 115 kV Bus to SONCY_TP 3 (524252) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PUCKETT 3 (524256) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0161_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to ESTACADO 3 (524432) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ESTACADO 3 (524432) 115 kV Bus b. 3. Drop Load 2 at ESTACADO 3 (524432) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0162_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to PRESTONWEST3 (524341) 115 kV Bus CKT 1 b. 2. Trip branch from PRESTONWEST3 (524341) 115 kV Bus to OWENSCORN 3 (524404) 115 kV Bus CKT 1 b. 3. Trip branch from OWENSCORN 3 (524404) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 4. Drop Load 1 at PRESTONWEST3 (524341) 115 kV Bus b. 5. Drop Load 1 at OWENSCORN 3 (524404) 115 kV Bus b. 6. Drop Shunt 1 at OWENSCORN 3 (524404) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0163_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to WHITAKER 3 (524058) 115 kV Bus CKT 1 b. 2. Trip branch from WHITAKER 3 (524058) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WHITAKER 3 (524058) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 524021 [NICHOLS_1 113.800], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0164_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0165_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0166_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR1 1 (524158) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0167_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR2 1 (524159) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0168_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus to EPLANT_TR3 1 (524160) 13.2 kV Bus CKT 1 b. 2. Trip branch from EAST_PLANT 6 (524163) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0169_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 3 (525154) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0170_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR1 1 (525151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0171_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR2 1 (525152) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0172_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to ARROWHEAD 3 (524397) 115 kV Bus CKT 1 b. 2. Trip branch from ARROWHEAD 3 (524397) 115 kV Bus to OSAGE 3 (524345) 115 kV Bus CKT 1 b. 3. Trip branch from OSAGE 3 (524345) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ARROWHEAD 3 (524397) 115 kV Bus b. 5. Drop Load 1 at OSAGE 3 (524345) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0173_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to SPRING_DRW 3 (524544) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SPRING_DRW 3 (524544) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0174_P1 | 3 phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply Fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TULIA_TP 3 (525179) 115 kV Bus to MU-TULIA 3 (522800) 115 kV Bus CKT 1 b. 2. Drop Load 1 at MU-TULIA 3 (522800) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0175_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SONCY 3 (524254) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SONCY 3 (524254) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0176_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SUNSET 3 (524249) 115 kV Bus CKT 1 b. 2. Trip branch from SUNSET 3 (524249) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SUNSET 3 (524249) 115 kV Bus b. 4. Drop Load 2 at SUNSET 3 (524249) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0177_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#1 2 (524142) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#1 2 (524142) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0178_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#2 2 (524149) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#2 2 (524149) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0179_P1 | 3 phase fault on HAPPY_INT 2 (525153) 69 kV Bus a. Apply Fault at the HAPPY_INT 2 (525153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_CTYTP2 (525143) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0180_P1 | 3 phase fault on SONCY_TP 2 (524251) 69 kV Bus a. Apply Fault at the SONCY_TP 2 (524251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 2 (524251) 69 kV Bus to NRTHWST_TP 2 (524096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0181_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0182_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTHWEST 3 (524106) 115 kV Bus to BUSH 3 (524124) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BUSH 3 (524124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0183_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTHWEST 3 (524106) 115 kV Bus to NORTHWEST 2 (524105) 69 kV Bus to NRTHWST_TR11 (524102) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0184_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to YARNELL_TP 3 (524072) 115 kV Bus CKT 1 b. 2. Trip branch from YARNELL_TP 3 (524072) 115 kV Bus to CONWAY 3 (524079) 115 kV Bus CKT 1 b. 3. Trip branch from CONWAY 3 (524079) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 b. 4. Drop Load 1 at CONWAY 3 (524079) 115 kV Bus b. 5. Drop Load D1 at CONWAY 3 (524079) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0185_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to CHERRY 3 (524009) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CHERRY 3 (524009) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0186_P1 | 3 phase fault on PRINGLE 3 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PRINGLE 3 (523266) 115 kV Bus to Q_RYTON_TP 3 (523478) 115 kV Bus CKT 1 b. 2. Trip branch from Q_RYTON_TP 3 (523478) 115 kV Bus to BLKHAWK_E 3 (523346) 115 kV Bus CKT 1 b. 3. Drop Load 1 at Q_RYTON_TP 3 (523478) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0187_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Trip three winding transformer from SHAM 3WT (512107) 115 kV Bus to SHAM 2WT (512106) 69 kV Bus to SR1TERT (512109) 14.4 kV Bus CKT 1 b. 5. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 6. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 7. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0188_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to W_BORGER_TP3 (523516) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0189_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0190_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to CPCOKER 3 (523470) 115 kV Bus CKT 1 b. 2. Trip branch from CPCOKER 3 (523470) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT 1 b. 3. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus b. 4. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0191_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0192_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0193_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 525783 [LRNZ2.3_GEN10.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0194_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 525783 [LRNZ2.3_GEN10.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0195_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM_345 (526936) 345 kV Bus to YOAKUM 6 (526935) 230 kV Bus to YOAKUM_TR1 (526937) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584223 [G14-040-GEN10.6900], 763309 [G18-112-GEN10.6600], 584226 [G14-040-GEN20.6900], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0196_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0197_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763090 [G18-073-GEN10.6600], 763084 [G18-073-GEN20.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0198_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0199_P1 | 3 phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus to EDDY_CNTY 7 (527802) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0200_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV Bus to HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_TR3 1 (527895) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25S | Transfer | Group5_Fault_0201_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR2 1 (526932) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0202_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR1 1 (526931) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800], 528361 [MADDOX_1 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0203_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0204_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 763397 [G18-124-GEN10.6600], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0205_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to BRU_SUB 6 (527009) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0206_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to MUSTANG 6 (527149) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0207_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0208_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0209_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to CROSSROADS 7 (527656) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0210_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to N_LOVING 7 (528185) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0211_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to RDRUNNER 7 (528027) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0212_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KIOWA 7 (527965) 345 kV Bus to KIOWA 3 (527966) 115 kV Bus to KIOWA_TR1 1 (527964) 13.2 kV Bus CKT 1 b. 2. Trip branch from KIOWA 3 (527966) 115 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 763397 [G18-124-GEN10.6600], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0213_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to ANDREWS 6 (528604) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584565 [G15-014-GE230.6900], 584226 [G14-040-GEN20.6900], 584223 [G14-040-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0214_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584226 [G14-040-GEN20.6900], 584223 [G14-040-GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0215_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0216_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR2 1 (527889) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0217_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR1 1 (527890) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0218_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to XTO_MAHONEY6 (527011) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0219_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to OXYBRU 6 (527010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0220_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to PLAINS_INT 3 (526928) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0221_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to ARCO_TP 3 (527041) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0222_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0223_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN10.6600], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0224_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0225_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to STANTON_W 3 (526076) 115 kV Bus CKT 1 b. 2. Trip branch from STANTON_W 3 (526076) 115 kV Bus to INDIANA 3 (526146) 115 kV Bus CKT 1 b. 3. Trip branch from INDIANA 3 (526146) 115 kV Bus to SP-ERSKINE 3 (526109) 115 kV Bus CKT 1 b. 4. Trip branch from SP-ERSKINE 3 (526109) 115 kV Bus to CARLISLE 3 (526160) 115 kV Bus CKT 1 b. 5. Drop Load 1 at STANTON_W 3 (526076) 115 kV Bus b. 6. Drop Load 1 at INDIANA 3 (526146) 115 kV Bus b. 7. Drop Load 2 at INDIANA 3 (526146) 115 kV Bus b. 8. Drop Load 1 at SP-ERSKINE 3 (526109) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0226_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to FLOYD_CNTY 3 (525780) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0227_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR5 1 (525822) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0228_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR6 1 (525823) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0229_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT2 2 (525816) 69 kV Bus to TUCO_TR7 1 (525814) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0230_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0231_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 584564 [G15-014-GE200.6900], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0232_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 525783 [LRNZ2.3_GEN10.6900], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0233_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RDRUNNER 7 (528027) 345 kV Bus to RDRUNNER 3 (528025) 115 kV Bus to RDRNNER_TR11 (528023) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527884 [CUNINGHAM4 113.800], 763309 [G18-112-GEN10.6600], 527883 [CUNINGHAM3 113.800], 523812 [LANOGSU10.600.6000], 525783 [LRNZ2.3_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0234_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV Bus to PHANTOM 7 (528015) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | Yes | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0235_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from N_LOVING 7 (528185) 345 kV Bus to NORTH_LOVNG3 (528182) 115 kV Bus to N_LOVING TR1 (528186) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 525783 [LRNZ2.3_GEN10.6900], 527884 [CUNINGHAM4 113.800], 527883 [CUNINGHAM3 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0236_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV Bus to CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 527884 [CUNINGHAM4 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0237_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to INTREPDW_TP3 (527999) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0238_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus to POTASH_TR1 1 (527958) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0239_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR2 1 (527959) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0240_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR3 1 (527960) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0241_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0242_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0243_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to PECOS 6 (528179) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0244_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0245_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0246_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0247_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHILL3 (528230) 115 kV Bus CKT 1 b. 2. Trip branch from AGAVE_RHILL3 (528230) 115 kV Bus to OCHOA 3 (528232) 115 kV Bus CKT 1 b. 3. Drop Load 1 at AGAVE_RHILL3 (528230) 115 kV Bus b. 4. Drop Load 1 at OCHOA 3 (528232) 115 kV Bus b. 5. Drop Load 1* at OCHOA 3 (528232) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0248_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHIL23 (528231) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AGAVE_RHIL23 (528231) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 527883 [CUNINGHAM3 113.800], 584223 [G14-040-GEN10.6900], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0249_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to RR_SVC_HV 3 (528024) 115 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0250_P1 | 3 phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply Fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTH_LOVNG3 (528182) 115 kV Bus to BLACKRIVER 3 (528193) 115 kV Bus CKT 1 b. 2. Trip branch from BLACKRIVER 3 (528193) 115 kV Bus to SENDERO +3 (528184) 115 kV Bus CKT 1 b. 3. Trip branch from SENDERO +3 (528184) 115 kV Bus to BLCKRVR_DST3 (528206) 115 kV Bus CKT 1 b. 4. Trip branch from BLCKRVR_DST3 (528206) 115 kV Bus to CHINA_DRAW 3 (528222) 115 kV Bus CKT 1 b. 5. Drop Load 1 at NORTH_LOVNG3 (528182) 115 kV Bus b. 6. Drop Load 1 at BLACKRIVER 3 (528193) 115 kV Bus b. 7. Drop Load 1 at SENDERO +3 (528184) 115 kV Bus b. 8. Drop Load 2 at SENDERO +3 (528184) 115 kV Bus b. 9. Drop Load 1 at BLCKRVR_DST3 (528206) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584564 [G15-014-GE200.6900], 525783 [LRNZ2.3_GEN10.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0251_P1 | 3 phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply Fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANDREWS 3 (528602) 115 kV Bus to NA_ENRICH 3 (528603) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0252_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to ALLRED_SUB 3 (527024) 115 kV Bus CKT 1 b. 2. Trip branch from ALLRED_SUB 3 (527024) 115 kV Bus to APACHE_ROB 3 (527022) 115 kV Bus CKT 1 b. 3. Trip branch from APACHE_ROB 3 (527022) 115 kV Bus to CORTEZ 3 (527021) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ALLRED_SUB 3 (527024) 115 kV Bus b. 5. Drop Load 1 at APACHE_ROB 3 (527022) 115 kV Bus b. 6. Drop Load 1 at CORTEZ 3 (527021) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0253_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to XTO_CORNEL+3 (527033) 115 kV Bus CKT 1 b. 2. Trip branch from XTO_CORNEL+3 (527033) 115 kV Bus to SHELLC3_TP 3 (527068) 115 kV Bus CKT 1 b. 3. Drop Load 1 at XTO_CORNEL+3 (527033) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0254_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0255_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to DRINKARD 3 (528589) 115 kV Bus CKT 1 b. 2. Trip branch from DRINKARD 3 (528589) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at DRINKARD 3 (528589) 115 kV Bus b. 6. Drop Load 1* at DRINKARD 3 (528589) 115 kV Bus b. 7. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 8. Drop Shunt 1 at DRINKARD 3 (528589) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0256_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to TARGA 3 (528605) 115 kV Bus CKT 1 b. 2. Trip branch from TARGA 3 (528605) 115 kV Bus to CARDINAL 3 (528596) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at TARGA 3 (528605) 115 kV Bus b. 6. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0257_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELL_C2 3 (527036) 115 kV Bus CKT 1 b. 2. Trip branch from SHELL_C2 3 (527036) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SHELL_C2 3 (527036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0258_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELLC3 3 (527074) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SHELLC3 3 (527074) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0259_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0260_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to ANTELOPE_1 6 (525840) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0261_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0262_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0263_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0264_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 6 (526161) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0265_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0266_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0267_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0268_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0269_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 b. 2. Trip branch from BENSING 3 (528433) 115 kV Bus to HIGG 3 (527363) 115 kV Bus CKT 1 b. 3. Drop Load 1 at BENSING 3 (528433) 115 kV Bus b. 4. Drop Load 1* at BENSING 3 (528433) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0270_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MILLEN_TPW 3 (528434) 115 kV Bus CKT 1 b. 2. Trip branch from MILLEN_TPW 3 (528434) 115 kV Bus to MILLEN 3 (528435) 115 kV Bus CKT *1 b. 3. Trip branch from MILLEN 3 (528435) 115 kV Bus to MILLEN_TPE 3 (528436) 115 kV Bus CKT *1 b. 4. Trip branch from MILLEN_TPE 3 (528436) 115 kV Bus to NE_HOBBS 3 (528442) 115 kV Bus CKT 1 b. 5. Trip branch from NE_HOBBS 3 (528442) 115 kV Bus to TAYLOR 3 (528413) 115 kV Bus CKT 1 b. 6. Drop Load 1 at MILLEN 3 (528435) 115 kV Bus b. 7. Drop Load 1* at MILLEN 3 (528435) 115 kV Bus b. 8. Drop Load 1 at NE_HOBBS 3 (528442) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 762226 [G17-151GEN3 0.6900], 524287 [GS-PHWD_GEN10.6900], 762223 [G17-151GEN2 0.6900], 762220 [G17-151GEN1 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0271_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to LE-WEST_SUB3 (528333) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0272_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0273_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0274_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to BUCKEYE_TP 3 (528348) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0275_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0276_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to QUAHADA 3 (528394) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 762441 [G18-004-GEN10.6300], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0277_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MONUMNT_TP 3 (528568) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762441 [G18-004-GEN10.6300], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0278_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CUNNINHAM 3 (527864) 115 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNHM_TR1 1 (527863) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0279_P1 | 3 phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply Fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WEST_SUB3 (528333) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0280_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to MONUMENT 3 (528491) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0281_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 unit. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 762441 [G18-004-GEN10.6300], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0282_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to PEARLE 3 (528392) 115 kV Bus CKT 1 b. 2. Trip branch from PEARLE 3 (528392) 115 kV Bus to ENRON_TP 3 (528317) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PEARLE 3 (528392) 115 kV Bus b. 4. Drop Load 1* at PEARLE 3 (528392) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 762441 [G18-004-GEN10.6300], 523812 [LANOGSU10.600.6000], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0283_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to HIGGEAST 3 (527286) 115 kV Bus CKT 1 b. 2. Trip branch from HIGGEAST 3 (527286) 115 kV Bus to DENVER_N 3 (527130) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0284_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0285_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to RUSSELL 3 (527284) 115 kV Bus CKT 1 b. 2. Drop Load 1 at RUSSELL 3 (527284) 115 kV Bus b. 3. Drop Load 2 at RUSSELL 3 (527284) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0286_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0287_P1 | 3 phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply Fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0288_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0289_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0290_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0291_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to W_BENDER 3 (528449) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0292_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to E_SANGER 3 (528470) 115 kV Bus CKT 1 b. 2. Trip branch from E_SANGER 3 (528470) 115 kV Bus to S_HOBBS 3 (528477) 115 kV Bus CKT 1 b. 3. Trip branch from S_HOBBS 3 (528477) 115 kV Bus to OXY_S_HOBBS3 (528480) 115 kV Bus CKT 1 b. 4. Trip branch from OXY_S_HOBBS3 (528480) 115 kV Bus to SW_4J44 3 (528484) 115 kV Bus CKT 1 b. 5. Trip branch from SW_4J44 3 (528484) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 b. 6. Drop Load 1 at E_SANGER 3 (528470) 115 kV Bus b. 7. Drop Load 1 at S_HOBBS 3 (528477) 115 kV Bus b. 8. Drop Load 2 at S_HOBBS 3 (528477) 115 kV Bus b. 9. Drop Load 1 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 10. Drop Load 2 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 11. Drop Load 3 at OXY_S_HOBBS3 (528480) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0293_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0294_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0295_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to OXY_NHU_RCF3 (528574) 115 kV Bus CKT 1 b. 2. Trip branch from OXY_NHU_RCF3 (528574) 115 kV Bus to OXYPERMIAN 3 (528575) 115 kV Bus CKT 1 b. 3. Trip branch from OXYPERMIAN 3 (528575) 115 kV Bus to SANGER_SW 3 (528463) 115 kV Bus CKT 1 b. 4. Drop Load 1 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 5. Drop Load 2 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 6. Drop Load 2 at OXYPERMIAN 3 (528575) 115 kV Bus b. 7. Drop Load 1 at OXYPERMIAN 3 (528575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0296_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to N_HOBBS 3 (528456) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_HOBBS 3 (528456) 115 kV Bus b. 3. Drop Load 2 at N_HOBBS 3 (528456) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0297_P1 | 3 phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply Fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SANGER_SW 3 (528463) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0298_P1 | 3 phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply Fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMENT 3 (528491) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0299_P1 | 3 phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply Fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_HOBBS 3 (528498) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0300_P1 | 3 phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply Fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRINKARD_TP3 (528533) 115 kV Bus to EUNICE 3 (528512) 115 kV Bus CKT 1 b. 2. Drop Load 1 at EUNICE 3 (528512) 115 kV Bus b. 3. Drop Load 1* at EUNICE 3 (528512) 115 kV Bus b. 4. Drop Shunt 1 at EUNICE 3 (528512) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0301_P1 | 3 phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply Fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMNT_TP 3 (528568) 115 kV Bus to BYRD_TP 3 (528581) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0302_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to OXY_WSEM_TP3 (527325) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0303_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to LE-ERF 3 (528775) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0304_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to MAPCO 3 (527360) 115 kV Bus CKT 1 b. 2. Trip branch from MAPCO 3 (527360) 115 kV Bus to AM_FRAC 3 (527300) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MAPCO 3 (527360) 115 kV Bus b. 4. Drop Load 1 at AM_FRAC 3 (527300) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0305_P1 | 3 phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply Fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INK_BASIN 3 (527027) 115 kV Bus to ALRDCRTZ_TP3 (527030) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0306_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-WAITS 2 (528617) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0307_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-DSYSRPOI2 (528677) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0308_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-TATMGOAB2 (528679) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0309_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0310_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to MUSTANG 3 (527146) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0311_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DENVER_N 3 (527130) 115 kV Bus to DENVER_CTY 2 (527125) 69 kV Bus to DNVER_N_TR11 (527122) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0312_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to BYRD 3 (528582) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BYRD 3 (528582) 115 kV Bus b. 3. Drop Load 1* at BYRD 3 (528582) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0313_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to COOPER_RNCH3 (528554) 115 kV Bus CKT 1 b. 2. Trip branch from COOPER_RNCH3 (528554) 115 kV Bus to OIL_CENTER 3 (528552) 115 kV Bus CKT 1 b. 3. Trip branch from OIL_CENTER 3 (528552) 115 kV Bus to LEA_ROAD 3 (528505) 115 kV Bus CKT 1 b. 4. Drop Load 1 at COOPER_RNCH3 (528554) 115 kV Bus b. 5. Drop Load 1 at OIL_CENTER 3 (528552) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0314_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to OXY_WSTSEM 3 (527323) 115 kV Bus CKT 1 b. 2. Drop Load 1 at OXY_WSTSEM 3 (527323) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0315_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to GAINES 3 (527322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0316_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-ERF 3 (528775) 115 kV Bus to LE-TALLCOTN3 (528779) 115 kV Bus CKT 1 b. 2. Trip branch from LE-TALLCOTN3 (528779) 115 kV Bus to LE-KCM 3 (527292) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LE-TALLCOTN3 (528779) 115 kV Bus b. 4. Drop Load 1 at LE-KCM 3 (527292) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0317_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LE-ERF 3 (528775) 115 kV Bus to LE-ERF 2 (528774) 69 kV Bus to LE-ERF_TR 1 (528773) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0318_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to PCA 3 (527930) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523936 [PANTEX_WIND10.6900], 524287 [GS-PHWD_GEN10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0319_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to TEAGUE 3 (528526) 115 kV Bus CKT 1 b. 2. Trip branch from TEAGUE 3 (528526) 115 kV Bus to S_JAL 3 (528547) 115 kV Bus CKT 1 b. 3. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus b. 4. Drop Load 1* at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0320_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to SAGE_BRUSH 3 (527955) 115 kV Bus CKT 1 b. 2. Trip branch from SAGE_BRUSH 3 (527955) 115 kV Bus to MEDANOS 3 (527954) 115 kV Bus CKT 1 b. 3. Trip branch from MEDANOS 3 (527954) 115 kV Bus to LIVSTNRIDGE3 (527953) 115 kV Bus CKT 1 b. 4. Drop Load 1 at SAGE_BRUSH 3 (527955) 115 kV Bus b. 5. Drop Load 1* at SAGE_BRUSH 3 (527955) 115 kV Bus b. 6. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0321_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to SEMINOLE 3 (527275) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0322_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to LEGACY 3 (527346) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0323_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR1 1 (527319) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0324_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR2 1 (527320) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0325_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV Bus to SAN_ANDS_TP3 (527105) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0326_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR21 (527274) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0327_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR11 (527273) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0328_P1 | 3 phase fault on GAINES 2 (527321) 69 kV Bus a. Apply Fault at the GAINES 2 (527321) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 2 (527321) 69 kV Bus to RILEY_TP 2 (527228) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0329_P1 | 3 phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply Fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAN_ANDS_TP3 (527105) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0330_P1 | 3 phase fault on RILEY_TP 2 (527228) 69 kV Bus a. Apply Fault at the RILEY_TP 2 (527228) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RILEY_TP 2 (527228) 69 kV Bus to RILEY 2 (527331) 69 kV Bus CKT 1 b. 2. Drop Load 1 at RILEY 2 (527331) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0331_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0332_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0333_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0334_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 589383 [G17-100-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0335_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0336_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 3. Trip branch from CROSSROADS 7 (527656) 345 kV to RSVLT_CC_E 7 (527655) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0337_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0338_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0339_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to BVRCNTY7 (515554) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 560584 [G06-44-2 4.1600]
05 - Southwest | 25S | Transfer | Group5_Fault_0340_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0341_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523122 [NBLWND-WTG110.7000]
05 - Southwest | 25S | Transfer | Group5_Fault_0342_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 524021 [NICHOLS_1 113.800], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0343_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0344_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus POTTER_CO 7 (523961) 345 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523942 [MAJSTC-WTG210.6900], 523941 [MAJSTC-WTG110.6900], 524021 [NICHOLS_1 113.800]
05 - Southwest | 25S | Transfer | Group5_Fault_0345_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0346_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to CRAWFISH_DR (560022) 345 kV CKT | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0347_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0348_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0349_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 524021 [NICHOLS_1 113.800], 524023 [NICHOLS_3 122.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0350_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0351_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0352_P4 | a. Apply single phase fault at CHINA_DRAW 7 (528223) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from CHINA_DRAW 7 (528223) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 4. Disconnect Bus CHINA_DRAW 7 (528223) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0353_P4 | a. Apply single phase fault at RDRUNNER 7 (528027) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from RDRUNNER 7 (528027) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7 (528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0354_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR21 (528012) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0355_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to RDRUNNER 7 (528027) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR11 (528011) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0356_P4 | a. Apply single phase fault at SUNDOWN 6 (526435) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV to AMOCO_SS 6 (526460) kV CKT 1 b. 2. Disconnect Bus AMOCO_SS 6 (526460) 230 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0357_P4 | a. Apply single phase fault at BORDER 7 (515458) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BORDER 7 (515458) 345 kV to CRAWFISH_DR (560022) 345 kV CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV to WWDBORDT (755000) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523941 [MAJSTC-WTG110.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0358_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 1 b. 3. Trip three winding transformer from WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 4. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0359_P4 | a. Apply single phase fault at SWEETWT6 (511541) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SWEETWT6 (511541) 230 kV to CHISHOLM6 (511557) 230 kV CKT 1 b. 2. Trip branch from SWEETWT6 (511541) 230 kV to STLN-DEMARC6 (523779) 230 kV CKT 1 b. 3. Trip branch from STLN-DEMARC6 (523779) 230 kV to WHEELER 6 (523777) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 511968 [ROARK0 0.6900], 511968 [ROARK0 0.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0360_P4 | a. Apply single phase fault at TUCO_INT 6 (525830) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 3 (525828) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 7 (525832) kV to TUCO_TR2 1 (525825) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0361_P4 | a. Apply single phase fault at PLANT_X 6 (525481) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV to SUNDOWN 6 (526435) 230 kV CKT 1 b. 2. Trip branch from PLANT_X 6 (525481) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0362_P4 | a. Apply single phase fault at NEWHART 6 (525461) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEWHART 6 (525461) 230 kV to POTTER_CO 6 (523959) 230 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR11 (525459) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0363_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 6 (525531) 230 kV to ROOSEVELT 6 (524909) 230 kV CKT 1 b. 2. Trip three winding transformer from TOLK 7 (525549) 345 kV to TOLK 6 (525531) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0364_P4 | a. Apply single phase fault at PLANT_X 3 (525480) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV to MULSHVLY_TP3 (525019) 115 kV CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV to MULESHVALLY3 (525018) 115 kV CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV to BAILEYCO 3 (525028) 115 kV CKT 1 b. 4. Drop Load 1 MULESHVALLY3 (525018) 115 kV b. 5. Drop Load 2 MULESHVALLY3 (525018) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0365_P4 | a. Apply single phase fault at ROOSEVELT 6 (524909) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV to OASIS 6 (524875) 230 kV CKT 1 b. 2. Trip branch from ROOSEVELT 6 (524909) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0366_P4 | a. Apply single phase fault at LAMB_CNTY 3 (525636) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV to HOCKLEY 3 (526020) 115 kV CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV to LAMB_CNTY 3 (525636) kV to LAMB_TR3 1 (525633) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0367_P4 | a. Apply single phase fault at CASTRO_CNTY3 (524746) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV to CASTRO_CNTY2 (524745) kV to CASTRO_TR1 1 (524744) 13.2 kV CKT1 b. 2. Trip branch from CASTRO_CNTY3 (524746) 115 kV to DS-#21 3 (524734) 115 kV CKT 1 b. 3. Trip branch from DS-#21 3 (524734) 115 kV to TIERABLANCA3 (524630) 115 kV CKT 1 b. 4. Drop Load 1 DS-#21 3 (524734) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0368_P4 | a. Apply single phase fault at TUCO_INT 3 (525828) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 6 (525830) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 3 (525828) 115 kV to FLOYD_CNTY 3 (525780) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0369_P4 | a. Apply single phase fault at KRESS_INT 3 (525192) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV to KRS_RURL_TP3 (525226) 115 kV CKT 1 b. 2. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV to KRESS_INT 2 (525191) kV to KRESS_TR1 1 (525190) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0370_P4 | a. Apply single phase fault at LUBBCK_STH 6 (526269) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 b. 2. Trip branch from JONES 6 (526337) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0371_P4 | a. Apply single phase fault at YOAKUM 6 (526935) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM 3 (526934) 115 kV to PLAINS_INT 3 (526928) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0372_P4 | a. Apply single phase fault at TERRY_CNTY 3 (526736) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TERRY_CNTY 3 (526736) 115 kV to WOLFFORTH 3 (526524) 115 kV CKT 1 b. 2. Trip three winding transformer from TERRY_CNTY 3 (526736) 115 kV to TERRY_CNTY 2 (526735) kV to TERRY_TR1 1 (526733) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0373_P4 | a. Apply single phase fault at TIERABLANCA3 (524630) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TIERABLANCA3 (524630) 115 kV to DFSMTH_EST 3 (524619) 115 kV CKT 1 b. 2. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV to DFSMTH_EST 3 (524619) kV to DEFSMTH_TR21 (524621) 13.8 kV CKT2 b. 3. Trip branch from TIERABLANCA3 (524630) 115 kV to NE_HEREFORD3 (524567) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0374_P4 | a. Apply single phase fault at ROLLHILLS 3 (524007) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV to NORTHWEST 3 (524106) 115 kV CKT 1 b. 2. Drop Shunt 1 ROLLHILLS 3 (524007) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0375_P4 | a. Apply single phase fault at AMA_SOUTH 3 (524414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from AMA_SOUTH 3 (524414) 115 kV to AMA_SOUTH 6 (524415) kV to AMA_SO_TR1 1 (524410) 13.2 kV CKT1 b. 2. Trip branch from AMA_SOUTH 3 (524414) 115 kV to OWENSCORN 3 (524404) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0376_P4 | a. Apply single phase fault at HITCHLAND 6 (523095) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV to HITCHLAND 7 (523097) kV to HITCHLD_TR21 (523094) 13.2 kV CKT2 b. 2. Trip branch from HITCHLAND 6 (523095) 230 kV to MOORE_CNTY 6 (523309) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0377_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV to SHERID4 (511474) 138 kV CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 3. Trip branch from 53CACHE4 (511509) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 4. Trip branch from ARTVLTP4 (511537) 138 kV to ARTVILL4 (511538) 138 kV CKT 1 b. 5. Trip branch from LWS-NTP4 (511471) 138 kV to 53CACHE4 (511509) 138 kV CKT 1 b. 6. Trip branch from LWS N4 (511430) 138 kV to LWS-NTP4 (511471) 138 kV CKT 1 b. 7. Drop Load 1 SHERID4 (511474) 138 kV b. 8. Drop Load 1 ARTVILL4 (511538) 138 kV b. 9. Drop Load 1 53CACHE4 (511509) 138 kV b. 10. Drop Load 1 LWS N4 (511430) 138 kV b. 11. Drop Shunt 1 ARTVILL4 (511538) 138 kV b. 12. Drop Shunt 1 LWS N4 (511430) 138 kV b. 13. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 14. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0378_P4 | a. Apply single phase fault at PLSNT_HILL 3 (524768) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV to PLSNT_HILL 3 (524768) kV to PLSNHIL_TR11 (524767) 13.2 kV CKT1 b. 2. Trip branch from PLSNT_HILL 3 (524768) 115 kV to N_CLOVIS_TP3 (524776) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0379_P4 | a. Apply single phase fault at CURRY 3 (524822) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CURRY 3 (524822) 115 kV to ROOSEVELT 3 (524908) 115 kV CKT 2 b. 2. Trip branch from CURRY 3 (524822) 115 kV to NORRIS_TP 3 (524764) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0380_P4 | a. Apply single phase fault at PORTALES 3 (524924) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 b. 2. Trip branch from OASIS 3 (524874) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0381_P4 | a. Apply single phase fault at NEWHART 3 (525460) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV to NEWHART 3 (525460) 115 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR21 (525458) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0382_P4 | a. Apply single phase fault at YOAKUM 3 (526934) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLAINS_INT 3 (526928) 115 kV to YOAKUM 3 (526934) 115 kV CKT 1 b. 2. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0383_P4 | a. Apply single phase fault at LAMB_CNTY 2 (525635) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from W_LITTLFLD 2 (525613) 69 kV to LAMB_CNTY 2 (525635) 69 kV CKT 1 b. 2. Trip branch from AMHERST 2 (525606) 69 kV to W_LITTLFLD 2 (525613) 69 kV CKT 1 b. 3. Trip branch from LC-SANDHLL+2 (525599) 69 kV to AMHERST 2 (525606) 69 kV CKT 1 b. 4. Trip branch from SUDANRURAL 2 (525592) 69 kV to LC-SANDHLL+2 (525599) 69 kV CKT 1 b. 5. Drop Load 1 W_LITTLFLD 2 (525613) 69 kV b. 6. Drop Load 1 AMHERST 2 (525606) 69 kV b. 7. Drop Load 1 LC-SANDHLL+2 (525599) 69 kV b. 8. Drop Load 2 LC-SANDHLL+2 (525599) 69 kV b. 9. Drop Load 1 SUDANRURAL 2 (525592) 69 kV b. 10. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV to LAMB_CNTY 2 (525635) kV to LAMB_TR1 1 (525631) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0384_P4 | a. Apply single phase fault at CARLISLE 3 (526160) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV to CARLISLE 3 (526160) kV to CRLSLE_TR1 1 (526157) 13.2 kV CKT1 b. 2. Trip branch from CARLISLE 3 (526160) 115 kV to MURPHY 3 (526192) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0385_P4 | a. Apply single phase fault at FLOYD_CNTY 3 (525780) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLOYD_CNTY 3 (525780) 115 kV to TUCO_INT 3 (525828) 115 kV CKT 1 b. 2. Trip three winding transformer from FLOYD_CNTY 3 (525780) 115 kV to FLOYD_CNTY 2 (525779) kV to FLOYD_TR1 1 (525777) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0386_P4 | a. Apply single phase fault at TUCO_INT 2 (525826) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 2 (525826) kV to TUCO_TR6 1 (525823) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 2 (525826) 69 kV to SP-NEWDEAL 2 (525885) 69 kV CKT 1 b. 3. Trip branch from SP-NEWDEAL 2 (525885) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 4. Trip branch from WHITEHEAD 2 (525891) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 5. Trip branch from WHITEHEAD 2 (525891) 69 kV to SP-SHALLWTR2 (525899) 69 kV CKT 1 b. 6. Trip branch from SP-SHALLWTR2 (525899) 69 kV to STANTON_N 2 (526073) 69 kV CKT 1 b. 7. Drop Load 1 SP-NEWDEAL 2 (525885) 69 kV b. 8. Drop Load 1 MONROE 2 (525892) 69 kV b. 9. Drop Load 1 WHITEHEAD 2 (525891) 69 kV b. 10. Drop Load SP-SHALLWTR2 (525899) 69 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0387_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 2. Trip branch from POTTER_CO 7 (523961) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 b. 3. Trip branch from CHISHOLM7 (511553) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0388_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0389_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV to TUCO_INT 6 (525830) kV to TUCO_TR1 1 (525824) 13.2 kV CKT1 b. 3. Drop Shunt 1 TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0390_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0391_P4 | a. Apply single phase fault at POTTER_CO 6 (523959) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV to HARRNG_EST 6 (523979) 230 kV CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV to ROLLHILLS 6 (524010) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0392_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0393_P4 | a. Apply single phase fault at HOBBS_INT 3 (527891) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from HOBBS_INT 3 (527891) 115 kV to MILLEN_TPW 3 (528434) 115 kV CKT 1 b. 3. Trip branch from MILLEN_TPW 3 (528434) 115 kV to MILLEN 3 (528435) 115 kV CKT *1 b. 4. Trip branch from MILLEN 3 (528435) 115 kV to MILLEN_TPE 3 (528436) 115 kV CKT *1 b. 5. Trip branch from MILLEN_TPE 3 (528436) 115 kV to NE_HOBBS 3 (528442) 115 kV CKT 1 b. 6. Trip branch from NE_HOBBS 3 (528442) 115 kV to TAYLOR 3 (528413) 115 kV CKT 1 b. 7. Drop Load 1 MILLEN 3 (528435) 115 kV b. 8. Drop Load 1* MILLEN 3 (528435) 115 kV b. 9. Drop Load 1 NE_HOBBS 3 (528442) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0394_P4 | a. Apply single phase fault at CUNNINHAM 3 (527864) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV to BUCKEYE_TP 3 (528348) 115 kV CKT 1 b. 2. Trip branch from CUNNINHAM 3 (527864) 115 kV to QUAHADA 3 (528394) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0395_P4 | a. Apply single phase fault at MADDOX 3 (528355) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from MADDOX 3 (528355) 115 kV to G18-004-TAP (762442) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0396_P4 | a. Apply single phase fault at JOHNSON_DRW3 (527362) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV to LE-ERF 3 (528775) 115 kV CKT @1 b. 2. Trip branch from JOHNSON_DRW3 (527362) 115 kV to HIGG 3 (527363) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0397_P4 | a. Apply single phase fault at LE-LOVINTON2 (528618) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-NRTH_INT3 (528334) 115 kV CKT 1 b. 2. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-DSYSRPOI2 (528677) 69 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0398_P4 | a. Apply single phase fault at DENVER_N 3 (527130) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV to MUSTANG 3 (527146) 115 kV CKT 1 b. 2. Trip branch from DENVER_N 3 (527130) 115 kV to HIGGEAST 3 (527286) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0399_P4 | a. Apply single phase fault at EDDY_NORTH 6 (527799) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV to CUNNIGHM_N 6 (527865) 230 kV CKT 1 b. 2. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV to EDDY_NORTH 6 (527799) kV to EDDY_TR 1 (527796) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0400_P4 | a. Apply single phase fault at POTASH_JCT 3 (527962) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV to KIOWA 3 (527966) 115 kV CKT 1 b. 2. Trip three winding transformer from KIOWA 7 (527965) 345 kV to KIOWA 3 (527966) kV to KIOWA_TR1 1 (527964) 13.2 kV CKT1 b. 3. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV to POTASH_JCT 3 (527962) kV to POTASH_TR1 1 (527958) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0401_P4 | a. Apply single phase fault at GAINES 3 (527322) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV to GAINES 3 (527322) 115 kV CKT 1 b. 2. Trip branch from GAINES 3 (527322) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 3. Trip branch from OXY_WSTSEM 3 (527323) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 4. Drop Load 1 OXY_WSTSEM 3 (527323) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0402_P4 | a. Apply single phase fault at HOBBS_INT 6 (527894) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV to HOBBS_INT 6 (527894) kV to HOBBS_TR3 1 (527895) 13.2 kV CKT1 b. 2. Trip branch from HOBBS_INT 6 (527894) 230 kV to ANDREWS 6 (528604) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0403_P4 | a. Apply single phase fault at RANDALL 3 (524364) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV to RANDALL 3 (524364) 115 kV CKT 1 b. 2. Trip three winding transformer from RANDALL 6 (524365) 230 kV to RANDALL 3 (524364) kV to RANDAL_TR1 1 (524361) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0404_P4 | a. Apply single phase fault at COULTER 3 (524306) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV to COULTER 3 (524306) 115 kV CKT 1 b. 2. Trip branch from COULTER 3 (524306) 115 kV to PUCKETT 3 (524256) 115 kV CKT 1 b. 3. Trip branch from PUCKETT 3 (524256) 115 kV to SONCY_TP 3 (524252) 115 kV CKT 1 b. 4. Drop Load 1 PUCKETT 3 (524256) 115 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0405_P4 | a. Apply single phase fault at EAST_PLANT 3 (524162) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV to EAST_PLANT 3 (524162) kV to EPLANT_TR3 1 (524160) 13.2 kV CKT1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV to EAST_PLANT 6 (524163) 230 kV CKT 1 b. 3. Trip branch from EAST_PLANT 3 (524162) 115 kV to PIERCE_TP 3 (524185) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0406_P4 | a. Apply single phase fault at NICHOLS 3 (524043) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV to NICHOLS 3 (524043) kV to NICHOLS_TR11 (524041) 13.2 kV CKT1 b. 2. Trip branch from NICHOLS 3 (524043) 115 kV to WHITAKER 3 (524058) 115 kV CKT 1 b. 3. Trip branch from WHITAKER 3 (524058) 115 kV to EAST_PLANT 3 (524162) 115 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 524287 [GS-PHWD_GEN10.6900], 524021 [NICHOLS_1 113.800], 524022 [NICHOLS_2 113.800], 523972 [HARRNGTON2 124.000]
05 - Southwest | 25S | Transfer | Group5_Fault_0407_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 589383 [G17-100-GEN10.5500]
05 - Southwest | 25S | Transfer | Group5_Fault_0408_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 523936 [PANTEX_WIND10.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0409_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0410_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0411_P4 | Apply single-phase fault at CROSSROADS 7 (527656) 345 kV Bus CB 6R45 Stuck b. Run for 21 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO TOLK 7 (525549) 345 kV Bus CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO SAGA_SCOL 7 (527610) 345 kV Bus CKT 1 b. 3. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 4. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 5. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 6. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 7. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 8. Disconnect Bus GRDXFR1 1 (527613) 0.5 kV b. 9. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 10. Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 11. Disconnect Bus GRDXFR2 1 (527616) 0.5 kV b. 12. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Clear fault at Bus CROSSROADS 7 (527656) 345 kV b. 15. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 17. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 18. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 19. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 20. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 21. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 22. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 23. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 24. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 25. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 26. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 27. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 28. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 29. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 30. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 31. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 32. Disconnect Bus SUB BUS #2 (527629) 34.5 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0412_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0413_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0414_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0415_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0416_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0417_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0418_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0419_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0420_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0421_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV b. 2. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0422_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB J23#### Stuck b. 1. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 2. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584226 [G14-040-GEN20.6900], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0423_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S120 Stuck b. 1. Run for 16 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0424_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 5 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Run for 11 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0425_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 16 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING (528185) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0426_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 523971 [HARRNGTON1 124.000], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0427_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J23#### Stuck b. 1. Run for 16 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 762463 [G18-015-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0428_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB #### Stuck b. 1. Run for 5 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Run for 11 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25S | Transfer | Group5_Fault_0429_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J22#### Stuck b. 1. Run for 16 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 5. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600], 584563 [G15-014-GE170.6900], 584564 [G15-014-GE200.6900], 584565 [G15-014-GE230.6900]
05 - Southwest | 25S | Transfer | Group5_Fault_0430_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0431_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0432_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0433_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0434_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0435_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0436_P4 | a. Apply single-phase fault at NICHOLS 6 (524044) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus NICHOLS_TR11 (524041) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus from NICHOLS_3 1 (524023) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0437_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0438_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0439_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0440_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0441_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0442_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0443_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 523941 [MAJSTC-WTG110.6900], 523942 [MAJSTC-WTG210.6900], 523942 [MAJSTC-WTG210.6900], 761358 [G17-239-GEN10.6900], 761361 [G17-239-GEN20.6900], 761799 [G17-187GEN1 0.6900], 761802 [G17-187GEN2 0.6900], 763084 [G18-073-GEN20.6600], 763090 [G18-073-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0444_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 2. Run for 11 cycles, Disconnect Bus BUSHLAND 6 (524267) 230 kV b. 3. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 4. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 5. Clear fault at BUSHLAND 6 (524267) 230 kV b. 6. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 7. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 8. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 9. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 10. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0445_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0446_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Clear fault and run for 11 cycles, Disconnect BusTUCO_TR3 1 (525819) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0447_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0448_P4 | a. Apply single-phase fault at HARRNG_WST 6 (523977) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO EAST_PLANT 6 (524163) 230 kV Bus CKT 1 b. 3. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 b. 4. Disconnect Bus HARRNG_WST 6 (523977) 230 kV b. 5. Disconnect Bus HARRNGTON1 1 (523971) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0449_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO RANDALL 6 (524365) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 3. Disconnect Bus HARRNG_MID 6 (523978) 230 kV b. 4. Disconnect Bus HARRNGTON2 1 (523972) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0450_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN10.6600], 763309 [G18-112-GEN10.6600]
05 - Southwest | 25S | Transfer | Group5_Fault_0451_P4 | a. Apply single-phase fault at JONES 6 (526337) 230 kV b. 1. Clear fault and run for 18 cycles, Disconnect Bus from JONES 6 (526337) 230 kV b. 2. Disconnect Bus from JONES_1 1 (526331) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Group5_Fault_0452_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from HARRNG_MID 6 (523978) 230 kV b. 2. Drop Generator 1 Bus 523972 b. 3. Drop Load S1 Bus 523972 b. 4. Disconnect Bus 523972 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25S | Transfer | Group5_Fault_0453_P4 | a. Apply single-phase fault at MOORE_E 3 (523308) 115 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from MOORE_E 3 (523308) 115 kV b. 2. Drop Generator 1 Bus 523297 b. 3. Drop Generator 3 Bus 523301 b. 4. Drop Load F1 Bus 523297 b. 5. Drop Load 1 Bus 523301 b. 6. Drop Load A3 Bus 523301 b. 7. Disconnect Bus 523294 b. 8. Disconnect Bus 523295 b. 9. Disconnect Bus 523296 b. 10. Disconnect Bus 523297 b. 11. Disconnect Bus 523301 b. 12. Disconnect Bus 523302 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25S | Transfer | Group5_Fault_0454_P4 | a. Apply single-phase fault at O.K.U.-7 (762467) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from G18-092 TAP (763215) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 b. 2. Trip branch from G17-151 (762216) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0001_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to PLANT_X 6 (525481) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0002_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0003_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0004_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0005_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV Bus to G17-146-TAP (760498) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0006_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR1 1 (525479) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0007_P1 | 3 phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply Fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLANT_X 6 (525481) 230 kV Bus to PLANT_X 3 (525480) 115 kV Bus to PLANTX_TR2 (525478) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0008_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to POTTER_CO 6 (523959) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0009_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 6 (525461) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0010_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR11 (525459) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0011_P1 | 3 phase fault on NEWHART 6 (525461) 230 kV Bus a. Apply Fault at the NEWHART 6 (525461) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NEWHART 6 (525461) 230 kV Bus to NEWHART 3 (525460) 115 kV Bus to NEWHART_TR21 (525458) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0012_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0013_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to NEEDMORE 6 (525586) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0014_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0015_P1 | 3 phase fault on TOLK 6 (525531) 230 kV Bus a. Apply Fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 6 (525531) 230 kV Bus to ROOSEVELT 6 (524909) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 763254 [G18-099-GEN10.6900], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0016_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0017_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0018_P1 | 3 phase fault on SUNDOWN 6 (526435) 230 kV Bus a. Apply Fault at the SUNDOWN 6 (526435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SUNDOWN 6 (526435) 230 kV Bus to SUNDOWN 3 (526434) 115 kV Bus to SUNDOWN_TR11 (526432) 13.8 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0019_P1 | 3 phase fault on G17-146-TAP (760498) 230 kV Bus a. Apply Fault at the G17-146-TAP (760498) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from G17-146-TAP (760498) 230 kV Bus to DEAFSMITH 6 (524623) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0020_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to MULSHVLY_TP3 (525019) 115 kV Bus CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to MULESHVALLY3 (525018) 115 kV Bus CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 b. 4. Drop Load 1 at MULESHVALLY3 (525018) 115 kV Bus b. 5. Drop Load 2 at MULESHVALLY3 (525018) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0021_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to RKYFORD_TP 3 (525446) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0022_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to LAMB_CNTY 3 (525636) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0023_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0024_P1 | 3 phase fault on PLANT_X 3 (525480) 115 kV Bus a. Apply Fault at the PLANT_X 3 (525480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV Bus to BC-EARTH 3 (525056) 115 kV Bus CKT 1 b. 2. Trip branch from BC-EARTH 3 (525056) 115 kV Bus to BC-KELLEY +3 (525050) 115 kV Bus CKT 1 b. 3. Trip branch from BC-KELLEY +3 (525050) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 b. 4. Drop Load 1 at BC-EARTH 3 (525056) 115 kV Bus b. 5. Drop Load 1 at BC-KELLEY +3 (525050) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0025_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0026_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SWISHER 6 (525213) 230 kV Bus to TUCO_INT 6 (525830) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0027_P1 | 3 phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply Fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SWISHER 6 (525213) 230 kV Bus to SWISHER 3 (525212) 115 kV Bus to SWISHER_TR11 (525211) 13.2 kV Bus CKT 1 b. 2. Trip branch from SWISHER 3 (525212) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0028_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to CASTRO_CNTY3 (524746) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0029_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to KRESS_INT 3 (525192) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0030_P1 | 3 phase fault on NEWHART 3 (525460) 115 kV Bus a. Apply Fault at the NEWHART 3 (525460) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEWHART 3 (525460) 115 kV Bus to HART_INDUST3 (525124) 115 kV Bus CKT 1 b. 2. Trip branch from HART_INDUST3 (525124) 115 kV Bus to LAMTON 3 (525414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HART_INDUST3 (525124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0031_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0032_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PNM-DC6 (599955) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0033_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROOSEVELT 6 (524909) 230 kV Bus to ROOSEVELT 3 (524908) 115 kV Bus to ROSEVLT_TR11 (524907) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0034_P1 | 3 phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply Fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV Bus to PLSNT_HILL 6 (524770) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0035_P1 | 3 phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply Fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NEEDMORE 6 (525586) 230 kV Bus to YOAKUM 6 (526935) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0036_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0037_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0038_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR4 1 (525821) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0039_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV Bus to TUCO_INT 3 (525828) 115 kV Bus to TUCO_TR3 1 (525819) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0040_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0041_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from WOLFFORTH 6 (526525) 230 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus to WOLFRTH_TR11 (526522) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0042_P1 | 3 phase fault on WOLFFORTH 6 (526525) 230 kV Bus a. Apply Fault at the WOLFFORTH 6 (526525) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0043_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to AMOCO_TP 3 (526445) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0044_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to LC-OPDYKE 3 (526036) 115 kV Bus CKT 1 b. 2. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LC-OPDYKE 3 (526036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0045_P1 | 3 phase fault on SUNDOWN 3 (526434) 115 kV Bus a. Apply Fault at the SUNDOWN 3 (526434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SUNDOWN 3 (526434) 115 kV Bus to PACIFIC 3 (526424) 115 kV Bus CKT 1 b. 2. Trip branch from PACIFIC 3 (526424) 115 kV Bus to COCHRAN 3 (526361) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PACIFIC 3 (526424) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0046_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DEAFSMITH 6 (524623) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0047_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_EST 3 (524619) 115 kV Bus to DEFSMTH_TR21 (524621) 13.8 kV Bus CKT 2 b. 2. Trip branch from DFSMTH_EST 3 (524619) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0048_P1 | 3 phase fault on LC-OPDYKE 3 (526036) 115 kV Bus a. Apply Fault at the LC-OPDYKE 3 (526036) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LC-OPDYKE 3 (526036) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0049_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to AMOCO_CRYO 3 (526452) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AMOCO_CRYO 3 (526452) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0050_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0051_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0052_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0053_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0054_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to MURPHY 3 (526192) 115 kV Bus CKT 1 b. 2. Trip branch from MURPHY 3 (526192) 115 kV Bus to QUINCY 3 (526195) 115 kV Bus CKT 1 b. 3. Trip branch from QUINCY 3 (526195) 115 kV Bus to SP-MILWAUKEE (526196) 115 kV Bus CKT 1 b. 4. Trip branch from SP-MILWAUKEE (526196) 115 kV Bus to SP-UPLAND (526198) 115 kV Bus CKT 1 b. 5. Drop Load 1 at MURPHY 3 (526192) 115 kV Bus b. 6. Drop Load D2 at MURPHY 3 (526192) 115 kV Bus b. 7. Drop Load 1 at SP-MILWAUKEE (526196) 115 kV Bus b. 8. Drop Load 1 at SP-UPLAND (526198) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0055_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to CHAN+TASCOS6 (523869) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0056_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to MCDWL_CREEK6 (523323) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0057_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to ROLLHILLS 6 (524010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0058_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to HARRNG_EST 6 (523979) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0059_P1 | 3 phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply Fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus to BUSHLAND 6 (524267) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0060_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK6 (523323) 230 kV Bus to MOORE_CNTY 6 (523309) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0061_P1 | 3 phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply Fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MCDWL_CREEK6 (523323) 230 kV Bus to MCDWL_CREEK3 (523322) 115 kV Bus to MCDWL_CRKTR1 (523321) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0062_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0063_P1 | 3 phase fault on HARRNG_EST 6 (523979) 230 kV Bus a. Apply Fault at the HARRNG_EST 6 (523979) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus to PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from PRINGLE 6 (523267) 230 kV Bus to PRINGLE 3 (523266) 115 kV Bus to PRINGLE_TR 1 (523265) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0064_P1 | 3 phase fault on ROLLHILLS 6 (524010) 230 kV Bus a. Apply Fault at the ROLLHILLS 6 (524010) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ROLLHILLS 6 (524010) 230 kV Bus to ROLLHILLS 3 (524007) 115 kV Bus to ROLHILLS_TR1 (524008) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0065_P1 | 3 phase fault on BUSHLAND 6 (524267) 230 kV Bus a. Apply Fault at the BUSHLAND 6 (524267) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from BUSHLAND 6 (524267) 230 kV Bus to BUSHLAND 3 (524266) 115 kV Bus to BSHLND_TR1 1 (524263) 13.2 kV Bus CKT 1 b. 2. Trip branch from BUSHLAND 3 (524266) 115 kV Bus to OUTPOST 3 (524243) 115 kV Bus CKT 1 b. 3. Trip branch from OUTPOST 3 (524243) 115 kV Bus to ARNOT 3 (524560) 115 kV Bus CKT 1 b. 4. Trip branch from ARNOT 3 (524560) 115 kV Bus to HILLSIDE 3 (524300) 115 kV Bus CKT 1 b. 5. Trip branch from HILLSIDE 3 (524300) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 b. 6. Drop Load 1 at OUTPOST 3 (524243) 115 kV Bus b. 7. Drop Load 1 at ARNOT 3 (524560) 115 kV Bus b. 8. Drop Load 1 at HILLSIDE 3 (524300) 115 kV Bus | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0066_P1 | 3 phase fault on NICHOLS 6 (524044) 230 kV Bus a. Apply Fault at the NICHOLS 6 (524044) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 6 (524044) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0067_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 6 (524365) 230 kV Bus to AMA_SOUTH 6 (524415) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0068_P1 | 3 phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply Fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from AMA_SOUTH 6 (524415) 230 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus to AMA_SO_TR1 1 (524410) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0069_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to TOLK 6 (525531) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0070_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR1 1 (525824) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at TUCO_TR1 1 (525824) 13.2 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0071_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV Bus to TUCO_INT 6 (525830) 230 kV Bus to TUCO_TR2 1 (525825) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0072_P1 | 3 phase fault on HARRNG_WST 6 (523977) 230 kV Bus a. Apply Fault at the HARRNG_WST 6 (523977) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus to HARRNG_MID 6 (523978) 230 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0073_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to RANDALL 6 (524365) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0074_P1 | 3 phase fault on HARRNG_MID 6 (523978) 230 kV Bus a. Apply Fault at the HARRNG_MID 6 (523978) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus to NICHOLS 6 (524044) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0075_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#22 3 (524694) 115 kV Bus CKT 1 b. 2. Drop Load 1 at DS-#22 3 (524694) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0076_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR1 1 (524744) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0077_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV Bus to CASTRO_CNTY2 (524745) 69 kV Bus to CASTRO_TR2 1 (524743) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0078_P1 | 3 phase fault on CASTRO_CNTY3 (524746) 115 kV Bus a. Apply Fault at the CASTRO_CNTY3 (524746) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV Bus to DS-#21 3 (524734) 115 kV Bus CKT 1 b. 2. Trip branch from DS-#21 3 (524734) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 3. Drop Load 1 at DS-#21 3 (524734) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 584223 [G14-040-GEN10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0079_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to KRS_RURL_TP3 (525226) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0080_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV Bus to KRESS_INT 2 (525191) 69 kV Bus to KRESS_TR1 1 (525190) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0081_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0082_P1 | 3 phase fault on KRESS_INT 3 (525192) 115 kV Bus a. Apply Fault at the KRESS_INT 3 (525192) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0083_P1 | 3 phase fault on MOORE_CNTY 6 (523309) 230 kV Bus a. Apply Fault at the MOORE_CNTY 6 (523309) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from MOORE_CNTY 6 (523309) 230 kV Bus to MOORE_E 3 (523308) 115 kV Bus to MOORE_TR1 1 (523302) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0084_P1 | 3 phase fault on MCDWL_CREEK3 (523322) 115 kV Bus a. Apply Fault at the MCDWL_CREEK3 (523322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MCDWL_CREEK3 (523322) 115 kV Bus to EXELL_TP 3 (523332) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0085_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV Bus to PLSNT_HILL 3 (524768) 115 kV Bus to PLSNHIL_TR11 (524767) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0086_P1 | 3 phase fault on PLSNT_HILL 6 (524770) 230 kV Bus a. Apply Fault at the PLSNT_HILL 6 (524770) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 6 (524770) 230 kV Bus to OASIS 6 (524875) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0087_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from OASIS 6 (524875) 230 kV Bus to OASIS 3 (524874) 115 kV Bus to OASIS_TR1 113.200 (524872) kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0088_P1 | 3 phase fault on OASIS 6 (524875) 230 kV Bus a. Apply Fault at the OASIS 6 (524875) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 6 (524875) 230 kV Bus to SN_JUAN_TAP6 (524885) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0089_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0090_P1 | 3 phase fault on ROOSEVELT 3 (524908) 115 kV Bus a. Apply Fault at the ROOSEVELT 3 (524908) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0091_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV Bus to HOCKLEY 3 (526020) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0092_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR1 1 (525631) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0093_P1 | 3 phase fault on LAMB_CNTY 3 (525636) 115 kV Bus a. Apply Fault at the LAMB_CNTY 3 (525636) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV Bus to LAMB_CNTY 2 (525635) 69 kV Bus to LAMB_TR2 1 (525632) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0094_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0095_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0096_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_STH 6 (526269) 230 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0097_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to GRASSLAND 6 (526677) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0098_P1 | 3 phase fault on JONES 6 (526337) 230 kV Bus a. Apply Fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JONES 6 (526337) 230 kV Bus to LUBBCK_EST 6 (526299) 230 kV Bus CKT 1 b. 2. Trip three winding transformer from LUBBCK_EST 6 (526299) 230 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus to LBB_EST TR11 (526294) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0099_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to HALE_CNTY 3 (525454) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0100_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to LUBBCK_EST 3 (526298) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0101_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to NORTON 3 (524502) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0102_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to E_CLOVIS 3 (524773) 115 kV Bus CKT 1 b. 2. Trip branch from E_CLOVIS 3 (524773) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 3. Drop Load 1 at E_CLOVIS 3 (524773) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0103_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to N_CLOVIS_TP3 (524776) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0104_P1 | 3 phase fault on PLSNT_HILL 3 (524768) 115 kV Bus a. Apply Fault at the PLSNT_HILL 3 (524768) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PLSNT_HILL 3 (524768) 115 kV Bus to FE-HOLLAND 3 (524831) 115 kV Bus CKT 1 b. 2. Trip branch from FE-HOLLAND 3 (524831) 115 kV Bus to FE-CLOVIS2+3 (524838) 115 kV Bus CKT 1 b. 3. Trip branch from FE-CLOVIS2+3 (524838) 115 kV Bus to CURRY 3 (524822) 115 kV Bus CKT 1 b. 4. Drop Load 1 at FE-HOLLAND 3 (524831) 115 kV Bus b. 5. Drop Load 1 at FE-CLOVIS2+3 (524838) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0105_P1 | 3 phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply Fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SN_JUAN_TAP6 (524885) 230 kV Bus to CHAVES_CNTY6 (527483) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0106_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PORTALES 3 (524924) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0107_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to PERIMETER 3 (524797) 115 kV Bus CKT 1 b. 2. Trip branch from PERIMETER 3 (524797) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PERIMETER 3 (524797) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0108_P1 | 3 phase fault on OASIS 3 (524874) 115 kV Bus a. Apply Fault at the OASIS 3 (524874) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OASIS 3 (524874) 115 kV Bus to FE-CHZPLT 3 (524863) 115 kV Bus CKT 1 b. 2. Trip branch from FE-CHZPLT 3 (524863) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FE-CHZPLT 3 (524863) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0109_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to NORRIS_TP 3 (524764) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0110_P1 | 3 phase fault on NORRIS_TP 3 (524764) 115 kV Bus a. Apply Fault at the NORRIS_TP 3 (524764) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORRIS_TP 3 (524764) 115 kV Bus to NORRIS 3 (524801) 115 kV Bus CKT 1 b. 2. Drop Load 1 at NORRIS 3 (524801) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0111_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR1 1 (524819) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0112_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CURRY 3 (524822) 115 kV Bus to CURRY 2 (524821) 69 kV Bus to CURRY_TR2 1 (524820) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0113_P1 | 3 phase fault on CURRY 3 (524822) 115 kV Bus a. Apply Fault at the CURRY 3 (524822) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CURRY 3 (524822) 115 kV Bus to BAILEYCO 3 (525028) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0114_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR11 (524921) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0115_P1 | 3 phase fault on PORTALES 3 (524924) 115 kV Bus a. Apply Fault at the PORTALES 3 (524924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from PORTALES 3 (524924) 115 kV Bus to PORTALES 2 (524923) 69 kV Bus to PORTLES_TR21 (524922) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0116_P1 | 3 phase fault on DEAFSMITH 6 (524623) 230 kV Bus a. Apply Fault at the DEAFSMITH 6 (524623) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV Bus to DFSMTH_WST 3 (524622) 115 kV Bus to DEFSMTH_TR11 (524620) 13.2 kV Bus CKT 1 b. 2. Trip branch from DFSMTH_WST 3 (524622) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0117_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0118_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR11 (526017) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0119_P1 | 3 phase fault on HOCKLEY 3 (526020) 115 kV Bus a. Apply Fault at the HOCKLEY 3 (526020) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOCKLEY 3 (526020) 115 kV Bus to HOCKLEY 2 (526019) 69 kV Bus to HOCKLEY_TR21 (526018) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0120_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to FE-CLVS_INT3 (524808) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0121_P1 | 3 phase fault on N_CLOVIS_TP3 (524776) 115 kV Bus a. Apply Fault at the N_CLOVIS_TP3 (524776) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from N_CLOVIS_TP3 (524776) 115 kV Bus to N_CLOVIS 3 (524777) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_CLOVIS 3 (524777) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0122_P1 | 3 phase fault on NORTON 3 (524502) 115 kV Bus a. Apply Fault at the NORTON 3 (524502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTON 3 (524502) 115 kV Bus to FE-TUCMCARI3 (524509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0123_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY6 (527483) 230 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0124_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR1 1 (527478) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0125_P1 | 3 phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply Fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CHAVES_CNTY6 (527483) 230 kV Bus to CHAVES_CNTY3 (527482) 115 kV Bus to CHAVES_TR2 1 (527479) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0126_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0127_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV Bus to EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_TR 1 (527796) 13.2 kV Bus CKT 1 b. 2. Drop Shunt 1 at EDDY_TR 1 (527796) 13.2 kV Bus | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0128_P1 | 3 phase fault on FE-CLVS_INT3 (524808) 115 kV Bus a. Apply Fault at the FE-CLVS_INT3 (524808) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from FE-CLVS_INT3 (524808) 115 kV Bus to W_CLOVIS 3 (524784) 115 kV Bus CKT 1 b. 2. Trip branch from W_CLOVIS 3 (524784) 115 kV Bus to CANNON_TP 3 (524790) 115 kV Bus CKT 1 b. 3. Drop Load 1 at W_CLOVIS 3 (524784) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0129_P1 | 3 phase fault on CANNON_TP 3 (524790) 115 kV Bus a. Apply Fault at the CANNON_TP 3 (524790) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANNON_TP 3 (524790) 115 kV Bus to CANNONAFB 3 (524794) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANNONAFB 3 (524794) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0130_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0131_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0132_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to PRICE_TAP 3 (527509) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0133_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to URTON 3 (527501) 115 kV Bus CKT 1 b. 2. Trip branch from URTON 3 (527501) 115 kV Bus to ROSWELL_CTY3 (527522) 115 kV Bus CKT 1 b. 3. Drop Load 1 at URTON 3 (527501) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25W | Transfer | Group5_Fault_0134_P1 | 3 phase fault on CHAVES_CNTY3 (527482) 115 kV Bus a. Apply Fault at the CHAVES_CNTY3 (527482) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CHAVES_CNTY3 (527482) 115 kV Bus to SAMSON 3 (527546) 115 kV Bus CKT 1 b. 2. Trip branch from SAMSON 3 (527546) 115 kV Bus to ROSWLL_INT 3 (527564) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SAMSON 3 (527546) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 583973 [G14-035-GEN10.5500]
05 - Southwest | 25W | Transfer | Group5_Fault_0135_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0136_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0137_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to LP-DOUD 3 (526176) 115 kV Bus CKT 1 b. 2. Drop Load 1 at LP-DOUD 3 (526176) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0138_P1 | 3 phase fault on AMOCO_TP 3 (526445) 115 kV Bus a. Apply Fault at the AMOCO_TP 3 (526445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMOCO_TP 3 (526445) 115 kV Bus to LG-LEVELAND3 (526484) 115 kV Bus CKT 1 b. 2. Trip branch from LG-LEVELAND3 (526484) 115 kV Bus to LG-CLAUENE 3 (526491) 115 kV Bus CKT 1 b. 3. Trip branch from LG-CLAUENE 3 (526491) 115 kV Bus to TERRY_CNTY 3 (526736) 115 kV Bus CKT 1 b. 4. Drop Load 1 at LG-LEVELAND3 (526484) 115 kV Bus b. 5. Drop Load 1 at LG-CLAUENE 3 (526491) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0139_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to YUMA_INT 3 (526475) 115 kV Bus CKT 1 b. 2. Trip branch from YUMA_INT 3 (526475) 115 kV Bus to WOLFFORTH 3 (526524) 115 kV Bus CKT 1 b. 3. Drop Load 1 at YUMA_INT 3 (526475) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0140_P1 | 3 phase fault on SP-WOLF_TP 3 (526481) 115 kV Bus a. Apply Fault at the SP-WOLF_TP 3 (526481) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SP-WOLF_TP 3 (526481) 115 kV Bus to SP-WOLFORTH3 (526483) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SP-WOLFORTH3 (526483) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0141_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to GEORGIA 3 (524322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0142_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to PALO_DURO 3 (524530) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0143_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to CANYON_E_TP3 (524522) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0144_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to SOUTHEAST 3 (524338) 115 kV Bus CKT 1 b. 2. Trip branch from SOUTHEAST 3 (524338) 115 kV Bus to PULLMAN 3 (524331) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SOUTHEAST 3 (524338) 115 kV Bus b. 4. Drop Load 1 at PULLMAN 3 (524331) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0145_P1 | 3 phase fault on RANDALL 3 (524364) 115 kV Bus a. Apply Fault at the RANDALL 3 (524364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RANDALL 3 (524364) 115 kV Bus to MANHATTAN 3 (524224) 115 kV Bus CKT 1 b. 2. Trip branch from MANHATTAN 3 (524224) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MANHATTAN 3 (524224) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0146_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR1 1 (524361) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0147_P1 | 3 phase fault on RANDALL 6 (524365) 230 kV Bus a. Apply Fault at the RANDALL 6 (524365) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RANDALL 6 (524365) 230 kV Bus to RANDALL 3 (524364) 115 kV Bus to RANDAL_TR2 1 (524360) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0148_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to WESTERN 3 (524325) 115 kV Bus CKT 1 b. 2. Trip branch from WESTERN 3 (524325) 115 kV Bus to 34TH_ST_TP 3 (524281) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WESTERN 3 (524325) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0149_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GEORGIA 3 (524322) 115 kV Bus to GEORGIA 2 (524321) 69 kV Bus to GEORGIA_TR11 (524320) 13.2 kV Bus CKT 1 b. 2. Trip branch from GEORGIA 2 (524321) 69 kV Bus to LAWRENPRK1 2 (524209) 69 kV Bus CKT 1 b. 3. Trip branch from LAWRENPRK1 2 (524209) 69 kV Bus to LAWRENPRK2 2 (524216) 69 kV Bus CKT @1 b. 4. Trip branch from LAWRENPRK2 2 (524216) 69 kV Bus to SONCY 2 (524200) 69 kV Bus CKT 1 b. 5. Trip branch from SONCY 2 (524200) 69 kV Bus to SONCY_TP 2 (524251) 69 kV Bus CKT 1 b. 6. Drop Load 1 at LAWRENPRK1 2 (524209) 69 kV Bus b. 7. Drop Load 1 at LAWRENPRK2 2 (524216) 69 kV Bus | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0150_P1 | 3 phase fault on GEORGIA 3 (524322) 115 kV Bus a. Apply Fault at the GEORGIA 3 (524322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV Bus to CRSE_HINDTP3 (524387) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0151_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to HUNSLEY 3 (524520) 115 kV Bus CKT 1 b. 2. Trip branch from HUNSLEY 3 (524520) 115 kV Bus to CANYON_WEST3 (524516) 115 kV Bus CKT 1 b. 3. Trip branch from CANYON_WEST3 (524516) 115 kV Bus to DAWN 3 (524590) 115 kV Bus CKT 1 b. 4. Trip branch from DAWN 3 (524590) 115 kV Bus to PANDAHFD 3 (524597) 115 kV Bus CKT 1 b. 5. Trip branch from PANDAHFD 3 (524597) 115 kV Bus to DS-#25+ 3 (524575) 115 kV Bus CKT 1 b. 6. Trip branch from DS-#25+ 3 (524575) 115 kV Bus to TIERABLANCA3 (524630) 115 kV Bus CKT 1 b. 7. Drop Load 1 at HUNSLEY 3 (524520) 115 kV Bus b. 8. Drop Load 1 at CANYON_WEST3 (524516) 115 kV Bus b. 9. Drop Load 1 at DAWN 3 (524590) 115 kV Bus b. 10. Drop Load 1 at PANDAHFD 3 (524597) 115 kV Bus b. 11. Drop Load 1 at DS-#25+ 3 (524575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0152_P1 | 3 phase fault on CANYON_E_TP3 (524522) 115 kV Bus a. Apply Fault at the CANYON_E_TP3 (524522) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CANYON_E_TP3 (524522) 115 kV Bus to CANYON_EAST3 (524523) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CANYON_EAST3 (524523) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0153_P1 | 3 phase fault on PALO_DURO 3 (524530) 115 kV Bus a. Apply Fault at the PALO_DURO 3 (524530) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PALO_DURO 3 (524530) 115 kV Bus to HAPPY_INT 3 (525154) 115 kV Bus CKT 1 b. 2. Drop Load 1 at PALO_DURO 3 (524530) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0154_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to CROUSE_HIND3 (524388) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CROUSE_HIND3 (524388) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0155_P1 | 3 phase fault on CRSE_HINDTP3 (524387) 115 kV Bus a. Apply Fault at the CRSE_HINDTP3 (524387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CRSE_HINDTP3 (524387) 115 kV Bus to FARMERS 3 (524377) 115 kV Bus CKT 1 b. 2. Trip branch from FARMERS 3 (524377) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 3. Drop Load 1 at FARMERS 3 (524377) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0156_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to 34TH_ST 3 (524282) 115 kV Bus CKT 1 b. 2. Drop Load 1 at 34TH_ST 3 (524282) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0157_P1 | 3 phase fault on 34TH_ST_TP 3 (524281) 115 kV Bus a. Apply Fault at the 34TH_ST_TP 3 (524281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV Bus to COULTER 3 (524306) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0158_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to ESTACADO_TP3 (524425) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0159_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from COULTER 3 (524306) 115 kV Bus to COULTER 2 (524305) 69 kV Bus to COLTER_TR1 1 (524304) 13.2 kV Bus CKT 1 b. 2. Trip branch from COULTER 2 (524305) 69 kV Bus to WATERFL_TP 2 (524234) 69 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0160_P1 | 3 phase fault on COULTER 3 (524306) 115 kV Bus a. Apply Fault at the COULTER 3 (524306) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from COULTER 3 (524306) 115 kV Bus to PUCKETT 3 (524256) 115 kV Bus CKT 1 b. 2. Trip branch from PUCKETT 3 (524256) 115 kV Bus to SONCY_TP 3 (524252) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PUCKETT 3 (524256) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0161_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to ESTACADO 3 (524432) 115 kV Bus CKT 1 b. 2. Drop Load 1 at ESTACADO 3 (524432) 115 kV Bus b. 3. Drop Load 2 at ESTACADO 3 (524432) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0162_P1 | 3 phase fault on ESTACADO_TP3 (524425) 115 kV Bus a. Apply Fault at the ESTACADO_TP3 (524425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ESTACADO_TP3 (524425) 115 kV Bus to PRESTONWEST3 (524341) 115 kV Bus CKT 1 b. 2. Trip branch from PRESTONWEST3 (524341) 115 kV Bus to OWENSCORN 3 (524404) 115 kV Bus CKT 1 b. 3. Trip branch from OWENSCORN 3 (524404) 115 kV Bus to AMA_SOUTH 3 (524414) 115 kV Bus CKT 1 b. 4. Drop Load 1 at PRESTONWEST3 (524341) 115 kV Bus b. 5. Drop Load 1 at OWENSCORN 3 (524404) 115 kV Bus b. 6. Drop Shunt 1 at OWENSCORN 3 (524404) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0163_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to WHITAKER 3 (524058) 115 kV Bus CKT 1 b. 2. Trip branch from WHITAKER 3 (524058) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at WHITAKER 3 (524058) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0164_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to HASTINGS 3 (524136) 115 kV Bus CKT 1 b. 2. Trip branch from HASTINGS 3 (524136) 115 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus CKT 1 b. 3. Drop Load 1 at HASTINGS 3 (524136) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0165_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 3 (524162) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0166_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR1 1 (524158) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0167_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 3 (524162) 115 kV Bus to EAST_PLANT 2 (524161) 69 kV Bus to EPLANT_TR2 1 (524159) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0168_P1 | 3 phase fault on EAST_PLANT 3 (524162) 115 kV Bus a. Apply Fault at the EAST_PLANT 3 (524162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV Bus to EAST_PLANT 3 (524162) 115 kV Bus to EPLANT_TR3 1 (524160) 13.2 kV Bus CKT 1 b. 2. Trip branch from EAST_PLANT 6 (524163) 230 kV Bus to HARRNG_WST 6 (523977) 230 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0169_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 3 (525154) 115 kV Bus to TULIA_TP 3 (525179) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0170_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR1 1 (525151) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0171_P1 | 3 phase fault on HAPPY_INT 3 (525154) 115 kV Bus a. Apply Fault at the HAPPY_INT 3 (525154) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HAPPY_INT 3 (525154) 115 kV Bus to HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_TR2 1 (525152) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0172_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to ARROWHEAD 3 (524397) 115 kV Bus CKT 1 b. 2. Trip branch from ARROWHEAD 3 (524397) 115 kV Bus to OSAGE 3 (524345) 115 kV Bus CKT 1 b. 3. Trip branch from OSAGE 3 (524345) 115 kV Bus to PIERCE_TP 3 (524185) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ARROWHEAD 3 (524397) 115 kV Bus b. 5. Drop Load 1 at OSAGE 3 (524345) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0173_P1 | 3 phase fault on AMA_SOUTH 3 (524414) 115 kV Bus a. Apply Fault at the AMA_SOUTH 3 (524414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from AMA_SOUTH 3 (524414) 115 kV Bus to SPRING_DRW 3 (524544) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SPRING_DRW 3 (524544) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0174_P1 | 3 phase fault on TULIA_TP 3 (525179) 115 kV Bus a. Apply Fault at the TULIA_TP 3 (525179) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TULIA_TP 3 (525179) 115 kV Bus to MU-TULIA 3 (522800) 115 kV Bus CKT 1 b. 2. Drop Load 1 at MU-TULIA 3 (522800) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0175_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SONCY 3 (524254) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SONCY 3 (524254) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0176_P1 | 3 phase fault on SONCY_TP 3 (524252) 115 kV Bus a. Apply Fault at the SONCY_TP 3 (524252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 3 (524252) 115 kV Bus to SUNSET 3 (524249) 115 kV Bus CKT 1 b. 2. Trip branch from SUNSET 3 (524249) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SUNSET 3 (524249) 115 kV Bus b. 4. Drop Load 2 at SUNSET 3 (524249) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0177_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#1 2 (524142) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#1 2 (524142) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0178_P1 | 3 phase fault on EAST_PLANT 2 (524161) 69 kV Bus a. Apply Fault at the EAST_PLANT 2 (524161) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EAST_PLANT 2 (524161) 69 kV Bus to VANBUREN#2 2 (524149) 69 kV Bus CKT 1 b. 2. Drop Load 1 at VANBUREN#2 2 (524149) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0179_P1 | 3 phase fault on HAPPY_INT 2 (525153) 69 kV Bus a. Apply Fault at the HAPPY_INT 2 (525153) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HAPPY_INT 2 (525153) 69 kV Bus to HAPPY_CTYTP2 (525143) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0180_P1 | 3 phase fault on SONCY_TP 2 (524251) 69 kV Bus a. Apply Fault at the SONCY_TP 2 (524251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SONCY_TP 2 (524251) 69 kV Bus to NRTHWST_TP 2 (524096) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0181_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to NORTHWEST 3 (524106) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0182_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTHWEST 3 (524106) 115 kV Bus to BUSH 3 (524124) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BUSH 3 (524124) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0183_P1 | 3 phase fault on NORTHWEST 3 (524106) 115 kV Bus a. Apply Fault at the NORTHWEST 3 (524106) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from NORTHWEST 3 (524106) 115 kV Bus to NORTHWEST 2 (524105) 69 kV Bus to NRTHWST_TR11 (524102) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0184_P1 | 3 phase fault on NICHOLS 3 (524043) 115 kV Bus a. Apply Fault at the NICHOLS 3 (524043) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NICHOLS 3 (524043) 115 kV Bus to YARNELL_TP 3 (524072) 115 kV Bus CKT 1 b. 2. Trip branch from YARNELL_TP 3 (524072) 115 kV Bus to CONWAY 3 (524079) 115 kV Bus CKT 1 b. 3. Trip branch from CONWAY 3 (524079) 115 kV Bus to KIRBY 3 (524088) 115 kV Bus CKT 1 b. 4. Drop Load 1 at CONWAY 3 (524079) 115 kV Bus b. 5. Drop Load D1 at CONWAY 3 (524079) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0185_P1 | 3 phase fault on ROLLHILLS 3 (524007) 115 kV Bus a. Apply Fault at the ROLLHILLS 3 (524007) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV Bus to CHERRY 3 (524009) 115 kV Bus CKT 1 b. 2. Drop Load 1 at CHERRY 3 (524009) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0186_P1 | 3 phase fault on PRINGLE 3 (523266) 115 kV Bus a. Apply Fault at the PRINGLE 3 (523266) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from PRINGLE 3 (523266) 115 kV Bus to Q_RYTON_TP 3 (523478) 115 kV Bus CKT 1 b. 2. Trip branch from Q_RYTON_TP 3 (523478) 115 kV Bus to BLKHAWK_E 3 (523346) 115 kV Bus CKT 1 b. 3. Drop Load 1 at Q_RYTON_TP 3 (523478) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0187_P1 | 3 phase fault on KIRBY 3 (524088) 115 kV Bus a. Apply Fault at the KIRBY 3 (524088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from KIRBY 3 (524088) 115 kV Bus to MCCLELLAN 3 (523804) 115 kV Bus CKT 1 b. 2. Trip branch from MCCLELLAN 3 (523804) 115 kV Bus to MCLEAN 3 (523811) 115 kV Bus CKT 1 b. 3. Trip branch from MCLEAN 3 (523811) 115 kV Bus to SHAM 3WT (512107) 115 kV Bus CKT 1 b. 4. Trip three winding transformer from SHAM 3WT (512107) 115 kV Bus to SHAM 2WT (512106) 69 kV Bus to SR1TERT (512109) 14.4 kV Bus CKT 1 b. 5. Drop Load 1 at MCCLELLAN 3 (523804) 115 kV Bus b. 6. Drop Load 1 at MCLEAN 3 (523811) 115 kV Bus b. 7. Drop Load D1 at MCLEAN 3 (523811) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0188_P1 | 3 phase fault on CAMX/AGR TP3 (523485) 115 kV Bus a. Apply Fault at the CAMX/AGR TP3 (523485) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CAMX/AGR TP3 (523485) 115 kV Bus to W_BORGER_TP3 (523516) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0189_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0190_P1 | 3 phase fault on BLKHAWK_E 3 (523346) 115 kV Bus a. Apply Fault at the BLKHAWK_E 3 (523346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BLKHAWK_E 3 (523346) 115 kV Bus to CPCOKER 3 (523470) 115 kV Bus CKT 1 b. 2. Trip branch from CPCOKER 3 (523470) 115 kV Bus to BLKHAWK_W 3 (523344) 115 kV Bus CKT 1 b. 3. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus b. 4. Drop Load 1 at CPCOKER 3 (523470) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0191_P1 | 3 phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply Fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV Bus to OKLAUN HVDC7 (511565) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0192_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to YOAKUM_345 (526936) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0193_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0194_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV Bus to HOBBS_INT 7 (527896) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0195_P1 | 3 phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply Fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM_345 (526936) 345 kV Bus to YOAKUM 6 (526935) 230 kV Bus to YOAKUM_TR1 (526937) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0196_P1 | 3 phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply Fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0197_P1 | 3 phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply Fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CRAWFISH_DR (560022) 345 kV Bus to TUCO_INT 7 (525832) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | No | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0198_P1 | 3 phase fault on G17-151TAP (762216) 345 kV Bus a. Apply Fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G17-151TAP (762216) 345 kV Bus to CRAWFISH_DR (560022) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | No | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0199_P1 | 3 phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply Fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus to EDDY_CNTY 7 (527802) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0200_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV Bus to HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_TR3 1 (527895) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0201_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR2 1 (526932) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0202_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV Bus to YOAKUM 3 (526934) 115 kV Bus to YOAKUM_TR1 1 (526931) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0203_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to AMOCO_SS 6 (526460) 230 kV Bus CKT 1 b. 2. Trip branch from AMOCO_SS 6 (526460) 230 kV Bus to SUNDOWN 6 (526435) 230 kV Bus CKT 1 b. 3. Drop Load 1 at AMOCO_SS 6 (526460) 230 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0204_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0205_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to BRU_SUB 6 (527009) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0206_P1 | 3 phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply Fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 6 (526935) 230 kV Bus to MUSTANG 6 (527149) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0207_P1 | 3 phase fault on TOLK 7 (525549) 345 kV Bus a. Apply Fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from TOLK 7 (525549) 345 kV Bus to POTTER_CO 7 (523961) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0208_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0209_P1 | 3 phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply Fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus to CROSSROADS 7 (527656) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0210_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to N_LOVING 7 (528185) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0211_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from KIOWA 7 (527965) 345 kV Bus to RDRUNNER 7 (528027) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0212_P1 | 3 phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply Fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from KIOWA 7 (527965) 345 kV Bus to KIOWA 3 (527966) 115 kV Bus to KIOWA_TR1 1 (527964) 13.2 kV Bus CKT 1 b. 2. Trip branch from KIOWA 3 (527966) 115 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0213_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to ANDREWS 6 (528604) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0214_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to INK_BASIN 6 (527028) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0215_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 6 (527894) 230 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0216_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR2 1 (527889) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0217_P1 | 3 phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply Fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from HOBBS_INT 6 (527894) 230 kV Bus to HOBBS_INT 3 (527891) 115 kV Bus to HOBBS_TR1 1 (527890) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0218_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to XTO_MAHONEY6 (527011) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0219_P1 | 3 phase fault on BRU_SUB 6 (527009) 230 kV Bus a. Apply Fault at the BRU_SUB 6 (527009) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BRU_SUB 6 (527009) 230 kV Bus to OXYBRU 6 (527010) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0220_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to PLAINS_INT 3 (526928) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0221_P1 | 3 phase fault on YOAKUM 3 (526934) 115 kV Bus a. Apply Fault at the YOAKUM 3 (526934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from YOAKUM 3 (526934) 115 kV Bus to ARCO_TP 3 (527041) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0222_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G18-092-TAP (763215) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0223_P1 | 3 phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply Fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-015-TAP (762467) 345 kV Bus to G17-151TAP (762216) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0224_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV Bus to CARLISLE 3 (526160) 115 kV Bus to CRLSLE_TR1 1 (526157) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0225_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to STANTON_W 3 (526076) 115 kV Bus CKT 1 b. 2. Trip branch from STANTON_W 3 (526076) 115 kV Bus to INDIANA 3 (526146) 115 kV Bus CKT 1 b. 3. Trip branch from INDIANA 3 (526146) 115 kV Bus to SP-ERSKINE 3 (526109) 115 kV Bus CKT 1 b. 4. Trip branch from SP-ERSKINE 3 (526109) 115 kV Bus to CARLISLE 3 (526160) 115 kV Bus CKT 1 b. 5. Drop Load 1 at STANTON_W 3 (526076) 115 kV Bus b. 6. Drop Load 1 at INDIANA 3 (526146) 115 kV Bus b. 7. Drop Load 2 at INDIANA 3 (526146) 115 kV Bus b. 8. Drop Load 1 at SP-ERSKINE 3 (526109) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0226_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 3 (525828) 115 kV Bus to FLOYD_CNTY 3 (525780) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0227_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR5 1 (525822) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0228_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT 2 (525826) 69 kV Bus to TUCO_TR6 1 (525823) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0229_P1 | 3 phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply Fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV Bus to TUCO_INT2 2 (525816) 69 kV Bus to TUCO_TR7 1 (525814) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0230_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0231_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_STH 3 (527793) 115 kV Bus to EDDY_TR3 1 (527795) 13.2 kV Bus CKT 2 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0232_P1 | 3 phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply Fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from EDDY_NORTH 6 (527799) 230 kV Bus to EDDY_NTH 3 (527798) 115 kV Bus to EDDY_TR2 1 (527797) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0233_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from RDRUNNER 7 (528027) 345 kV Bus to RDRUNNER 3 (528025) 115 kV Bus to RDRNNER_TR11 (528023) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0234_P1 | 3 phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply Fault at the RDRUNNER 7 (528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV Bus to PHANTOM 7 (528015) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0235_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip three winding transformer from N_LOVING 7 (528185) 345 kV Bus to NORTH_LOVNG3 (528182) 115 kV Bus to N_LOVING TR1 (528186) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0236_P1 | 3 phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply Fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV Bus to CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0237_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to INTREPDW_TP3 (527999) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0238_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV Bus to POTASH_JCT 3 (527962) 115 kV Bus to POTASH_TR1 1 (527958) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0239_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR2 1 (527959) 13.2 kV Bus CKT 1 | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0240_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from POTASH_JCT 3 (527962) 115 kV Bus to POTASH_JCT 2 (527961) 69 kV Bus to POTASH_TR3 1 (527960) 13.2 kV Bus CKT 2 | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0241_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0242_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0243_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to PECOS 6 (528179) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0244_P1 | 3 phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply Fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 6 (527963) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0245_P1 | 3 phase fault on CARLISLE 3 (526160) 115 kV Bus a. Apply Fault at the CARLISLE 3 (526160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 3 (526160) 115 kV Bus to LP-DOUD_TP 3 (526162) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0246_P1 | 3 phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus to CARPENTER 7 (523823) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0247_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHILL3 (528230) 115 kV Bus CKT 1 b. 2. Trip branch from AGAVE_RHILL3 (528230) 115 kV Bus to OCHOA 3 (528232) 115 kV Bus CKT 1 b. 3. Drop Load 1 at AGAVE_RHILL3 (528230) 115 kV Bus b. 4. Drop Load 1 at OCHOA 3 (528232) 115 kV Bus b. 5. Drop Load 1* at OCHOA 3 (528232) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0248_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to AGAVE_RHIL23 (528231) 115 kV Bus CKT 1 b. 2. Drop Load 1 at AGAVE_RHIL23 (528231) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0249_P1 | 3 phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply Fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RDRUNNER 3 (528025) 115 kV Bus to RR_SVC_HV 3 (528024) 115 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0250_P1 | 3 phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply Fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NORTH_LOVNG3 (528182) 115 kV Bus to BLACKRIVER 3 (528193) 115 kV Bus CKT 1 b. 2. Trip branch from BLACKRIVER 3 (528193) 115 kV Bus to SENDERO +3 (528184) 115 kV Bus CKT 1 b. 3. Trip branch from SENDERO +3 (528184) 115 kV Bus to BLCKRVR_DST3 (528206) 115 kV Bus CKT 1 b. 4. Trip branch from BLCKRVR_DST3 (528206) 115 kV Bus to CHINA_DRAW 3 (528222) 115 kV Bus CKT 1 b. 5. Drop Load 1 at NORTH_LOVNG3 (528182) 115 kV Bus b. 6. Drop Load 1 at BLACKRIVER 3 (528193) 115 kV Bus b. 7. Drop Load 1 at SENDERO +3 (528184) 115 kV Bus b. 8. Drop Load 2 at SENDERO +3 (528184) 115 kV Bus b. 9. Drop Load 1 at BLCKRVR_DST3 (528206) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0251_P1 | 3 phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply Fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ANDREWS 3 (528602) 115 kV Bus to NA_ENRICH 3 (528603) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0252_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to ALLRED_SUB 3 (527024) 115 kV Bus CKT 1 b. 2. Trip branch from ALLRED_SUB 3 (527024) 115 kV Bus to APACHE_ROB 3 (527022) 115 kV Bus CKT 1 b. 3. Trip branch from APACHE_ROB 3 (527022) 115 kV Bus to CORTEZ 3 (527021) 115 kV Bus CKT 1 b. 4. Drop Load 1 at ALLRED_SUB 3 (527024) 115 kV Bus b. 5. Drop Load 1 at APACHE_ROB 3 (527022) 115 kV Bus b. 6. Drop Load 1 at CORTEZ 3 (527021) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0253_P1 | 3 phase fault on ALRDCRTZ_TP3 (527030) 115 kV Bus a. Apply Fault at the ALRDCRTZ_TP3 (527030) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from ALRDCRTZ_TP3 (527030) 115 kV Bus to XTO_CORNEL+3 (527033) 115 kV Bus CKT 1 b. 2. Trip branch from XTO_CORNEL+3 (527033) 115 kV Bus to SHELLC3_TP 3 (527068) 115 kV Bus CKT 1 b. 3. Drop Load 1 at XTO_CORNEL+3 (527033) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0254_P1 | 3 phase fault on LP-DOUD_TP 3 (526162) 115 kV Bus a. Apply Fault at the LP-DOUD_TP 3 (526162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LP-DOUD_TP 3 (526162) 115 kV Bus to SP-WOLF_TP 3 (526481) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0255_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to DRINKARD 3 (528589) 115 kV Bus CKT 1 b. 2. Trip branch from DRINKARD 3 (528589) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at DRINKARD 3 (528589) 115 kV Bus b. 6. Drop Load 1* at DRINKARD 3 (528589) 115 kV Bus b. 7. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 8. Drop Shunt 1 at DRINKARD 3 (528589) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0256_P1 | 3 phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply Fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from NA_ENRICH 3 (528603) 115 kV Bus to TARGA 3 (528605) 115 kV Bus CKT 1 b. 2. Trip branch from TARGA 3 (528605) 115 kV Bus to CARDINAL 3 (528596) 115 kV Bus CKT 1 b. 3. Drop Load 1 at NA_ENRICH 3 (528603) 115 kV Bus b. 4. Drop Load 5* at NA_ENRICH 3 (528603) 115 kV Bus b. 5. Drop Load 1 at TARGA 3 (528605) 115 kV Bus b. 6. Drop Shunt 1 at NA_ENRICH 3 (528603) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0257_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELL_C2 3 (527036) 115 kV Bus CKT 1 b. 2. Trip branch from SHELL_C2 3 (527036) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 b. 3. Drop Load 1 at SHELL_C2 3 (527036) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0258_P1 | 3 phase fault on SHELLC3_TP 3 (527068) 115 kV Bus a. Apply Fault at the SHELLC3_TP 3 (527068) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SHELLC3_TP 3 (527068) 115 kV Bus to SHELLC3 3 (527074) 115 kV Bus CKT 1 b. 2. Drop Load 1 at SHELLC3 3 (527074) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0259_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to JONES 6 (526337) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0260_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to ANTELOPE_1 6 (525840) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0261_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to CARLISLE 6 (526161) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0262_P1 | 3 phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply Fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TUCO_INT 6 (525830) 230 kV Bus to SWISHER 6 (525213) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0263_P1 | 3 phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply Fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus to KIOWA 7 (527965) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0264_P1 | 3 phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply Fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARLISLE 6 (526161) 230 kV Bus to WOLFFORTH 6 (526525) 230 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0265_P1 | 3 phase fault on CARPENTER 7 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus to HARBNGR7 (531512) 345 kV Bus CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0266_P1 | 3 phase fault on G18-092-TAP (763215) 345 kV Bus a. Apply Fault at the G18-092-TAP (763215) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b. 1. Trip branch from G18-092-TAP (763215) 345 kV Bus to O.K.U.-7 (511456) 345 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0267_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0268_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to CUNNINHAM 3 (527864) 115 kV Bus CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0269_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 b. 2. Trip branch from BENSING 3 (528433) 115 kV Bus to HIGG 3 (527363) 115 kV Bus CKT 1 b. 3. Drop Load 1 at BENSING 3 (528433) 115 kV Bus b. 4. Drop Load 1* at BENSING 3 (528433) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0270_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MILLEN_TPW 3 (528434) 115 kV Bus CKT 1 b. 2. Trip branch from MILLEN_TPW 3 (528434) 115 kV Bus to MILLEN 3 (528435) 115 kV Bus CKT *1 b. 3. Trip branch from MILLEN 3 (528435) 115 kV Bus to MILLEN_TPE 3 (528436) 115 kV Bus CKT *1 b. 4. Trip branch from MILLEN_TPE 3 (528436) 115 kV Bus to NE_HOBBS 3 (528442) 115 kV Bus CKT 1 b. 5. Trip branch from NE_HOBBS 3 (528442) 115 kV Bus to TAYLOR 3 (528413) 115 kV Bus CKT 1 b. 6. Drop Load 1 at MILLEN 3 (528435) 115 kV Bus b. 7. Drop Load 1* at MILLEN 3 (528435) 115 kV Bus b. 8. Drop Load 1 at NE_HOBBS 3 (528442) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0271_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to LE-WEST_SUB3 (528333) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0272_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0273_P1 | 3 phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply Fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV Bus to BENSING 3 (528433) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0274_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to BUCKEYE_TP 3 (528348) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0275_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MADDOX 3 (528355) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0276_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to QUAHADA 3 (528394) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0277_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV Bus to MONUMNT_TP 3 (528568) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0278_P1 | 3 phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply Fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from CUNNINHAM 3 (527864) 115 kV Bus to CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNHM_TR1 1 (527863) 13.2 kV Bus CKT 1 | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0279_P1 | 3 phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply Fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WEST_SUB3 (528333) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0280_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to MONUMENT 3 (528491) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0281_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0282_P1 | 3 phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply Fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MADDOX 3 (528355) 115 kV Bus to PEARLE 3 (528392) 115 kV Bus CKT 1 b. 2. Trip branch from PEARLE 3 (528392) 115 kV Bus to ENRON_TP 3 (528317) 115 kV Bus CKT 1 b. 3. Drop Load 1 at PEARLE 3 (528392) 115 kV Bus b. 4. Drop Load 1* at PEARLE 3 (528392) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0283_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to HIGGEAST 3 (527286) 115 kV Bus CKT 1 b. 2. Trip branch from HIGGEAST 3 (527286) 115 kV Bus to DENVER_N 3 (527130) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0284_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0285_P1 | 3 phase fault on HIGG 3 (527363) 115 kV Bus a. Apply Fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from HIGG 3 (527363) 115 kV Bus to RUSSELL 3 (527284) 115 kV Bus CKT 1 b. 2. Drop Load 1 at RUSSELL 3 (527284) 115 kV Bus b. 3. Drop Load 2 at RUSSELL 3 (527284) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0286_P1 | 3 phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply Fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from INK_BASIN 6 (527028) 230 kV Bus to INK_BASIN 3 (527027) 115 kV Bus to INKBASN_TR 1 (527026) 13.2 kV Bus CKT 1 | P1 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0287_P1 | 3 phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply Fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CUNNIGHM_S 6 (527867) 230 kV Bus to CUNNIGHM_N 6 (527865) 230 kV Bus CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0288_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR21 (528600) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0289_P1 | 3 phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply Fault at the ANDREWS 6 (528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from ANDREWS 6 (528604) 230 kV Bus to ANDREWS 3 (528602) 115 kV Bus to ANDREWS_TR11 (528601) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0290_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to JOHNSON_DRW3 (527362) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0291_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to W_BENDER 3 (528449) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0292_P1 | 3 phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply Fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from TAYLOR 3 (528413) 115 kV Bus to E_SANGER 3 (528470) 115 kV Bus CKT 1 b. 2. Trip branch from E_SANGER 3 (528470) 115 kV Bus to S_HOBBS 3 (528477) 115 kV Bus CKT 1 b. 3. Trip branch from S_HOBBS 3 (528477) 115 kV Bus to OXY_S_HOBBS3 (528480) 115 kV Bus CKT 1 b. 4. Trip branch from OXY_S_HOBBS3 (528480) 115 kV Bus to SW_4J44 3 (528484) 115 kV Bus CKT 1 b. 5. Trip branch from SW_4J44 3 (528484) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 b. 6. Drop Load 1 at E_SANGER 3 (528470) 115 kV Bus b. 7. Drop Load 1 at S_HOBBS 3 (528477) 115 kV Bus b. 8. Drop Load 2 at S_HOBBS 3 (528477) 115 kV Bus b. 9. Drop Load 1 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 10. Drop Load 2 at OXY_S_HOBBS3 (528480) 115 kV Bus b. 11. Drop Load 3 at OXY_S_HOBBS3 (528480) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0293_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0294_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-NRTH_INT3 (528334) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0295_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to OXY_NHU_RCF3 (528574) 115 kV Bus CKT 1 b. 2. Trip branch from OXY_NHU_RCF3 (528574) 115 kV Bus to OXYPERMIAN 3 (528575) 115 kV Bus CKT 1 b. 3. Trip branch from OXYPERMIAN 3 (528575) 115 kV Bus to SANGER_SW 3 (528463) 115 kV Bus CKT 1 b. 4. Drop Load 1 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 5. Drop Load 2 at OXY_NHU_RCF3 (528574) 115 kV Bus b. 6. Drop Load 2 at OXYPERMIAN 3 (528575) 115 kV Bus b. 7. Drop Load 1 at OXYPERMIAN 3 (528575) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0296_P1 | 3 phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply Fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_BENDER 3 (528449) 115 kV Bus to N_HOBBS 3 (528456) 115 kV Bus CKT 1 b. 2. Drop Load 1 at N_HOBBS 3 (528456) 115 kV Bus b. 3. Drop Load 2 at N_HOBBS 3 (528456) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0297_P1 | 3 phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply Fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SANGER_SW 3 (528463) 115 kV Bus to G18-004-TAP (762442) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0298_P1 | 3 phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply Fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMENT 3 (528491) 115 kV Bus to W_HOBBS 3 (528498) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0299_P1 | 3 phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply Fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from W_HOBBS 3 (528498) 115 kV Bus to DRINKARD_TP3 (528533) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0300_P1 | 3 phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply Fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DRINKARD_TP3 (528533) 115 kV Bus to EUNICE 3 (528512) 115 kV Bus CKT 1 b. 2. Drop Load 1 at EUNICE 3 (528512) 115 kV Bus b. 3. Drop Load 1* at EUNICE 3 (528512) 115 kV Bus b. 4. Drop Shunt 1 at EUNICE 3 (528512) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0301_P1 | 3 phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply Fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from MONUMNT_TP 3 (528568) 115 kV Bus to BYRD_TP 3 (528581) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0302_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to OXY_WSEM_TP3 (527325) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0303_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to LE-ERF 3 (528775) 115 kV Bus CKT "@1" c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0304_P1 | 3 phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply Fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV Bus to MAPCO 3 (527360) 115 kV Bus CKT 1 b. 2. Trip branch from MAPCO 3 (527360) 115 kV Bus to AM_FRAC 3 (527300) 115 kV Bus CKT 1 b. 3. Drop Load 1 at MAPCO 3 (527360) 115 kV Bus b. 4. Drop Load 1 at AM_FRAC 3 (527300) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0305_P1 | 3 phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply Fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from INK_BASIN 3 (527027) 115 kV Bus to ALRDCRTZ_TP3 (527030) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0306_P1 | 3 phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply Fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-WAITS 3 (528325) 115 kV Bus to LE-WAITS 2 (528617) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0307_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-DSYSRPOI2 (528677) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0308_P1 | 3 phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply Fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV Bus to LE-TATMGOAB2 (528679) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0309_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT @1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0310_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV Bus to MUSTANG 3 (527146) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0311_P1 | 3 phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply Fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from DENVER_N 3 (527130) 115 kV Bus to DENVER_CTY 2 (527125) 69 kV Bus to DNVER_N_TR11 (527122) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0312_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to BYRD 3 (528582) 115 kV Bus CKT 1 b. 2. Drop Load 1 at BYRD 3 (528582) 115 kV Bus b. 3. Drop Load 1* at BYRD 3 (528582) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0313_P1 | 3 phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply Fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from BYRD_TP 3 (528581) 115 kV Bus to COOPER_RNCH3 (528554) 115 kV Bus CKT 1 b. 2. Trip branch from COOPER_RNCH3 (528554) 115 kV Bus to OIL_CENTER 3 (528552) 115 kV Bus CKT 1 b. 3. Trip branch from OIL_CENTER 3 (528552) 115 kV Bus to LEA_ROAD 3 (528505) 115 kV Bus CKT 1 b. 4. Drop Load 1 at COOPER_RNCH3 (528554) 115 kV Bus b. 5. Drop Load 1 at OIL_CENTER 3 (528552) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0314_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to OXY_WSTSEM 3 (527323) 115 kV Bus CKT 1 b. 2. Drop Load 1 at OXY_WSTSEM 3 (527323) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0315_P1 | 3 phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply Fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from OXY_WSEM_TP3 (527325) 115 kV Bus to GAINES 3 (527322) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0316_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from LE-ERF 3 (528775) 115 kV Bus to LE-TALLCOTN3 (528779) 115 kV Bus CKT 1 b. 2. Trip branch from LE-TALLCOTN3 (528779) 115 kV Bus to LE-KCM 3 (527292) 115 kV Bus CKT 1 b. 3. Drop Load 1 at LE-TALLCOTN3 (528779) 115 kV Bus b. 4. Drop Load 1 at LE-KCM 3 (527292) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0317_P1 | 3 phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply Fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from LE-ERF 3 (528775) 115 kV Bus to LE-ERF 2 (528774) 69 kV Bus to LE-ERF_TR 1 (528773) 12.47 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0318_P1 | 3 phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply Fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV Bus to PCA 3 (527930) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0319_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to TEAGUE 3 (528526) 115 kV Bus CKT 1 b. 2. Trip branch from TEAGUE 3 (528526) 115 kV Bus to S_JAL 3 (528547) 115 kV Bus CKT 1 b. 3. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus b. 4. Drop Load 1* at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0320_P1 | 3 phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply Fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from CARDINAL 3 (528596) 115 kV Bus to SAGE_BRUSH 3 (527955) 115 kV Bus CKT 1 b. 2. Trip branch from SAGE_BRUSH 3 (527955) 115 kV Bus to MEDANOS 3 (527954) 115 kV Bus CKT 1 b. 3. Trip branch from MEDANOS 3 (527954) 115 kV Bus to LIVSTNRIDGE3 (527953) 115 kV Bus CKT 1 b. 4. Drop Load 1 at SAGE_BRUSH 3 (527955) 115 kV Bus b. 5. Drop Load 1* at SAGE_BRUSH 3 (527955) 115 kV Bus b. 6. Drop Load 1 at TEAGUE 3 (528526) 115 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0321_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to SEMINOLE 3 (527275) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0322_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 3 (527322) 115 kV Bus to LEGACY 3 (527346) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0323_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR1 1 (527319) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0324_P1 | 3 phase fault on GAINES 3 (527322) 115 kV Bus a. Apply Fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from GAINES 3 (527322) 115 kV Bus to GAINES 2 (527321) 69 kV Bus to GAINES_TR2 1 (527320) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0325_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV Bus to SAN_ANDS_TP3 (527105) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0326_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR21 (527274) 13.2 kV Bus CKT 2 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0327_P1 | 3 phase fault on SEMINOLE 3 (527275) 115 kV Bus a. Apply Fault at the SEMINOLE 3 (527275) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip three winding transformer from SEMINOLE 3 (527275) 115 kV Bus to SEMINOLE 6 (527276) 230 kV Bus to SEMINLE_TR11 (527273) 13.2 kV Bus CKT 1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0328_P1 | 3 phase fault on GAINES 2 (527321) 69 kV Bus a. Apply Fault at the GAINES 2 (527321) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from GAINES 2 (527321) 69 kV Bus to RILEY_TP 2 (527228) 69 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0329_P1 | 3 phase fault on SAN_ANDS_TP3 (527105) 115 kV Bus a. Apply Fault at the SAN_ANDS_TP3 (527105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from SAN_ANDS_TP3 (527105) 115 kV Bus to DENVER_S 3 (527136) 115 kV Bus CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0330_P1 | 3 phase fault on RILEY_TP 2 (527228) 69 kV Bus a. Apply Fault at the RILEY_TP 2 (527228) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b. 1. Trip branch from RILEY_TP 2 (527228) 69 kV Bus to RILEY 2 (527331) 69 kV Bus CKT 1 b. 2. Drop Load 1 at RILEY 2 (527331) 69 kV Bus c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0331_P4 | a. Apply single phase fault at O.K.U.-7 (511456) 345 kV CB 3409A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip branch from O.K.U.-7 (511456) 345 kV to G18-092-TAP (763215) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0332_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3429B Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from O.K.U.-7 (511456) 345 kV to L.E.S.-7 (511468) 345 kV CKT 1 b. 2. Trip three winding transformer from LES#5-1 (511411) 13.8 kV to L.E.S.-4 (511467) kV to L.E.S.-7 (511468) 345 kV CKT2 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0333_P4 | a. Apply single phase fault at L.E.S.-7 (511468) 345 kV CB 3433A Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-7 (511468) 345 kV to O.K.U.-7 (511456) 345 kV CKT 1 b. 2. Trip branch from L.E.S.-7 (511468) 345 kV to G17-171-TAP (760938) 345 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Lawton Eastside 345 kV Substation Upgrade to Double-Bus-Double-Breaker Configuration | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0334_P4 | a. Apply single phase fault at BVRCNTY7 (515554) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 2 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523121 [GRPLNS-WT4-10.5750], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0335_P4 | a. Apply single phase fault at CARPENTER 7 (523823) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV to FINNEY 7 (523853) 345 kV CKT 1 b. 2. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0336_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 3. Trip branch from CROSSROADS 7 (527656) 345 kV to RSVLT_CC_E 7 (527655) 345 kV CKT 1 b. 4. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 5. Disconnect Bus MILO_WIND 1 (527653) 0.7 kV b. 6. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 7. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 8. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 9. Disconnect Bus CROSSROADS 7 (527656) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0337_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Trip three winding transformer from EDDY_TR 1 (527796) 13.2 kV to EDDY_NORTH 6 (527799) kV to EDDY_CNTY 7 (527802) 345 kV CKT1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0338_P4 | a. Apply single phase fault at FINNEY 7 (523853) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FINNEY 7 (523853) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from FINNEY 7 (523853) 345 kV to HOLCOMB7 (531449) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0339_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to BVRCNTY7 (515554) 345 kV CKT 2 b. 2. Disconnect Bus NOVUS_WND 1 (523107) 4.16 kV b. 3. Disconnect Bus NOVUS1 1 (523109) 34.5 kV b. 4. Disconnect Bus NOVUS1 3 (523111) 115 kV b. 5. Disconnect Bus NOVUS1_TR1 1 (523110) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0340_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Drop Shunt HITCHLAND 7 (523097) 345 kV b. 3. Trip three winding transformer from HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 6 (523095) kV to HITCHLAND 7 (523097) 345 kV CKT2 | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0341_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to POTTER_CO 7 (523961) 345 kV CKT 1 b. 2. Disconnect Bus NOBLE_TR 1 (523102) 13.8 kV b. 3. Disconnect Bus NOBLE_WND 3 (523103) 115 kV b. 4. Disconnect Bus GRPLNS-HV4-3 (523130) 115 kV b. 5. Disconnect Bus GRPLNS-HV2-3 (523131) 115 kV b. 6. Disconnect Bus GRPLNS-LV4-1 (523127) 34.5 kV b. 7. Disconnect Bus GRPLNS-LV2-1 (523129) 34.5 kV b. 8. Disconnect Bus GRPLNS-CB4-1 (523124) 34.5 kV b. 9. Disconnect Bus GRPLNS-CB2-1 (523126) 34.5 kV b. 10. Disconnect Bus GRPLNS-WT4-1 (523121) 0.575 kV b. 11. Disconnect Bus GRPLNS-WT2-1 (523123) 0.575 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523122 [NBLWND-WTG110.7000]
05 - Southwest | 25W | Transfer | Group5_Fault_0342_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0343_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Trip three winding transformer from NORTH_LOVNG3 (528182) 115 kV to N_LOVING 7 (528185) kV to N_LOVING TR1 (528186) 13.2 kV CKT1 b. 4. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 5. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0344_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 b. 2. Trip three winding transformer from POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 6 (523959) kV to POTTER_CO 7 (523961) 345 kV CKT1 b. 3. Disconnect Bus POTTER_CO 7 (523961) 345 kV b. 4. Disconnect Bus SPNSPUR_WND7 (524296) 345 kV b. 5. Disconnect Bus SPNSPUR_GEN1 (524295) 0.69 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0345_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM_345 (526936) kV to YOAKUM_TR1 (526937) 13.2 kV CKT1 b. 4. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0346_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to CRAWFISH_DR (560022) 345 kV CKT | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0347_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Disconnect Bus ELK_CT1 (525850) 345 kV b. 3. Disconnect Bus ELK_1 1 (525844) 18 kV b. 4. Disconnect Bus ELK_2 1 (525845) 18 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0348_P4 | a. Apply single phase fault at EDDY_CNTY 7 (527802) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Trip branch from EDDY_CNTY 7 (527802) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0349_P4 | a. Apply single phase fault at HOBBS_INT 7 (527896) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 2. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0350_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to TUCO_INT 7 (525832) 345 kV CKT 1 b. 2. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0351_P4 | a. Apply single phase fault at N_LOVING 7 (528185) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from N_LOVING 7 (528185) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Trip branch from N_LOVING 7 (528185) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING 7 (528185) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0352_P4 | a. Apply single phase fault at CHINA_DRAW 7 (528223) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from CHINA_DRAW 7 (528223) 345 kV to N_LOVING 7 (528185) 345 kV CKT 1 b. 3. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 4. Disconnect Bus CHINA_DRAW 7 (528223) 345 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0353_P4 | a. Apply single phase fault at RDRUNNER 7 (528027) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from RDRUNNER 7 (528027) 345 kV to PHANTOM 7 (528015) 345 kV CKT 1 b. 2. Trip branch from RDRUNNER 7 (528027) 345 kV to KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7 (528027) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0354_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to CHINA_DRAW 7 (528223) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR21 (528012) 13.2 kV | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0355_P4 | a. Apply single phase fault at PHANTOM 7 (528015) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PHANTOM 7 (528015) 345 kV to RDRUNNER 7 (528027) 345 kV CKT 1 b. 2. Disconnect Bus PHANTOM TR11 (528011) 13.2 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0356_P4 | a. Apply single phase fault at SUNDOWN 6 (526435) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SUNDOWN 6 (526435) 230 kV to AMOCO_SS 6 (526460) kV CKT 1 b. 2. Disconnect Bus AMOCO_SS 6 (526460) 230 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0357_P4 | a. Apply single phase fault at BORDER 7 (515458) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from BORDER 7 (515458) 345 kV to CRAWFISH_DR (560022) 345 kV CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV to WWDBORDT (755000) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0358_P4 | a. Apply single phase fault at WWRDEHV7 (515375) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WWRDEHV7 (515375) 345 kV to WWDBORDT (755000) 345 kV CKT 1 b. 2. Trip branch from WWRDEHV7 (515375) 345 kV to TATONGA7 (515407) 345 kV CKT 1 b. 3. Trip three winding transformer from WWRDEHV7 (515375) 345 kV to WWRDEHV4 (515376) kV to WWDEHV21 (515799) 13.8 kV CKT2 b. 4. Drop Shunt 1 WWDEHV21 (515799) 13.8 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0359_P4 | a. Apply single phase fault at SWEETWT6 (511541) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SWEETWT6 (511541) 230 kV to CHISHOLM6 (511557) 230 kV CKT 1 b. 2. Trip branch from SWEETWT6 (511541) 230 kV to STLN-DEMARC6 (523779) 230 kV CKT 1 b. 3. Trip branch from STLN-DEMARC6 (523779) 230 kV to WHEELER 6 (523777) 230 kV CKT 1 | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 511967 [BUFFCK0 0.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0360_P4 | a. Apply single phase fault at TUCO_INT 6 (525830) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 3 (525828) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip three winding transformer from TUCO_INT 6 (525830) 230 kV to TUCO_INT 7 (525832) kV to TUCO_TR2 1 (525825) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0361_P4 | a. Apply single phase fault at PLANT_X 6 (525481) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 6 (525481) 230 kV to SUNDOWN 6 (526435) 230 kV CKT 1 b. 2. Trip branch from PLANT_X 6 (525481) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0362_P4 | a. Apply single phase fault at NEWHART 6 (525461) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from NEWHART 6 (525461) 230 kV to POTTER_CO 6 (523959) 230 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR11 (525459) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0363_P4 | a. Apply single phase fault at TOLK 6 (525531) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 6 (525531) 230 kV to ROOSEVELT 6 (524909) 230 kV CKT 1 b. 2. Trip three winding transformer from TOLK 7 (525549) 345 kV to TOLK 6 (525531) kV to TOLK_TR 1 (525537) 13.2 kV CKT1 b. 3. Drop Shunt 1 TOLK_TR 1 (525537) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0364_P4 | a. Apply single phase fault at PLANT_X 3 (525480) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLANT_X 3 (525480) 115 kV to MULSHVLY_TP3 (525019) 115 kV CKT 1 b. 2. Trip branch from MULSHVLY_TP3 (525019) 115 kV to MULESHVALLY3 (525018) 115 kV CKT 1 b. 3. Trip branch from MULSHVLY_TP3 (525019) 115 kV to BAILEYCO 3 (525028) 115 kV CKT 1 b. 4. Drop Load 1 MULESHVALLY3 (525018) 115 kV b. 5. Drop Load 2 MULESHVALLY3 (525018) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0365_P4 | a. Apply single phase fault at ROOSEVELT 6 (524909) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 6 (524909) 230 kV to OASIS 6 (524875) 230 kV CKT 1 b. 2. Trip branch from ROOSEVELT 6 (524909) 230 kV to TOLK 6 (525531) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0366_P4 | a. Apply single phase fault at LAMB_CNTY 3 (525636) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LAMB_CNTY 3 (525636) 115 kV to HOCKLEY 3 (526020) 115 kV CKT 1 b. 2. Trip three winding transformer from LAMB_CNTY 6 (525637) 230 kV to LAMB_CNTY 3 (525636) kV to LAMB_TR3 1 (525633) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0367_P4 | a. Apply single phase fault at CASTRO_CNTY3 (524746) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CASTRO_CNTY3 (524746) 115 kV to CASTRO_CNTY2 (524745) kV to CASTRO_TR1 1 (524744) 13.2 kV CKT1 b. 2. Trip branch from CASTRO_CNTY3 (524746) 115 kV to DS-#21 3 (524734) 115 kV CKT 1 b. 3. Trip branch from DS-#21 3 (524734) 115 kV to TIERABLANCA3 (524630) 115 kV CKT 1 b. 4. Drop Load 1 DS-#21 3 (524734) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0368_P4 | a. Apply single phase fault at TUCO_INT 3 (525828) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 6 (525830) kV to TUCO_TR4 1 (525821) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 3 (525828) 115 kV to FLOYD_CNTY 3 (525780) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0369_P4 | a. Apply single phase fault at KRESS_INT 3 (525192) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from KRESS_INT 3 (525192) 115 kV to KRS_RURL_TP3 (525226) 115 kV CKT 1 b. 2. Trip three winding transformer from KRESS_INT 3 (525192) 115 kV to KRESS_INT 2 (525191) kV to KRESS_TR1 1 (525190) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0370_P4 | a. Apply single phase fault at LUBBCK_STH 6 (526269) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from WOLFFORTH 6 (526525) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 b. 2. Trip branch from JONES 6 (526337) 230 kV to LUBBCK_STH 6 (526269) 230 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0371_P4 | a. Apply single phase fault at YOAKUM 6 (526935) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 b. 2. Trip branch from YOAKUM 3 (526934) 115 kV to PLAINS_INT 3 (526928) 115 kV CKT 1 | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0372_P4 | a. Apply single phase fault at TERRY_CNTY 3 (526736) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TERRY_CNTY 3 (526736) 115 kV to WOLFFORTH 3 (526524) 115 kV CKT 1 b. 2. Trip three winding transformer from TERRY_CNTY 3 (526736) 115 kV to TERRY_CNTY 2 (526735) kV to TERRY_TR1 1 (526733) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0373_P4 | a. Apply single phase fault at TIERABLANCA3 (524630) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TIERABLANCA3 (524630) 115 kV to DFSMTH_EST 3 (524619) 115 kV CKT 1 b. 2. Trip three winding transformer from DEAFSMITH 6 (524623) 230 kV to DFSMTH_EST 3 (524619) kV to DEFSMTH_TR21 (524621) 13.8 kV CKT2 b. 3. Trip branch from TIERABLANCA3 (524630) 115 kV to NE_HEREFORD3 (524567) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0374_P4 | a. Apply single phase fault at ROLLHILLS 3 (524007) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROLLHILLS 3 (524007) 115 kV to NORTHWEST 3 (524106) 115 kV CKT 1 b. 2. Drop Shunt 1 ROLLHILLS 3 (524007) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0375_P4 | a. Apply single phase fault at AMA_SOUTH 3 (524414) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from AMA_SOUTH 3 (524414) 115 kV to AMA_SOUTH 6 (524415) kV to AMA_SO_TR1 1 (524410) 13.2 kV CKT1 b. 2. Trip branch from AMA_SOUTH 3 (524414) 115 kV to OWENSCORN 3 (524404) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0376_P4 | a. Apply single phase fault at HITCHLAND 6 (523095) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HITCHLAND 6 (523095) 230 kV to HITCHLAND 7 (523097) kV to HITCHLD_TR21 (523094) 13.2 kV CKT2 b. 2. Trip branch from HITCHLAND 6 (523095) 230 kV to MOORE_CNTY 6 (523309) 230 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0377_P4 | a. Apply single phase fault at L.E.S.-4 (511467) 138 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from L.E.S.-4 (511467) 138 kV to SHERID4 (511474) 138 kV CKT 1 b. 2. Trip branch from SHERID4 (511474) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 3. Trip branch from 53CACHE4 (511509) 138 kV to ARTVLTP4 (511537) 138 kV CKT 1 b. 4. Trip branch from ARTVLTP4 (511537) 138 kV to ARTVILL4 (511538) 138 kV CKT 1 b. 5. Trip branch from LWS-NTP4 (511471) 138 kV to 53CACHE4 (511509) 138 kV CKT 1 b. 6. Trip branch from LWS N4 (511430) 138 kV to LWS-NTP4 (511471) 138 kV CKT 1 b. 7. Drop Load 1 SHERID4 (511474) 138 kV b. 8. Drop Load 1 ARTVILL4 (511538) 138 kV b. 9. Drop Load 1 53CACHE4 (511509) 138 kV b. 10. Drop Load 1 LWS N4 (511430) 138 kV b. 11. Drop Shunt 1 ARTVILL4 (511538) 138 kV b. 12. Drop Shunt 1 LWS N4 (511430) 138 kV b. 13. Trip three winding transformer from L.E.S.-4 (511467) 138 kV to L.E.S.-7 (511468) kV to LES#5-1 (511411) 13.8 kV CKT2 b. 14. Drop Shunt 1 LES#5-1 (511411) 13.8 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0378_P4 | a. Apply single phase fault at PLSNT_HILL 3 (524768) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from PLSNT_HILL 6 (524770) 230 kV to PLSNT_HILL 3 (524768) kV to PLSNHIL_TR11 (524767) 13.2 kV CKT1 b. 2. Trip branch from PLSNT_HILL 3 (524768) 115 kV to N_CLOVIS_TP3 (524776) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0379_P4 | a. Apply single phase fault at CURRY 3 (524822) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CURRY 3 (524822) 115 kV to ROOSEVELT 3 (524908) 115 kV CKT 2 b. 2. Trip branch from CURRY 3 (524822) 115 kV to NORRIS_TP 3 (524764) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0380_P4 | a. Apply single phase fault at PORTALES 3 (524924) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from ROOSEVELT 3 (524908) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 b. 2. Trip branch from OASIS 3 (524874) 115 kV to PORTALES 3 (524924) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0381_P4 | a. Apply single phase fault at NEWHART 3 (525460) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CASTRO_CNTY3 (524746) 115 kV to NEWHART 3 (525460) 115 kV CKT 1 b. 2. Trip three winding transformer from NEWHART 6 (525461) 230 kV to NEWHART 3 (525460) kV to NEWHART_TR21 (525458) 13.2 kV CKT2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0382_P4 | a. Apply single phase fault at YOAKUM 3 (526934) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from PLAINS_INT 3 (526928) 115 kV to YOAKUM 3 (526934) 115 kV CKT 1 b. 2. Trip three winding transformer from YOAKUM 6 (526935) 230 kV to YOAKUM 3 (526934) kV to YOAKUM_TR1 1 (526931) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0383_P4 | a. Apply single phase fault at LAMB_CNTY 2 (525635) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from W_LITTLFLD 2 (525613) 69 kV to LAMB_CNTY 2 (525635) 69 kV CKT 1 b. 2. Trip branch from AMHERST 2 (525606) 69 kV to W_LITTLFLD 2 (525613) 69 kV CKT 1 b. 3. Trip branch from LC-SANDHLL+2 (525599) 69 kV to AMHERST 2 (525606) 69 kV CKT 1 b. 4. Trip branch from SUDANRURAL 2 (525592) 69 kV to LC-SANDHLL+2 (525599) 69 kV CKT 1 b. 5. Drop Load 1 W_LITTLFLD 2 (525613) 69 kV b. 6. Drop Load 1 AMHERST 2 (525606) 69 kV b. 7. Drop Load 1 LC-SANDHLL+2 (525599) 69 kV b. 8. Drop Load 2 LC-SANDHLL+2 (525599) 69 kV b. 9. Drop Load 1 SUDANRURAL 2 (525592) 69 kV b. 10. Trip three winding transformer from LAMB_CNTY 3 (525636) 115 kV to LAMB_CNTY 2 (525635) kV to LAMB_TR1 1 (525631) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0384_P4 | a. Apply single phase fault at CARLISLE 3 (526160) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from CARLISLE 6 (526161) 230 kV to CARLISLE 3 (526160) kV to CRLSLE_TR1 1 (526157) 13.2 kV CKT1 b. 2. Trip branch from CARLISLE 3 (526160) 115 kV to MURPHY 3 (526192) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0385_P4 | a. Apply single phase fault at FLOYD_CNTY 3 (525780) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from FLOYD_CNTY 3 (525780) 115 kV to TUCO_INT 3 (525828) 115 kV CKT 1 b. 2. Trip three winding transformer from FLOYD_CNTY 3 (525780) 115 kV to FLOYD_CNTY 2 (525779) kV to FLOYD_TR1 1 (525777) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0386_P4 | a. Apply single phase fault at TUCO_INT 2 (525826) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from TUCO_INT 3 (525828) 115 kV to TUCO_INT 2 (525826) kV to TUCO_TR6 1 (525823) 13.2 kV CKT1 b. 2. Trip branch from TUCO_INT 2 (525826) 69 kV to SP-NEWDEAL 2 (525885) 69 kV CKT 1 b. 3. Trip branch from SP-NEWDEAL 2 (525885) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 4. Trip branch from WHITEHEAD 2 (525891) 69 kV to MONROE 2 (525892) 69 kV CKT 1 b. 5. Trip branch from WHITEHEAD 2 (525891) 69 kV to SP-SHALLWTR2 (525899) 69 kV CKT 1 b. 6. Trip branch from SP-SHALLWTR2 (525899) 69 kV to STANTON_N 2 (526073) 69 kV CKT 1 b. 7. Drop Load 1 SP-NEWDEAL 2 (525885) 69 kV b. 8. Drop Load 1 MONROE 2 (525892) 69 kV b. 9. Drop Load 1 WHITEHEAD 2 (525891) 69 kV b. 10. Drop Load SP-SHALLWTR2 (525899) 69 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0387_P4 | a. Apply single phase fault at POTTER_CO 7 (523961) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 7 (523961) 345 kV to TOLK 7 (525549) 345 kV CKT 1 b. 2. Trip branch from POTTER_CO 7 (523961) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 b. 3. Trip branch from CHISHOLM7 (511553) 345 kV to GRAPEVINE (560035) 345 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0388_P4 | a. Apply single phase fault at CROSSROADS 7 (527656) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TOLK 7 (525549) 345 kV to CROSSROADS 7 (527656) 345 kV CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV to EDDY_CNTY 7 (527802) 345 kV CKT 1 | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0389_P4 | a. Apply single phase fault at TUCO_INT 7 (525832) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 b. 2. Trip three winding transformer from TUCO_INT 7 (525832) 345 kV to TUCO_INT 6 (525830) kV to TUCO_TR1 1 (525824) 13.2 kV CKT1 b. 3. Drop Shunt 1 TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0390_P4 | a. Apply single phase fault at HITCHLAND 7 (523097) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV to CARPENTER 7 (523823) 345 kV CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV to HITCHLAND 7 (523097) 345 kV CKT 1 | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0391_P4 | a. Apply single phase fault at POTTER_CO 6 (523959) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV to HARRNG_EST 6 (523979) 230 kV CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV to ROLLHILLS 6 (524010) 230 kV CKT 1 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0392_P4 | a. Apply single phase fault at YOAKUM_345 (526936) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from YOAKUM_345 (526936) 345 kV to HOBBS_INT 7 (527896) 345 kV CKT 1 b. 2. Trip branch from TUCO_INT 7 (525832) 345 kV to YOAKUM_345 (526936) 345 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0393_P4 | a. Apply single phase fault at HOBBS_INT 3 (527891) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from HOBBS_INT 3 (527891) 115 kV to MILLEN_TPW 3 (528434) 115 kV CKT 1 b. 3. Trip branch from MILLEN_TPW 3 (528434) 115 kV to MILLEN 3 (528435) 115 kV CKT *1 b. 4. Trip branch from MILLEN 3 (528435) 115 kV to MILLEN_TPE 3 (528436) 115 kV CKT *1 b. 5. Trip branch from MILLEN_TPE 3 (528436) 115 kV to NE_HOBBS 3 (528442) 115 kV CKT 1 b. 6. Trip branch from NE_HOBBS 3 (528442) 115 kV to TAYLOR 3 (528413) 115 kV CKT 1 b. 7. Drop Load 1 MILLEN 3 (528435) 115 kV b. 8. Drop Load 1* MILLEN 3 (528435) 115 kV b. 9. Drop Load 1 NE_HOBBS 3 (528442) 115 kV | P4 | Yes | No | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0394_P4 | a. Apply single phase fault at CUNNINHAM 3 (527864) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from CUNNINHAM 3 (527864) 115 kV to BUCKEYE_TP 3 (528348) 115 kV CKT 1 b. 2. Trip branch from CUNNINHAM 3 (527864) 115 kV to QUAHADA 3 (528394) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0395_P4 | a. Apply single phase fault at MADDOX 3 (528355) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from HOBBS_INT 3 (527891) 115 kV to MADDOX 3 (528355) 115 kV CKT 1 b. 2. Trip branch from MADDOX 3 (528355) 115 kV to G18-004-TAP (762442) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0396_P4 | a. Apply single phase fault at JOHNSON_DRW3 (527362) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from JOHNSON_DRW3 (527362) 115 kV to LE-ERF 3 (528775) 115 kV CKT @1 b. 2. Trip branch from JOHNSON_DRW3 (527362) 115 kV to HIGG 3 (527363) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0397_P4 | a. Apply single phase fault at LE-LOVINTON2 (528618) 69 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-NRTH_INT3 (528334) 115 kV CKT 1 b. 2. Trip branch from LE-LOVINTON2 (528618) 69 kV to LE-DSYSRPOI2 (528677) 69 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0398_P4 | a. Apply single phase fault at DENVER_N 3 (527130) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from DENVER_N 3 (527130) 115 kV to MUSTANG 3 (527146) 115 kV CKT 1 b. 2. Trip branch from DENVER_N 3 (527130) 115 kV to HIGGEAST 3 (527286) 115 kV CKT 1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0399_P4 | a. Apply single phase fault at EDDY_NORTH 6 (527799) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from EDDY_NORTH 6 (527799) 230 kV to CUNNIGHM_N 6 (527865) 230 kV CKT 1 b. 2. Trip three winding transformer from EDDY_CNTY 7 (527802) 345 kV to EDDY_NORTH 6 (527799) kV to EDDY_TR 1 (527796) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0400_P4 | a. Apply single phase fault at POTASH_JCT 3 (527962) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from POTASH_JCT 3 (527962) 115 kV to KIOWA 3 (527966) 115 kV CKT 1 b. 2. Trip three winding transformer from KIOWA 7 (527965) 345 kV to KIOWA 3 (527966) kV to KIOWA_TR1 1 (527964) 13.2 kV CKT1 b. 3. Trip three winding transformer from POTASH_JCT 6 (527963) 230 kV to POTASH_JCT 3 (527962) kV to POTASH_TR1 1 (527958) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0401_P4 | a. Apply single phase fault at GAINES 3 (527322) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from SEMINOLE 3 (527275) 115 kV to GAINES 3 (527322) 115 kV CKT 1 b. 2. Trip branch from GAINES 3 (527322) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 3. Trip branch from OXY_WSTSEM 3 (527323) 115 kV to OXY_WSEM_TP3 (527325) 115 kV CKT 1 b. 4. Drop Load 1 OXY_WSTSEM 3 (527323) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0402_P4 | a. Apply single phase fault at HOBBS_INT 6 (527894) 230 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from HOBBS_INT 7 (527896) 345 kV to HOBBS_INT 6 (527894) kV to HOBBS_TR3 1 (527895) 13.2 kV CKT1 b. 2. Trip branch from HOBBS_INT 6 (527894) 230 kV to ANDREWS 6 (528604) 230 kV CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0403_P4 | a. Apply single phase fault at RANDALL 3 (524364) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from GEORGIA 3 (524322) 115 kV to RANDALL 3 (524364) 115 kV CKT 1 b. 2. Trip three winding transformer from RANDALL 6 (524365) 230 kV to RANDALL 3 (524364) kV to RANDAL_TR1 1 (524361) 13.2 kV CKT1 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0404_P4 | a. Apply single phase fault at COULTER 3 (524306) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from 34TH_ST_TP 3 (524281) 115 kV to COULTER 3 (524306) 115 kV CKT 1 b. 2. Trip branch from COULTER 3 (524306) 115 kV to PUCKETT 3 (524256) 115 kV CKT 1 b. 3. Trip branch from PUCKETT 3 (524256) 115 kV to SONCY_TP 3 (524252) 115 kV CKT 1 b. 4. Drop Load 1 PUCKETT 3 (524256) 115 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0405_P4 | a. Apply single phase fault at EAST_PLANT 3 (524162) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from EAST_PLANT 6 (524163) 230 kV to EAST_PLANT 3 (524162) kV to EPLANT_TR3 1 (524160) 13.2 kV CKT1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV to EAST_PLANT 6 (524163) 230 kV CKT 1 b. 3. Trip branch from EAST_PLANT 3 (524162) 115 kV to PIERCE_TP 3 (524185) 115 kV CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0406_P4 | a. Apply single phase fault at NICHOLS 3 (524043) 115 kV b. Clear Fault after 16 cycles: b. 1. Trip three winding transformer from NICHOLS 6 (524044) 230 kV to NICHOLS 3 (524043) kV to NICHOLS_TR11 (524041) 13.2 kV CKT1 b. 2. Trip branch from NICHOLS 3 (524043) 115 kV to WHITAKER 3 (524058) 115 kV CKT 1 b. 3. Trip branch from WHITAKER 3 (524058) 115 kV to EAST_PLANT 3 (524162) 115 kV CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0407_P4 | a. Apply single-phase fault at BVRCNTY7 (515554) 345 kV Bus CB 307 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 1 b. 2. Trip branch from BVRCNTY7 (515554) 345 kV Bus TO BADGER 7 (515677) 345 kV Bus CKT 2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0408_P4 | a. Apply single-phase fault at WWDBORDT (755000) 345 kV Bus CB 384 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from WWDBORDT (755000) 345 kV Bus TO BORDER 7 (515458) 345 kV Bus CKT 1 b. 2. Trip branch from BORDER 7 (515458) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0409_P4 | a. Apply single-phase fault at CARPENTER 7 (523823) 345 kV Bus CB OR335 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from CARPENTER 7 (523823) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Clear fault and Disconnect CARPENTER 7 (523823) 345 kV Bus | P4 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points)
05 - Southwest | 25W | Transfer | Group5_Fault_0410_P4 | a. Apply single-phase fault at CROSSROADS 7 (527656) 345 kV CB 6R30 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 2. Trip branch from TOLK 7 (525549) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus RSVLT_CC_E 7 (527655) 345 kV b. 4. Disconnect Bus MILO_WIND 1 (527653) 0.70 kV b. 5. Disconnect Bus RSVLT_GEN1 1 (527651) 0.69 kV b. 6. Disconnect Bus RSVLT_GEN2 1 (527652) 0.69 kV b. 7. Disconnect Bus RSVLT_CC_W 7 (527654) 345 kV b. 8. Drop Generator 1 Bus SAGSFT3_2.21 (527605) 0.70 kV b. 9. Drop Generator 1 Bus SAGSFT4_2.21 (527607) 0.70 kV b. 10. Drop Generator 1 Bus SAGSFT1_2.21 (527614) 0.70 kV b. 11. Drop Generator 1 Bus SAGSFT1_2.01 (527615) 0.70 kV b. 12. Drop Generator 1 Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Drop Generator 1 Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 15. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 17. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 18. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 19. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 20. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 21. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 22. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 23. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 24. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 25. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 26. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 27. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 28. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 29. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 30. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 31. Disconnect Bus GRDXFR1 1 (527613) 0.50 kV b. 32. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 33.Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 34. Disconnect Bus GRDXFR2 1 (527616) 0.50 kV b. 35. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 36. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 37. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 38. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 39. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 40. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 41. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 42. Disconnect Bus SUB BUS #2 (527629) 34.5 kV b. 43. Disconnect Bus CROSSROADS 7 (527656) 345 kV b. 44. Disconnect Bus RSVLT_WIND11 (527658) 34.5 kV b. 45. Disconnect Bus RSVLT_WIND21 (527659) 34.5 kV b. 46. Disconnect Bus RSVLT_COL1 1 (527660) 34.5 kV b. 47. Disconnect Bus RSVLT_COL2 1 (527661) 34.5 kV b. 48. Disconnect Bus RSVLT_TR1 1 (527662) 13.2 kV b. 49. Disconnect Bus RSVLT_TR2 1 (527663) 13.2 kV b. 50. Disconnect Bus RSVLT_COL1 7 (527666) 345 kV b. 51. Disconnect Bus RSVLT_COL2 7 (527667) 345 kV b. 52. Disconnect Bus MILO_CB (577120) 34.5 kV b. 53. Disconnect Bus MILO_WND (577121) 34.5 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0411_P4 | Apply single-phase fault at CROSSROADS 7 (527656) 345 kV Bus CB 6R45 Stuck b. Run for 21 cycles: b. 1. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO TOLK 7 (525549) 345 kV Bus CKT 1 b. 2. Trip branch from CROSSROADS 7 (527656) 345 kV Bus TO SAGA_SCOL 7 (527610) 345 kV Bus CKT 1 b. 3. Disconnect Bus SAGSFT3_2.21 (527605) 0.70 kV b. 4. Disconnect Bus GRDXFR4 1 (527606) 0.50 kV b. 5. Disconnect Bus SAGSFT4_2.21 (527607) 0.70 kV b. 6. Disconnect Bus SUB BUS #3 1 (527608) 34.5 kV b. 7. Disconnect Bus SUB BUS #4 1 (527609) 34.5 kV b. 8. Disconnect Bus GRDXFR1 1 (527613) 0.5 kV b. 9. Disconnect Bus SAGSFT1_2.21 (527614) 0.70 kV b. 10. Disconnect Bus SAGSFT1_2.01 (527615) 0.70 kV b. 11. Disconnect Bus GRDXFR2 1 (527616) 0.5 kV b. 12. Disconnect Bus SAGSFT2_2.21 (527617) 0.70 kV b. 13. Disconnect Bus SAGSFT2_2.01 (527618) 0.70 kV b. 14. Clear fault at Bus CROSSROADS 7 (527656) 345 kV b. 15. Drop Load 1 Bus SAGA_SCOL 7 (527610) 345 kV b. 16. Drop Load 2 Bus SAGA_SCOL 7 (527610) 345 kV b. 17. Disconnect Bus SAGA_NDCOL 7 (527598) 345 kV b. 18. Disconnect Bus SAGA_SDCOL 7 (527599) 345 kV b. 19. Disconnect Bus SAGA_SMEAS 7 (527600) 345 kV b. 20. Disconnect Bus SAGA_NCOL 7 (527601) 345 kV b. 21. Disconnect Bus SAGANCOL1 1 (527602) 34.5 kV b. 22. Disconnect Bus SAGANCOL2 1 (527603) 34.5 kV b. 23. Disconnect Bus GRDXFR3 1 (527604) 0.50 kV b. 24. Disconnect Bus SAGA_SCOL 7 (527610) 345 kV b. 25. Disconnect Bus SAGASCOL1 1 (527611) 34.5 kV b. 26. Disconnect Bus SAGASCOL2 1 (527612) 34.5 kV b. 27. Disconnect Bus SAGA_NCLTR31 (527621) 13.8 kV b. 28. Disconnect Bus SAGA_NCLTR41 (527622) 13.8 kV b. 29. Disconnect Bus SAGA_SCLTR11 (527623) 13.8 kV b. 30. Disconnect Bus SAGA_SCLTR21 (527624) 13.8 kV b. 31. Disconnect Bus SUB BUS #1 (527628) 34.5 kV b. 32. Disconnect Bus SUB BUS #2 (527629) 34.5 kV | P4 | No | Yes | Yes | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0412_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB 4T805 Stuck b. Clear Fault after 16 cycles: b. 1. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 3. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0413_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Run for 11 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 5. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523936 [PANTEX_WIND10.6900]
05 - Southwest | 25W | Transfer | Group5_Fault_0414_P4 | a. Apply single-phase fault at CHINA_DRAW 7 (528223) 345 kV Bus CB J27#### Stuck b. 1. Run for 16 cycles, Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO N_LOVING 7 (528185) 345 kV Bus CKT 1 b. 4. Trip branch from CHINA_DRAW 7 (528223) 345 kV Bus TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 5. Disconnect Bus CHINA_DRAW 1 (528219) 13.2 kV b. 6. Disconnect Bus CARPENTER 7 (523823) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0415_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB 4R00 Stuck b. 1. Run for 16 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 4. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0416_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB J24#### Stuck b. 1. Run for 16 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 4. Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 5. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 6. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0417_P4 | a. Apply single-phase fault at EDDY_CNTY 7 (527802) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 2. Run for 11 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO CROSSROADS 7 (527656) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from EDDY_CNTY 7 (527802) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 4. Disconnect Bus EDDY_TR 1 (527796) 13.2 kV b. 5. Disconnect Bus EDDY_CNTY 7 (527802) 345 kV | P4 | No | No | No | No | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0418_P4 | a. Apply single-phase fault at FINNEY 7 (523853) 345 kV Bus CB OR70 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOLCOMB7 (531449) 345 kV Bus TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 2. Trip branch from CARPENTER 7 (523823) 345 kV TO FINNEY 7 (523853) 345 kV Bus CKT 1 b. 3. Disconnect Bus 523853 b. 4. Disconnect Bus 599950 b. 5. Disconnect Bus 599951 b. 6. Disconnect Bus 523118 b. 7. Disconnect Bus 523114 b. 8. Disconnect Bus 523115 b. 9. Disconnect Bus 523116 b. 10. Disconnect Bus 523117 b. 11. Drop Generator 1 Bus 523061 b. 12. Drop Generator 1 Bus 523062 b. 13. Disconnect Bus 523061 b. 14. Disconnect Bus 523062 b. 15. Disconnect Bus 523063 b. 16. Disconnect Bus 523064 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0419_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus CB 1R75 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO BVRCNTY7 (515554) 345 kV Bus CKT 2 b. 2. Disconnect Bus 523112 b. 3. Disconnect Bus 523111 b. 4. Disconnect Bus 523109 b. 5. Disconnect Bus 523107 b. 6. Disconnect Bus 523110 b. 7. Drop Generator 1 Bus 523107 b. 8. Drop Load A1 Bus 523107 b. 9. Drop Generator 1 Bus 560585 b. 10. Drop Generator 1 Bus 560586 b. 11. Disconnect Bus 560577 b. 12. Disconnect Bus 560582 b. 13. Disconnect Bus 560585 b. 14. Disconnect Bus 560583 b. 15. Disconnect Bus 560586 b. 16. Disconnect Bus 560578 | P4 | Yes | Yes | Yes | No | Yes | Yes | No | Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended.
05 - Southwest | 25W | Transfer | Group5_Fault_0420_P4 | a. Apply single-phase fault at HOBBS_INT 7 (527896) 345 kV Bus CB 4R240 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO KIOWA 7 (527965) 345 kV Bus CKT 1 b. 2. Trip branch from HOBBS_INT 7 (527896) 345 kV Bus TO YOAKUM_345 (526936) 345 kV Bus CKT 1 b. 3. Disconnect Bus HOBBS_TR3 1 (527895) 13.2 kV b. 4. Disconnect Bus HOBBS_INT 7 (527896) 345 kV | P4 | Yes | No | Yes | No | Yes | Yes | No | Low voltage issues observed | Operational steady state fixes (existing caps/taps/gen set points) |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0421_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB TF#### Stuck b. 1. Run for 5 cycles, Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV b. 2. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0422_P4 | a. Apply single-phase fault at KIOWA 7 (527965) 345 kV Bus CB J23#### Stuck b. 1. Clear fault and run for 16 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 2. Disconnect Bus KIOWA_TR1 1 (527964) 13.2 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0423_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S120 Stuck b. 1. Run for 16 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | No | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0424_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 5 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Run for 11 cycles, Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0425_P4 | a. Apply single-phase fault at N_LOVING (528185) 345 kV Bus CB 4S110 Stuck b. 1. Run for 16 cycles, Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from N_LOVING (528185) 345 kV TO CHINA_DRAW 7 (528223) 345 kV Bus CKT 1 b. 4. Trip branch from N_LOVING (528185) 345 kV TO KIOWA 7 (527965) 345 kV CKT 1 b. 5. Disconnect Bus N_LOVING TR1 (528186) 13.2 kV b. 6. Disconnect Bus N_LOVING (528185) 345 kV | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763397 [G18-124-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0426_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus CB 2R05 Stuck b. Clear Fault after 21 cycles: b. 1. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 2. Disconnect bus 523957 b. 3. Disconnect bus 523957 b. 4. Disconnect bus 523961 b. 5. Disconnect bus 524296 b. 6. Disconnect bus 524299 b. 7. Disconnect bus 524298 b. 8. Disconnect bus 524294 b. 9. Disconnect bus 524295 b. 10. Disconnect bus 524297 | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0427_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J23#### Stuck b. 1. Run for 16 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0428_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB #### Stuck b. 1. Run for 5 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Run for 11 cycles, Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0429_P4 | a. Apply single-phase fault at RDRUNNER 7 (528027) 345 kV Bus CB J22#### Stuck b. 1. Run for 16 cycles, Disconnect Bus RDRNNER_TR11 (528023) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from RDRUNNER 7(528027) 345 kV TO PHANTOM 7 (528015) 345 kV Bus CKT 1 b. 4. Trip branch from KIOWA 7 (527965) 345 kV TO RDRUNNER 7 (528027) Bus CKT 1 b. 5. Disconnect Bus RDRUNNER 7(528027) 345 kV | P4 | No | No | No | Yes | No | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0430_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J18#### Stuck b. 1. Run for 16 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 2. Clear fault and run for 5 cycles, Tri branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0431_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB TF##### Stuck b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Run for 11 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 3. Clear fault and run for 5 cycles, Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0432_P4 | a. Apply single-phase fault at YOAKUM_345 (526936) 345 kV Bus CB J17#### Stuck b. 1. Run for 16 cycles, Disconnect Bus YOAKUM_TR1 (526937) 13.2 kV b. 2. Clear fault and run for 5 cycles: b. 3. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO TUCO_INT 7 (525832) 345 kV Bus CKT 1 b. 4. Trip branch from YOAKUM_345 (526936) 345 kV Bus TO HOBBS_INT 7 (527896) 345 kV Bus CKT 1 b. 5. Disconnect Bus YOAKUM_345 (526936) 345 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0433_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus CB NR20 Stuck b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0434_P4 | a. Apply single-phase fault at MUSTANG 3 (527146) 115 kV Bus b. 1. Run for 5 cycles, Disconnect Bus MUSTANG_2 1 (527162) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SEAGRAVES 3 (527202) 115 kV Bus TO MUSTANG 3 (527146) 115 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0435_P4 | a. Apply SLG fault at NICHOLS 6 (524044) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from NICHOLS (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 2. Trip branch from HUTCHISON 6 (523551) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0436_P4 | a. Apply single-phase fault at NICHOLS 6 (524044) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus NICHOLS_TR11 (524041) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus from NICHOLS_3 1 (524023) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0437_P4 | a. Apply single-phase fault at POTTER_CO 6 (523959) 230 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO BUSHLAND 6 (524267) 230 kV Bus CKT 1 b. 2. Trip branch from POTTER_CO 6 (523959) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 | P4 | No | No | No | No | Yes | No | No | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0438_P4 | a. Apply single-phase fault at YOAKUM 6 (526935) 230 kV Bus b. 1. Run for 5 cycles, Disconnect Bus YOAKUM_TR1 1 (526931) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from YOAKUM 6 (526935) 230 kV Bus TO NEEDMORE 6 (525586) 230 kV Bus CKT 1 | P4 | No | No | No | Yes | No | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0439_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR1 1 (525824) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | No |  |  |  | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0440_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. Clear Fault after 21 cycles: b. 1. Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 b. 2. Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763084 [G18-073-GEN20.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0441_P4 | a. Apply single-phase fault at TUCO_INT 7 (525832) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus TUCO_TR2 1 (525825) 13.2 kV b. 2. Clear fault and run for 11 cycles, Trip branch from TUCO_INT 7 (525832) 345 kV Bus TO CRAWFISH_DR (560022) 345 kV Bus CKT 1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0442_P4 | a. Apply single-phase fault at HITCHLAND 7 (523097) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus HITCHLD_TR01 (523091) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0443_P4 | a. Apply single-phase fault at POTTER_CO 7 (523961) 345 kV Bus b. 1. Run for 5 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 2. Clear fault and run for 11 cycles, Disconnect Bus POTTER_TR 1 (523957) 13.2 kV b. 3. Run for 5 cycles: b. 4. Trip branch from HITCHLAND 7 (523097) 345 kV Bus TO POTTER_CO 7 (523961) 345 kV Bus CKT 1 b. 5. Disconnect bus 523957 b. 6. Disconnect bus 523961 b. 7. Disconnect bus 524296 b. 8. Disconnect bus 524299 b. 9. Disconnect bus 524298 b. 10. Disconnect bus 524294 b. 11. Disconnect bus 524295 b. 12. Disconnect bus 524297 | P4 | No | No | No | No | No | No | No | Out Of Step Generators and damping issues observed | Potter to Tolk 345 kV Double Circuit Line Build Potter to Chisholm 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer Potter to Tolk 345 kV | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000], 763397 [G18-124-GEN1], 763309 [G18-112-GEN1]
05 - Southwest | 25W | Transfer | Group5_Fault_0444_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. 1. Run for 5 cycles, Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 2. Run for 11 cycles, Disconnect Bus BUSHLAND 6 (524267) 230 kV b. 3. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 4. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 5. Clear fault at BUSHLAND 6 (524267) 230 kV b. 6. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 7. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 8. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 9. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 10. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0445_P4 | a. Apply single-phase fault at SWISHER 6 (525213) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 SWISHER 6 (525213) 230 kV b. 2. Clear fault and run for 11 cycles, Trip branch from SWISHER 6 (525213) 230 kV Bus TO TUCO_INT 6 (525830) 230 kV Bus CKT 1 | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 763309 [G18-112-GEN10.6600]
05 - Southwest | 25W | Transfer | Group5_Fault_0446_P4 | a. Apply single-phase fault at TUCO_INT 6 (525830) 230 kV b. 1. Run for 5 cycles, Drop Shunt 1 TUCO_INT 6 (525830) 230 kV b. 2. Clear fault and run for 11 cycles, Disconnect BusTUCO_TR3 1 (525819) 13.2 kV | P4 | Yes | Yes | Yes | No | Yes | No | No | Damping issues observed. Low voltage ride through fails due to the tripping of G18-115-GEN10 and G18-115-GEN20 units. No cascading was observed and the issue was localized. Model tuning is recommended. | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0447_P4 | a. Apply single-phase fault at BUSHLAND 6 (524267) 230 kV Bus b. Clear Fault after 5 cycles: b. 1. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO WILDOR2_JUS6 (524290) 230 kV Bus CKT 1 b. 2. Drop Shunt 1 BUSHLAND 6 (524267) 230 kV Bus b. 3. Disconnect Bus BSHLND_TR1 1 (524263) 13.2 kV b. 4. Disconnect Bus WILDORA_GEN1 (524285) 0.69 kV b. 5. Disconnect Bus GS-PHWD_GEN1 (524287) 0.69 kV b. 6. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 7. Clear Fault after 16 cycles: b. 8. Trip branch from BUSHLAND 6 (524267) 230 kV Bus TO DEAFSMITH 6 (524623) 230 kV Bus CKT 1 b. 9. Disconnect Bus WILDOR_WND 1 (524275) 34.5 kV b. 10. Disconnect Bus WILDOR_WND 6 (524276) 230 kV b. 11. Disconnect Bus GS-PHWDRNCH1 (524289) 34.5 kV b. 12. Disconnect Bus WILDOR2_JUS6 (524290) 230 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0448_P4 | a. Apply single-phase fault at HARRNG_WST 6 (523977) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO ROLLHILLS 6 (524010) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO EAST_PLANT 6 (524163) 230 kV Bus CKT 1 b. 3. Trip branch from HARRNG_WST 6 (523977) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 1 b. 4. Disconnect Bus HARRNG_WST 6 (523977) 230 kV b. 5. Disconnect Bus HARRNGTON1 1 (523971) 24 kV | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0449_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO RANDALL 6 (524365) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_MID 6 (523978) 230 kV Bus TO NICHOLS 6 (524044) 230 kV Bus CKT 2 b. 3. Disconnect Bus HARRNG_MID 6 (523978) 230 kV b. 4. Disconnect Bus HARRNGTON2 1 (523972) 24 kV | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0450_P4 | a. Apply single-phase fault at HARRNG_EST 6 (523979) 230 kV Bus b. Clear Fault after 16 cycles: b. 1. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO PRINGLE 6 (523267) 230 kV Bus CKT 1 b. 2. Trip branch from HARRNG_EST 6 (523979) 230 kV Bus TO POTTER_CO 6 (523959) 230 kV Bus CKT 1 b. 3. Disconnect Bus HARRNG_EST 6 (523979) 230 kV b. 4. Disconnect Bus HARRNGTON3 1 (523973) 24 kV | P4 | No | Yes | Yes | Yes | Yes | No | Yes | Out Of Step Generators and damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0451_P4 | a. Apply single-phase fault at JONES 6 (526337) 230 kV b. 1. Clear fault and run for 18 cycles, Disconnect Bus from JONES 6 (526337) 230 kV b. 2. Disconnect Bus from JONES_1 1 (526331) 22 kV | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer
05 - Southwest | 25W | Transfer | Group5_Fault_0452_P4 | a. Apply single-phase fault at HARRNG_MID 6 (523978) 230 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from HARRNG_MID 6 (523978) 230 kV b. 2. Drop Generator 1 Bus 523972 b. 3. Drop Load S1 Bus 523972 b. 4. Disconnect Bus 523972 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Damping issues observed | Crawfish to Lawton Eastside 345 kV Double Circuit Line Build | Crawfish Draw 765/345kV New Substation, Crawfish Draw 765/345kV New Transformer, Crawfish Draw to Seminole 765kV New Line Double Circuit (OKGE), Crawfish Draw to Seminole 765kV New Line Double Circuit (SWPS), Seminole 765/345 New Transformer | Generator relays were disabled for the following generators: 523812 [LANOGSU10.600.6000]
05 - Southwest | 25W | Transfer | Group5_Fault_0453_P4 | a. Apply single-phase fault at MOORE_E 3 (523308) 115 kV b. 1. Clear fault and run for 5 cycles, Disconnect Bus from MOORE_E 3 (523308) 115 kV b. 2. Drop Generator 1 Bus 523297 b. 3. Drop Generator 3 Bus 523301 b. 4. Drop Load F1 Bus 523297 b. 5. Drop Load 1 Bus 523301 b. 6. Drop Load A3 Bus 523301 b. 7. Disconnect Bus 523294 b. 8. Disconnect Bus 523295 b. 9. Disconnect Bus 523296 b. 10. Disconnect Bus 523297 b. 11. Disconnect Bus 523301 b. 12. Disconnect Bus 523302 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Group5_Fault_0454_P4 | a. Apply single-phase fault at O.K.U.-7 (762467) 345 kV b. Clear Fault after 16 cycles: b. 1. Trip branch from G18-092 TAP (763215) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 b. 2. Trip branch from G17-151 (762216) 345 kV Bus TO G18-015 TAP (762467) 345 kV Bus Ckt 1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BORDER_____7__CRAWFISH_DR_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__GEN_2016_073_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2016-073 345.0 KV 587500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CACHEJ4__G20_016_TAP_7 | 3 Phase fault on CACHEJ4 (521190) 138 kV Bus a. Apply fault at the CACHEJ4 (521190) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM7__BECKHAM7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM7__POTTER_CO__7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON7__NSUB345_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRAWFISH_DR__G17_151TAP_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CRAWFISH_DR__G18_015_TAP_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CRAWFISH_DR__G18_092_PROX_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__GEN_2015_095_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2015-095 138.0 KV 585300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_7__NSUB345_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_063_TAP__GEN_2016_063_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G18_015_TAP__G18_092_PROX_6 | 3 Phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-015-TAP 345.0 KV 762467 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2017_167__GEN_2017_167_6 | 3 Phase fault on GEN-2017-167 (761859) 345 kV Bus a. Apply fault at the GEN-2017-167 (761859) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-167 345.0 KV 761859 TO GEN-2017-167 345.0 KV 761880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_016__G20_016_TAP_7 | 3 Phase fault on GEN-2020-016 (764495) 138 kV Bus a. Apply fault at the GEN-2020-016 (764495) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-016 138.0 KV 764495 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT7__GEN_2015_093_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HENESEY4__DOVERSW4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUGO___7__G16_063_TAP_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | JOHNCO_7__GEN_2020_015_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2020-015 345.0 KV 764270 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LES_7__G18_015_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-020 post-fault power less than 10% of pre-fault GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Power Plant Controller monitor branches were updated to each generator's respective collector system branch. It is recommended that generators should ensure proper plant design and model tuning. Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LES_7__G18_092_PROX_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 & GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LYDIA__7__GEN_2018_088_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2018-088 345.0 KV 763164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__JEFFRSN4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__MARSHAL4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__PIRKEY_4_7 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOONER_7__RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | MATHWSN7__TRAVERSE3_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCARBDE4__G20_092_TAP_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCARBDE4__PRY_CRK4_7 | 3 Phase fault on MCARBDE4 (510366) 138 kV Bus a. Apply fault at the MCARBDE4 (510366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCARBDE4 138.0 KV 510366 TO PRY_CRK4 138.0 KV 510431 CKT 1 b.2. LOAD 1 510431 b.3. EXCLART4 138.0 KV 510401 TO PRY_CRK4 138.0 KV 510431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCNAB_____3__TURK___3_7 | 3 Phase fault on MCNAB 3 (504122) 115 kV Bus a. Apply fault at the MCNAB 3 (504122) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCNAB 3 115.0 KV 504122 TO TURK 3 115.0 KV 507456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MDCPRK4__CACHEJ4_7 | 3 Phase fault on MDCPRK4 (520404) 138 kV Bus a. Apply fault at the MDCPRK4 (520404) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDCPRK4 138.0 KV 520404 TO CACHEJ4 138.0 KV 521190 CKT 1 b.2. MDCPRK4 138.0 KV 520404 TO PARADSE4 138.0 KV 521024 CKT 1 b.3. LOAD 1 521024 b.4. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MENOTAP4__IMO____4_7 | 3 Phase fault on MENOTAP4 (514789) 138 kV Bus a. Apply fault at the MENOTAP4 (514789) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENOTAP4 138.0 KV 514789 TO IMO 4 138.0 KV 514790 CKT 1 b.2. LOAD 1 514790 b.3. MENOTAP4 138.0 KV 514789 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MILLCKT4__SXMLCKT4_7 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MILLERT4__SOONER_4_7 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__GEN_2017_233_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__NORMHLL7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__NSUB345_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MNCWND37__MNCWND47_6 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MOORLND2__CRTSJCT2_7 | 3 Phase fault on MOORLND2 (520995) 69 kV Bus a. Apply fault at the MOORLND2 (520995) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND2 69.0 KV 520995 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MOORLND4__GEN_2016_020_7 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MORWODS4__MORWOOD4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MORWODS4__NINMLTP4_7 | 3 Phase fault on MORWODS4 (521001) 138 kV Bus a. Apply fault at the MORWODS4 (521001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORWODS4 138.0 KV 521001 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MRIETA_2__ROCKYPT4_7 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MRIETA_4__MARIETA4_7 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MTNVIEW2__MTNVWTP2_7 | 3 Phase fault on MTNVIEW2 (520490) 69 kV Bus a. Apply fault at the MTNVIEW2 (520490) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVIEW2 69.0 KV 520490 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MTNVWTP2__PINERTP2_7 | 3 Phase fault on MTNVWTP2 (521003) 69 kV Bus a. Apply fault at the MTNVWTP2 (521003) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MTNVWTP2 69.0 KV 521003 TO PINERTP2 69.0 KV 521027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUNZCTY4__DUGLASV4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUNZCTY4__WILKES_4_7 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NASH___4__ALUMAX_4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NASH___4__BANN___4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NASH___4__NWTXARK4_7 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NAVAJO_2__NAVJOTP2_7 | 3 Phase fault on NAVAJO 2 (520491) 69 kV Bus a. Apply fault at the NAVAJO 2 (520491) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NAVAJO 2 69.0 KV 520491 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEO184_5__NOL435_5_7 | 3 Phase fault on NEO184 5 (547471) 161 kV Bus a. Apply fault at the NEO184 5 (547471) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO184 5 161.0 KV 547471 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEO_SPA5__NEO184_5_7 | 3 Phase fault on NEO SPA5 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 161.0 KV 505486 TO NEO184 5 161.0 KV 547471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEWBOST2__NNBOSTN2_7 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEWGRTP2__WODWRD_2_7 | 3 Phase fault on NEWGRTP2 (514776) 69 kV Bus a. Apply fault at the NEWGRTP2 (514776) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWGRTP2 69.0 KV 514776 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE_ENID4__ENIDINT4_7 | 3 Phase fault on NE ENID4 (514769) 138 kV Bus a. Apply fault at the NE ENID4 (514769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE ENID4 138.0 KV 514769 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NINMILE4__NINMLTP4_7 | 3 Phase fault on NINMILE4 (520492) 138 kV Bus a. Apply fault at the NINMILE4 (520492) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NINMILE4 138.0 KV 520492 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NKNGFSH4__DOVERSW4_7 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN4__G18_003_TAP_7 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NOL435_2__GRA700_2_7 | 3 Phase fault on NOL435 2 (547610) 69 kV Bus a. Apply fault at the NOL435 2 (547610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL435 2 69.0 KV 547610 TO GRA700 2 69.0 KV 547617 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NOL443_2__NOL435_2_7 | 3 Phase fault on NOL443 2 (547561) 69 kV Bus a. Apply fault at the NOL443 2 (547561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOL443 2 69.0 KV 547561 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORAM__4__LONGWD_4_7 | 3 Phase fault on NORAM 4 (507774) 138 kV Bus a. Apply fault at the NORAM 4 (507774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORTWST7__ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | NORTWST7__CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | NORTWST7__SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | NWTXARK4__SUGARHL4_7 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__G20_020_TAP_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__LYDIA__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__WELSH__7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__WILKES_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWT_BNT4__G18_003_TAP_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWT_BNT4__NWTXARK4_7 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O.K.U._7__G18_092_PROX_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O.K.U._7__G20_009_TAP_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O.K.U._7__GEN_2017_033_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O.K.U._7__OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKAY___4__TURK___4_7 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__ARMFTWD4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__WOODRNG4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__WRVALLY4_7 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OVERTON4__JACKSNV4_7 | 3 Phase fault on OVERTON4 (509080) 138 kV Bus a. Apply fault at the OVERTON4 (509080) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVERTON4 138.0 KV 509080 TO JACKSNV4 138.0 KV 509242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__NWTXARK4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__SNASHVL4_7 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PCP_TAP2__PRYORC12_7 | 3 Phase fault on PCP-TAP2 (510408) 69 kV Bus a. Apply fault at the PCP-TAP2 (510408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCP-TAP2 69.0 KV 510408 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PERDUE_4__DIANA__4_7 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PERRY__4__SOONER_4_7 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PETTY__4__CHAPELH4_7 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIC4__CDRDLTP4_7 | 3 Phase fault on PIC4 (520425) 138 kV Bus a. Apply fault at the PIC4 (520425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PINTAIL7__KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__HALLSVLS4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__SABMINT4_7 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_7__DIANA__7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_7__LEBROCK7_6 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__C_RIVER7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__GEN_2018_082_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO GEN-2018-082 345.0 KV 763131 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__JOHNCO_7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | PITTSB_7__KIOWA__7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | PITTSB_7__SEMINOL7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | PITTSB_7__VALIANT7_6 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-082 trips on frequency protection settings | Disabling frequency protection settings for GEN-2018-082 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25S | Transfer | POCASET4__TUTLETP4_7 | 3 Phase fault on POCASET4 (521031) 138 kV Bus a. Apply fault at the POCASET4 (521031) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POOLVIL4__CARTRCO4_7 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__7__TOLK_______7_6 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO TOLK 7 345.0 KV 525549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRICESF4__HONEYCK4_7 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRYORC32__PRYORC12_7 | 3 Phase fault on PRYORC32 (512622) 69 kV Bus a. Apply fault at the PRYORC32 (512622) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRYORC32 69.0 KV 512622 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT2__PRYORC12_7 | 3 Phase fault on PRY-JCT2 (510400) 69 kV Bus a. Apply fault at the PRY-JCT2 (510400) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT2 69.0 KV 510400 TO PRYORC12 69.0 KV 512810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT4__G20_092_TAP_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PRY_JCT4__GEN_2017_074_7 | 3 Phase fault on PRY-JCT4 (510419) 138 kV Bus a. Apply fault at the PRY-JCT4 (510419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRY-JCT4 138.0 KV 510419 TO GEN-2017-074 138.0 KV 589120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RANCHRD7__FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RANCHRD7__G18_071_TAP_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO G18-071_TAP 345.0 KV 763069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RANCHRD7__OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RANCHRD7__OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RANDLET4__GRNDFLD4_7 | 3 Phase fault on RANDLET4 (520602) 138 kV Bus a. Apply fault at the RANDLET4 (520602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RANDLET4 138.0 KV 520602 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RATLIFF4__CARTRCO4_7 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDCLFT4__REDCLF_4_7 | 3 Phase fault on REDCLFT4 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCLFT4 138.0 KV 515533 TO REDCLF 4 138.0 KV 515863 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDHLSW4__RHWIND_4_7 | 3 Phase fault on REDHLSW4 (521116) 138 kV Bus a. Apply fault at the REDHLSW4 (521116) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDHLSW4 138.0 KV 521116 TO RHWIND 4 138.0 KV 521117 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDNGTN7__REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDSPRG4__EYLAU__4_7 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDWATR4__EYLAU__4_7 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW4__GRANTCO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW4__MDFRDTP4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW4__WFEC_RNFRO4_7 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW7__G18_128_TAP_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW7__GEN_2017_203_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW7__GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROCKYPT2__SCMMRCT2_7 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROCKYPT4__SPRNDAL4_7 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | ROMNOSE4__GEARYTP4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROMNOSE4__OMEGA__4_7 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROSVTAP2__HOBART_2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROSVTAP2__TOMSTEED2_7 | 3 Phase fault on ROSVTAP2 (511444) 69 kV Bus a. Apply fault at the ROSVTAP2 (511444) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSVTAP2 69.0 KV 511444 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSHSPR7__GEN_2015_092_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSHSPR7__GEN_2018_055_6 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | RUSHSPT4__SANTAFE4_7 | 3 Phase fault on RUSHSPT4 (511491) 138 kV Bus a. Apply fault at the RUSHSPT4 (511491) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSPT4 138.0 KV 511491 TO SANTAFE4 138.0 KV 511492 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSHSP_4__RUSHSPT4_7 | 3 Phase fault on RUSHSP 4 (511426) 138 kV Bus a. Apply fault at the RUSHSP 4 (511426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHSP 4 138.0 KV 511426 TO RUSHSPT4 138.0 KV 511491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSELL2__OMMANGM2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO OMMANGM2 69.0 KV 529342 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSELL2__VERNON_2_7 | 3 Phase fault on RUSSELL2 (521042) 69 kV Bus a. Apply fault at the RUSSELL2 (521042) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL2 69.0 KV 521042 TO VERNON 2 69.0 KV 521081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSET_4__GLASSES4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSET_4__RUSSETT4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSSET_4__STIRLNG4_7 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_AMOCO2__ROSVTAP2_7 | 3 Phase fault on R-AMOCO2 (511432) 69 kV Bus a. Apply fault at the R-AMOCO2 (511432) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R-AMOCO2 69.0 KV 511432 TO ROSVTAP2 69.0 KV 511444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SABMINT4__SABINEM4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SABMINT4__SEMRSHL4_7 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SCOTTSV4__LONGWD_4_7 | 3 Phase fault on SCOTTSV4 (508567) 138 kV Bus a. Apply fault at the SCOTTSV4 (508567) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEILING4__G20_010_TAP_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEILING4__MOORLND4_7 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL7__G17_092_TAP_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__ANADARK4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__CKSHATP4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__SEQOYAH4_7 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__NNBOSTN4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__PATTERS4_7 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SHERID4__ARTVLTP4_7 | 3 Phase fault on SHERID4 (511474) 138 kV Bus a. Apply fault at the SHERID4 (511474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SKELTON7__GEN_2016_128_6 | 3 Phase fault on SKELTON7 (515990) 345 kV Bus a. Apply fault at the SKELTON7 (515990) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SKELTON7 345.0 KV 515990 TO GEN-2016-128 345.0 KV 588190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNRPMPT4__SOONER_4_7 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_2__TIPTONJ2_7 | 3 Phase fault on SNYDER 2 (521051) 69 kV Bus a. Apply fault at the SNYDER 2 (521051) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 2 69.0 KV 521051 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_2__TOMSTEED2_7 | 3 Phase fault on SNYDER-2 (511475) 69 kV Bus a. Apply fault at the SNYDER-2 (511475) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-2 69.0 KV 511475 TO TOMSTEED2 69.0 KV 511495 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__G17_036_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__G20_012_TAP_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__G20_016_TAP_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__GEN_2015_013_7 | 3 Phase fault on SNYDER 4 (521052) 138 kV Bus a. Apply fault at the SNYDER 4 (521052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER 4 138.0 KV 521052 TO GEN-2015-013 138.0 KV 562683 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDER_4__SNYDER_4_7 | 3 Phase fault on SNYDER-4 (511435) 138 kV Bus a. Apply fault at the SNYDER-4 (511435) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDER-4 138.0 KV 511435 TO SNYDER 4 138.0 KV 521052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SNYDRSB2__NAVJOTP2_7 | 3 Phase fault on SNYDRSB2 (520541) 69 kV Bus a. Apply fault at the SNYDRSB2 (520541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNYDRSB2 69.0 KV 520541 TO NAVJOTP2 69.0 KV 521009 CKT 1 b.2. SNYDRSB2 69.0 KV 520541 TO SNYDER 2 69.0 KV 521051 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__2__CHSTNTT2_7 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2 (514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 69.0 KV 514730 TO CHSTNTT2 69.0 KV 515456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__4__BRECKNR4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__4__IMO____4_7 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOONER_4__MORISNT4_7 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOONER_7__PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SOONER_7__G16_119_TAP_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | SOONER_7__G15_066T_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SOONER_7__THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOUTHRD4__CANTNLK4_7 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO CANTNLK4 138.0 KV 515964 CKT 1 b.2. LOAD 1 515964 b.3. DEWEY 4 138.0 KV 514787 TO CANTNLK4 138.0 KV 515964 CKT 1 b.4. LOAD 1 515964 b.5. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPNKY_CK4__CATOOSA4_7 | 3 Phase fault on SPNKY CK4 (509722) 138 kV Bus a. Apply fault at the SPNKY CK4 (509722) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPNKY CK4 138.0 KV 509722 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPPMAINBUS__WELSH__7_6 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPRHILL4__DIANA__4_7 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPRNDAL4__DRPSPRG4_7 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPRNGCK7__G16_119_TAP_6 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STALOGA2__TALOGA_2_7 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. STALOGA2 69.0 KV 520454 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.3. LOAD 1 521033 b.4. HM-BTTP2 69.0 KV 520942 TO PUTNAM 2 69.0 KV 521033 CKT 1 b.5. LOAD 1 521033 b.6. ARAPAHO2 69.0 KV 520815 TO HM-BTTP2 69.0 KV 520942 CKT 1 b.7. ARAPAHO2 69.0 KV 520815 TO INDPARK2 69.0 KV 520955 CKT 1 b.8. LOAD 1 520955 b.9. WCORDELLJ2 69.0 KV 520424 TO INDPARK2 69.0 KV 520955 CKT 1 b.10. LOAD 1 520955 b.11. WCORDELLJ2 69.0 KV 520424 TO CORDELL2 69.0 KV 520866 CKT 1 b.12. LOAD 1 520866 b.13. CORDELL2 69.0 KV 520866 TO GOTEBO 2 69.0 KV 520925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STOCKHOLM2__FTSUPLY2_7 | 3 Phase fault on STOCKHOLM2 (520421) 69 kV Bus a. Apply fault at the STOCKHOLM2 (520421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STOCKHOLM2 69.0 KV 520421 TO FTSUPLY2 69.0 KV 520919 CKT 1 b.2. STOCKHOLM2 69.0 KV 520421 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__CARTRCO4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__LONEGRV4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SUNNYSD4__ROCKYPT4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__UNIROY_4_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SUNNYSD7__G16_063_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | SUNNYSD7__G20_074_TAP_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD7__GEN_2017_167_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWC414_2__NOL435_2_7 | 3 Phase fault on SWC414 2 (547428) 69 kV Bus a. Apply fault at the SWC414 2 (547428) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWC414 2 69.0 KV 547428 TO NOL435 2 69.0 KV 547610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWEETWT6__CHISHOLM6_7 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__ANADARK4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__ELSWORTH___4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__G16_097_TAP_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__NORGE__4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWS_4__WASHITA4_7 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__DIANA__7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__LONGWD_7_6 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SXMLCKT4__HOWE___4_7 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_2__VICI___2_7 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICI 2 69.0 KV 521082 TO WOODWRD2 69.0 KV 521096 CKT 1 b.2. LOAD 1 521096 b.3. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_4__G20_010_TAP_7 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4 (521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 138.0 KV 521065 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENRUSK7__CROCKET7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENRUSK7__GEN_2020_081_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO GEN-2020-081 345.0 KV 764120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENRUSK7__TENGEN_7_6 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TERRYRD7__G17_171_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 & GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TERRYRD7__G20_074_TAP_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 & GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TERRYRD7__RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | THISTLE7__GEN_2017_018_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | THISTLE7__GEN_2018_049_6 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TIPTCTY2__TIPTON_2_7 | 3 Phase fault on TIPTCTY2 (511479) 69 kV Bus a. Apply fault at the TIPTCTY2 (511479) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTCTY2 69.0 KV 511479 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TIPTE_T2__SNYDER_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO SNYDER-2 69.0 KV 511475 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TIPTE_T2__TIPTON_2_7 | 3 Phase fault on TIPTE T2 (511472) 69 kV Bus a. Apply fault at the TIPTE T2 (511472) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTE T2 69.0 KV 511472 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TIPTN_T2__TIPTON_2_7 | 3 Phase fault on TIPTN T2 (511543) 69 kV Bus a. Apply fault at the TIPTN T2 (511543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTN T2 69.0 KV 511543 TO TIPTON 2 69.0 KV 511545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TIPTON_2__TIPTONJ2_7 | 3 Phase fault on TIPTON-2 (521069) 69 kV Bus a. Apply fault at the TIPTON-2 (521069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIPTON-2 69.0 KV 521069 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TOMSTEED2__ROSEVLT2_7 | 3 Phase fault on TOMSTEED2 (511495) 69 kV Bus a. Apply fault at the TOMSTEED2 (511495) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOMSTEED2 69.0 KV 511495 TO ROSEVLT2 69.0 KV 520528 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TOTAL__4__CHIKSAW4_7 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TRAVERSE3__TRW2_TRW3_6 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TREASILD7__G20_075_TAP_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings GEN-2015-045 trips on voltage protection settings GEN-2020-009 trips on voltage protection settings | Disabling instantaneous voltage & frequency protection settings for GEN-2016-095, GEN-2015-045 & GEN-2020-009 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TREASILD7__GEN_2016_091_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-091 345.0 KV 587740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TREASILD7__GEN_2016_095_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TREASILD7__GRACMNT7_6 | 3 Phase fault on TREASILD7 (511409) 345 kV Bus a. Apply fault at the TREASILD7 (511409) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TREASILD7 345.0 KV 511409 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on frequency protection settings GEN-2015-045 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage & frequency protection settings for GEN-2016-095, GEN-2015-045, GEN-2017-171, GEN-2017-172, GEN-2017-173, GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TUCO_INT___7__CRAWFISH_DR_6 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO CRAWFISH_DR 345.0 KV 560022 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | TURK___4__MANDEVILTP4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 b.2. LOAD A1 508105 b.3. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___4__SUGARHL4_7 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c.Trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___7__NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___7__VALIANT7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUTTLE_4__TUTLETP4_7 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT7__G20_020_TAP_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT7__HUGO___7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VANCE__2__SO4TH__2_7 | 3 Phase fault on VANCE 2 (514718) 69 kV Bus a. Apply fault at the VANCE 2 (514718) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANCE 2 69.0 KV 514718 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VERDEN_4__SWS_4_7 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VINEOTP2__ESH_TP_2_7 | 3 Phase fault on VINEOTP2 (512673) 69 kV Bus a. Apply fault at the VINEOTP2 (512673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINEOTP2 69.0 KV 512673 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VINITA_2__ESH_TP_2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VINITA_2__VINTAJC2_7 | 3 Phase fault on VINITA-2 (510404) 69 kV Bus a. Apply fault at the VINITA-2 (510404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINITA-2 69.0 KV 510404 TO VINTAJC2 69.0 KV 510418 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VIOLA___7__G18_128_TAP_6 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 345.0 KV 532798 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATLANT4__CASSTP4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATLANT4__WILKES_4_7 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__CALUMET4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__OKEENE_4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__OMEGA__4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__WATONGA4_7 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOMI4__WAUKOTP4_7 | 3 Phase fault on WAUKOMI4 (514710) 138 kV Bus a. Apply fault at the WAUKOMI4 (514710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 b.2. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOTP4__SO4TH__4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOTP4__WOODRNG4_7 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__SAPLPRD7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__SOONER_7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__T.NO.__7_6 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WELSH__7__DIANA__7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WELSH__7__WILKES_7_6 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WHITNEY4__EASTEX_4_7 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WINDFRM4__FPLWIND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO FPLWIND4 138.0 KV 515786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WINDFRM4__MOORLND4_7 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WODWRD_2__WOODWRD2_7 | 3 Phase fault on WODWRD 2 (514782) 69 kV Bus a. Apply fault at the WODWRD 2 (514782) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WODWRD 2 69.0 KV 514782 TO WOODWRD2 69.0 KV 521096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOLFCRK4__CHEEKTP4_7 | 3 Phase fault on WOLFCRK4 (515143) 138 kV Bus a. Apply fault at the WOLFCRK4 (515143) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG4__MARSHL_4_7 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__GEN_2017_164_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__GEN_2020_023_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2020-023 345.0 KV 764525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__HUNTERS7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__PINTAIL7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__REDNGTN7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__SKELTON7_6 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD2__CRTSJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD2__FARGOJCT2_7 | 3 Phase fault on WOODWRD2 (521096) 69 kV Bus a. Apply fault at the WOODWRD2 (521096) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD2 69.0 KV 521096 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD4__CENT___4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO CENT 4 138.0 KV 515363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD4__WINDFRM4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WINDFRM4 138.0 KV 515785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD4__WWRDEHV4_7 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WRVALLY4__WARREN_4_7 | 3 Phase fault on WRVALLY4 (514713) 138 kV Bus a. Apply fault at the WRVALLY4 (514713) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRVALLY4 138.0 KV 514713 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4__KEENAN_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4__OUSPRT_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4__WWDPST_4_7 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__BECKHAM7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__BOBCAT_7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BOBCAT 7 345.0 KV 516106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__BVRCNTY7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO BVRCNTY7 345.0 KV 515554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__DGRASSE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__G07621119_20_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__GEN_2019_012_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GEN-2019-012 345.0 KV 763527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__GUTHRIE7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7__TATONGA7_6 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 112GORE4__LAIRGST4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 112GORE4__RPPAPER4_7 | 3 Phase fault on 112GORE4 (511488) 138 kV Bus a. Apply fault at the 112GORE4 (511488) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 112GORE4 138.0 KV 511488 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2ESHOSP__ESH_TP_2_7 | 3 Phase fault on 2ESHOSP (301468) 69 kV Bus a. Apply fault at the 2ESHOSP (301468) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ESHOSP 69.0 KV 301468 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2GROVNEO__COWSKIN2_7 | 3 Phase fault on 2GROVNEO (301457) 69 kV Bus a. Apply fault at the 2GROVNEO (301457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GROVNEO 69.0 KV 301457 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2TURKEY__COWSKIN2_7 | 3 Phase fault on 2TURKEY (301463) 69 kV Bus a. Apply fault at the 2TURKEY (301463) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEY 69.0 KV 301463 TO COWSKIN2 69.0 KV 512717 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2VINITAHQ__ESH_TP_2_7 | 3 Phase fault on 2VINITAHQ (300983) 69 kV Bus a. Apply fault at the 2VINITAHQ (300983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VINITAHQ 69.0 KV 300983 TO ESH TP 2 69.0 KV 512680 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4COLSTTA__4GRIMES_7 | 3 Phase fault on 4COLSTTA% (334021) 138 kV Bus a. Apply fault at the 4COLSTTA% (334021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4COLSTTA% 138.0 KV 334021 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4GRIMES__4BENTWATER_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4BENTWATER! 138.0 KV 334039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4GRIMES__4MT.ZION_7 | 3 Phase fault on 4GRIMES% (334026) 138 kV Bus a. Apply fault at the 4GRIMES% (334026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4GRIMES% 138.0 KV 334026 TO 4MT.ZION 138.0 KV 334060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4MAG_AND__4GRIMES_7 | 3 Phase fault on 4MAG AND (334025) 138 kV Bus a. Apply fault at the 4MAG AND (334025) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MAG AND 138.0 KV 334025 TO 4GRIMES% 138.0 KV 334026 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 6GRIMES__6PONDEROSA_7 | 3 Phase fault on 6GRIMES! (334027) 230 kV Bus a. Apply fault at the 6GRIMES! (334027) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6GRIMES! 230.0 KV 334027 TO 6PONDEROSA! 230.0 KV 334088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7GRIMES__7FRONTR_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7FRONTR 345.0 KV 334029 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7GRIMES__7ROCKYCRK_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO 7ROCKYCRK% 345.0 KV 334197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7GRIMES__CROCKET7_6 | 3 Phase fault on 7GRIMES% (334028) 345 kV Bus a. Apply fault at the 7GRIMES% (334028) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7GRIMES% 345.0 KV 334028 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7SAREPTA__7EL_DORADO_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7SAREPTA__LONGWD_7_6 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ADAIR__2__PRY_JCT2_7 | 3 Phase fault on ADAIR--2 (510387) 69 kV Bus a. Apply fault at the ADAIR--2 (510387) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADAIR--2 69.0 KV 510387 TO PRY-JCT2 69.0 KV 510400 CKT 1 b.2. LOAD 1 510400 b.3. ADAIR--2 69.0 KV 510387 TO VINITA-2 69.0 KV 510404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALINETP2__CLEOTP_2_7 | 3 Phase fault on ALINETP2 (515803) 69 kV Bus a. Apply fault at the ALINETP2 (515803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINETP2 69.0 KV 515803 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALINE__2__ALINETP2_7 | 3 Phase fault on ALINE 2 (514793) 69 kV Bus a. Apply fault at the ALINE 2 (514793) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALINE 2 69.0 KV 514793 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSAF2__ALTUSSW2_7 | 3 Phase fault on ALTUSAF2 (520804) 69 kV Bus a. Apply fault at the ALTUSAF2 (520804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSAF2 69.0 KV 520804 TO ALTUSSW2 69.0 KV 520805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSJT2__TIPTN_T2_7 | 3 Phase fault on ALTUSJT2 (511441) 69 kV Bus a. Apply fault at the ALTUSJT2 (511441) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT2 69.0 KV 511441 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSJT4__G20_012_TAP_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSJT4__RUSSELL4_7 | 3 Phase fault on ALTUSJT4 (511440) 138 kV Bus a. Apply fault at the ALTUSJT4 (511440) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSJT4 138.0 KV 511440 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUSSW2__NAVJOTP2_7 | 3 Phase fault on ALTUSSW2 (520805) 69 kV Bus a. Apply fault at the ALTUSSW2 (520805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUSSW2 69.0 KV 520805 TO NAVJOTP2 69.0 KV 521009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALTUS__2__ALTUSSW2_7 | 3 Phase fault on ALTUS_ 2 (520803) 69 kV Bus a. Apply fault at the ALTUS_ 2 (520803) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTUS_ 2 69.0 KV 520803 TO ALTUSSW2 69.0 KV 520805 CKT 1 b.2. ALTUS_ 2 69.0 KV 520803 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ALVAOGE2__ALINETP2_7 | 3 Phase fault on ALVAOGE2 (514792) 69 kV Bus a. Apply fault at the ALVAOGE2 (514792) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALVAOGE2 69.0 KV 514792 TO ALINETP2 69.0 KV 515803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK2__CADDO__2_7 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK4__CHERRYRD_4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK4__GEORGIA4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK4__POCASET4_7 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANDRSNC4__BRYANML4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANDRSNC4__RIFFIN_REC4_7 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARBWIND4__HONEYCK4_7 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARCADIA7__SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARTVLTP4__ARTVILL4_7 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASHDWNR4__OKAY___4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASHDWNR4__PATTERS4_7 | 3 Phase fault on ASHDWNR4 (507402) 138 kV Bus a. Apply fault at the ASHDWNR4 (507402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASHDWN_W__4__PATTERS4_7 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASPEN__4__BEARCAT4_7 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO BEARCAT4 138.0 KV 520500 CKT 1 b.2. LOAD 1 520500 b.3. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 b.4. BEARCAT4 138.0 KV 520500 TO NINMLTP4 138.0 KV 521128 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__KINGHWY2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__LSORDTP2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__REDLICK2_7 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___4__NWT_BNT4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___4__REDSPRG4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___4__SETEXAR4_7 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BCV_SW_4__CHERRYRD_4_7 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BEAVERJ2__FTSUPLY2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BEAVERJ2__SPERMOR2_7 | 3 Phase fault on BEAVERJ2 (520825) 69 kV Bus a. Apply fault at the BEAVERJ2 (520825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVERJ2 69.0 KV 520825 TO SPERMOR2 69.0 KV 521054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BEAVER_2__BEAVERJ2_7 | 3 Phase fault on BEAVER 2 (520824) 69 kV Bus a. Apply fault at the BEAVER 2 (520824) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEAVER 2 69.0 KV 520824 TO BEAVERJ2 69.0 KV 520825 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BIRDHOL4__PRY_JCT4_7 | 3 Phase fault on BIRDHOL4 (510398) 138 kV Bus a. Apply fault at the BIRDHOL4 (510398) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BIRDHOL4 138.0 KV 510398 TO PRY-JCT4 138.0 KV 510419 CKT 1 b.2. BIRDHOL4 138.0 KV 510398 TO JAY 4 138.0 KV 510421 CKT 1 b.3. LOAD 1 510421 b.4. GROVE 4 138.0 KV 510402 TO JAY 4 138.0 KV 510421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BORDER_____7__BECKHAM7_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BORDER_____7__CRAWFISH_DR_6 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO CRAWFISH_DR 345.0 KV 560022 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRANDYBR__EASTON_4_7 | 3 Phase fault on BRANDYBR (508596) 138 kV Bus a. Apply fault at the BRANDYBR (508596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRANTLEY4__MORWOOD4_7 | 3 Phase fault on BRANTLEY4 (520832) 138 kV Bus a. Apply fault at the BRANTLEY4 (520832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRANTLEY4 138.0 KV 520832 TO MORWOOD4 138.0 KV 521002 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRCKWND4__BRECKNR4_7 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRECKNR4__ENIDINT4_7 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRIDGCR4__TUTLETP4_7 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRYANML4__MUNZCTY4_7 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BTLRJCT2__MORWODS2_7 | 3 Phase fault on BTLRJCT2 (520457) 69 kV Bus a. Apply fault at the BTLRJCT2 (520457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BTLRJCT2 69.0 KV 520457 TO MORWODS2 69.0 KV 521000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO2__BUFBEAR2_7 | 3 Phase fault on BUFFALO2 (520835) 69 kV Bus a. Apply fault at the BUFFALO2 (520835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFFALO2 69.0 KV 520835 TO BUFBEAR2 69.0 KV 521120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__GEN_2016_073_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2016-073 345.0 KV 587500 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__GEN_2017_220_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__THISTLE7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BULFOOT4__BULFTTP4_7 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BULFTTP4__DOVERSW4_7 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUNCHCK4__BRECKNR4_7 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CACHE4__INDHOMA4_7 | 3 Phase fault on CACHE4 (520410) 138 kV Bus a. Apply fault at the CACHE4 (520410) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 520410 TO INDHOMA4 138.0 KV 520954 CKT 1 b.2. LOAD 1 520954 b.3. CACHE4 138.0 KV 520410 TO CACHEJ4 138.0 KV 521190 CKT 1 b.4. INDHOMA4 138.0 KV 520954 TO GRNDFLD4 138.0 KV 521106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CACHE4__LAIRGST4_7 | 3 Phase fault on CACHE4 (511500) 138 kV Bus a. Apply fault at the CACHE4 (511500) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHE4 138.0 KV 511500 TO LAIRGST4 138.0 KV 511510 CKT 1 b.2. CACHE4 138.0 KV 511500 TO G17-036_TAP 138.0 KV 588779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CACHEJ4__G20_016_TAP_7 | 3 Phase fault on CACHEJ4 (521190) 138 kV Bus a. Apply fault at the CACHEJ4 (521190) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CACHEJ4 138.0 KV 521190 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANEYCK4__LTLCITY4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANEYCK4__TEXOMAJ4_7 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANTON_2__TALOGA_2_7 | 3 Phase fault on CANTON-2 (520843) 69 kV Bus a. Apply fault at the CANTON-2 (520843) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 b.2. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARNEG_4__HOB_JCT4_7 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO HOB-JCT4 138.0 KV 511463 CKT 1 b.2. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTERJ2__LKCREEK2_7 | 3 Phase fault on CARTERJ2 (520846) 69 kV Bus a. Apply fault at the CARTERJ2 (520846) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTERJ2 69.0 KV 520846 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTER_4__CHIKSAW4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTER_4__HONEYCK4_7 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTRCO4__GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTRCO4__ORIGINW4_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CATOOSA4__LLANETP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CATOOSA4__OWAS88_4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO OWAS88_4 138.0 KV 509887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CATOOSA4__PCATSAT4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO PCATSAT4 138.0 KV 509841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CATOOSA4__TERNITP4_7 | 3 Phase fault on CATOOSA4 (509790) 138 kV Bus a. Apply fault at the CATOOSA4 (509790) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATOOSA4 138.0 KV 509790 TO TERNITP4 138.0 KV 509835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CDRDLTP4__OKEENE_4_7 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CEDARAV2__WODWRD_2_7 | 3 Phase fault on CEDARAV2 (514781) 69 kV Bus a. Apply fault at the CEDARAV2 (514781) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARAV2 69.0 KV 514781 TO WODWRD 2 69.0 KV 514782 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CEDRDAL4__CDRDLTP4_7 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAPELH4__CHAPLHL4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAPELH4__WELSHRE4_7 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 b.2. LOAD 1 508355 b.3. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHEEKTP4__CHEEK_4_7 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CHILD4WT__HOLTP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO HOLTP4WT 138.0 KV 512103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHILD4WT__LAKEP4WT_7 | 3 Phase fault on CHILD4WT (512101) 138 kV Bus a. Apply fault at the CHILD4WT (512101) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHILD4WT 138.0 KV 512101 TO LAKEP4WT 138.0 KV 512110 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM7__BECKHAM7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO BECKHAM7 345.0 KV 516059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM7__G16_037_TAP_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM7__POTTER_CO__7_6 | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHOUTEA4__EXCLART4_7 | 3 Phase fault on CHOUTEA4 (510373) 138 kV Bus a. Apply fault at the CHOUTEA4 (510373) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEA4 138.0 KV 510373 TO EXCLART4 138.0 KV 510401 CKT 1 b.2. CHOUTEA4 138.0 KV 510373 TO ROCKPT-4 138.0 KV 510437 CKT 1 b.3. LOAD 1 510437 b.4. INOLATP4 138.0 KV 509752 TO ROCKPT-4 138.0 KV 510437 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25S | Transfer | NORTWST7__MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CIMARON7__NORMHLL7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NORMHLL7 345.0 KV 516096 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__NSUB345_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__G16_046_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G16-046-TAP 345.0 KV 560080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__G19_030_TAP_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO G19-030-TAP 345.0 KV 763677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__GEN_2011_008_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2011-008 345.0 KV 539840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__GEN_2019_058_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO GEN-2019-058 345.0 KV 763890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__THISTLE7_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__TRANSFORMER_6 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO TRANSFORMER 345.0 KV 539813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR2__CLEOSW_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOSW 2 69.0 KV 520855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR2__CLEOTP_2_7 | 3 Phase fault on CLEOCOR2 (514777) 69 kV Bus a. Apply fault at the CLEOCOR2 (514777) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR2 69.0 KV 514777 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR4__CLEOPLT4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR4__GLASMTN4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO GLASMTN4 138.0 KV 514788 CKT 1 b.2. LOAD 1 514788 b.3. LOAD 2 514788 b.4. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOCOR4__SUNDANC4_7 | 3 Phase fault on CLEOCOR4 (514778) 138 kV Bus a. Apply fault at the CLEOCOR4 (514778) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 138.0 KV 514778 TO SUNDANC4 138.0 KV 516025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOSW_2__RNGWODJ2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEOSW_2__RNGWOOD2_7 | 3 Phase fault on CLEOSW 2 (520855) 69 kV Bus a. Apply fault at the CLEOSW 2 (520855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOSW 2 69.0 KV 520855 TO RNGWOOD2 69.0 KV 521040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEO_PL4__CLEOPLT4_7 | 3 Phase fault on CLEO PL4 (515553) 138 kV Bus a. Apply fault at the CLEO PL4 (515553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO PL4 138.0 KV 515553 TO CLEOPLT4 138.0 KV 515562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEO___2__CLEOTP_2_7 | 3 Phase fault on CLEO 2 (514791) 69 kV Bus a. Apply fault at the CLEO 2 (514791) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEO 2 69.0 KV 514791 TO CLEOTP 2 69.0 KV 515804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEVETP2__SO4TH__2_7 | 3 Phase fault on CLEVETP2 (514722) 69 kV Bus a. Apply fault at the CLEVETP2 (514722) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEVETP2 69.0 KV 514722 TO SO4TH 2 69.0 KV 514730 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLEVLND7__G15_066T_6 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__AMBERTP4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__ANADARK4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__COGAR__4_7 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CL_AFTP4__CLIN_AF4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO CLIN-AF4 138.0 KV 511535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CL_AFTP4__ELKCTY_4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO ELKCTY-4 138.0 KV 511458 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CL_AFTP4__HOB_JCT4_7 | 3 Phase fault on CL-AFTP4 (511446) 138 kV Bus a. Apply fault at the CL-AFTP4 (511446) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CL-AFTP4 138.0 KV 511446 TO HOB-JCT4 138.0 KV 511463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMANC_2__LES_2_7 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMANC_4__112GORE4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMANC_4__COMMTAP4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMANC_4__LES_4_7 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMMTAP4__OMDUNCN4_7 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COWCRK_4__MORRISN4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO MORRISN4 138.0 KV 515006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COWCRK_4__PERRY__4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO PERRY 4 138.0 KV 514707 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COWCRK_4__WRVALLY4_7 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CRAWFISH_DR__G17_151TAP_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CRAWFISH_DR__G18_015_TAP_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CRAWFISH_DR__G18_092_PROX_6 | 3 Phase fault on CRAWFISH_DR (560022) 345 kV Bus a. Apply fault at the CRAWFISH_DR (560022) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAWFISH_DR 345.0 KV 560022 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-068 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2020-068 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | CTNWOOD4__ARCADIA4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__CRESENT4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__LBRTYLK4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__PINE_ST4_7 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CURTIS_2__CRTSJCT2_7 | 3 Phase fault on CURTIS 2 (520480) 69 kV Bus a. Apply fault at the CURTIS 2 (520480) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CURTIS 2 69.0 KV 520480 TO CRTSJCT2 69.0 KV 521197 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | C_RIVER7__G17_092_TAP_6 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO G17-092-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DAV_TAP2__DAVDSON2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO DAVDSON2 69.0 KV 511521 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DAV_TAP2__VRNMTAP2_7 | 3 Phase fault on DAV TAP2 (511520) 69 kV Bus a. Apply fault at the DAV TAP2 (511520) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAV TAP2 69.0 KV 511520 TO VRNMTAP2 69.0 KV 512113 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEC392_5__NOL435_5_7 | 3 Phase fault on DEC392 5 (547484) 161 kV Bus a. Apply fault at the DEC392 5 (547484) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEC392 5 161.0 KV 547484 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEWEY__4__REDCLFT4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEWEY__4__TALOGA_4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TALOGA 4 138.0 KV 521065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEWEY__4__TLGAWND4_7 | 3 Phase fault on DEWEY 4 (514787) 138 kV Bus a. Apply fault at the DEWEY 4 (514787) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 138.0 KV 514787 TO TLGAWND4 138.0 KV 515390 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__GEN_2015_095_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2015-095 138.0 KV 585300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__GEN_2019_045_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2019-045 138.0 KV 763769 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__MOORLND4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__ROSEVLY4_7 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE7__THISTLE7_6 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__DIANASW4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__NGPLTAP4_7 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOLHILL7__SW_SHV_7_6 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__GEN_2016_118_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__GEN_2018_011_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__OKEENE_4_7 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVER__4__DOVERSW4_7 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_7__NORMHLL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NORMHLL7 345.0 KV 516096 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_7__NSUB345_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_7__SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUKE___2__GYPSUM_2_7 | 3 Phase fault on DUKE 2 (520534) 69 kV Bus a. Apply fault at the DUKE 2 (520534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE 2 69.0 KV 520534 TO GYPSUM 2 69.0 KV 520929 CKT 1 b.2. LOAD 1 520929 b.3. DUKE 2 69.0 KV 520534 TO RUSSELL2 69.0 KV 521042 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUKE___2__RUSSELL2_7 | 3 Phase fault on DUKE---2 (511438) 69 kV Bus a. Apply fault at the DUKE---2 (511438) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUKE---2 69.0 KV 511438 TO RUSSELL2 69.0 KV 521042 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUNCAN_2__DUNTOS_TP2_7 | 3 Phase fault on DUNCAN-2 (511452) 69 kV Bus a. Apply fault at the DUNCAN-2 (511452) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-2 69.0 KV 511452 TO DUNTOS TP2 69.0 KV 511457 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUNCAN_4__DUNCHERTP4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.2. LOAD 1 511552 b.3. D.E.S.-4 138.0 KV 511455 TO DUNCHERTP4 138.0 KV 511552 CKT 1 b.4. LOAD 1 511552 b.5. D.E.S.-4 138.0 KV 511455 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.6. LOAD 1 529344 b.7. LOAD 2 529344 b.8. OMMARLO4 138.0 KV 529307 TO OMDUNE-4 138.0 KV 529344 CKT 1 b.9. LOAD 1 529344 b.10. LOAD 2 529344 b.11. RUSHSPT4 138.0 KV 511491 TO OMMARLO4 138.0 KV 529307 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUNCAN_4__OMDUNCN4_7 | 3 Phase fault on DUNCAN-4 (511453) 138 kV Bus a. Apply fault at the DUNCAN-4 (511453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN-4 138.0 KV 511453 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELDORDJ2__GYPSUM_2_7 | 3 Phase fault on ELDORDJ2 (520895) 69 kV Bus a. Apply fault at the ELDORDJ2 (520895) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELDORDJ2 69.0 KV 520895 TO GYPSUM 2 69.0 KV 520929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELGINJT4__ELSWORTH___4_7 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCITY6__CHISHOLM6_7 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_4__CLINTJC4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO CLINTJC4 138.0 KV 511485 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_4__FALCNRD4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO FALCNRD4 138.0 KV 511511 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_4__REDHLSW4_7 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4 (511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 138.0 KV 511458 TO REDHLSW4 138.0 KV 521116 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELLIS__4__CUSTER_4_7 | 3 Phase fault on ELLIS 4 (511561) 138 kV Bus a. Apply fault at the ELLIS 4 (511561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLIS 4 138.0 KV 511561 TO CUSTER 4 138.0 KV 520459 CKT 1 b.2. LOAD 1 520459 b.3. CUSTER 4 138.0 KV 520459 TO REDHLSW4 138.0 KV 521116 CKT 1 b.4. ELLIS 4 138.0 KV 511561 TO MORWODS4 138.0 KV 521001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO4__CIMARON4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO4__JENSENT4_7 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EMPIRE_4__FLETCH_4_7 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ENID___2__SO4TH__2_7 | 3 Phase fault on ENID 2 (514727) 69 kV Bus a. Apply fault at the ENID 2 (514727) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENID 2 69.0 KV 514727 TO SO4TH 2 69.0 KV 514730 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EXCLART4__EXPCLAR4_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO EXPCLAR4 138.0 KV 510405 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EXCLART4__GEN_2017_077_7 | 3 Phase fault on EXCLART4 (510401) 138 kV Bus a. Apply fault at the EXCLART4 (510401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXCLART4 138.0 KV 510401 TO GEN-2017-077 138.0 KV 589150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EYLAU__4__BUCHANN4_7 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRMON4__PLNSMEN4_7 | 3 Phase fault on FAIRMON4 (514712) 138 kV Bus a. Apply fault at the FAIRMON4 (514712) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__OKEENE_2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__OMFAIRV2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__RNGWODJ2_7 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FARGO__2__FARGOJCT2_7 | 3 Phase fault on FARGO 2 (520910) 69 kV Bus a. Apply fault at the FARGO 2 (520910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 2 69.0 KV 520910 TO FARGOJCT2 69.0 KV 521196 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLETCHR4__FLE_TAP4_7 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLETCH_4__GEORGIA4_7 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4 (520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLE_TAP4__G16_097_TAP_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLE_TAP4__LES_4_7 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLINTCR5__DEC392_5_7 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO DEC392 5 161.0 KV 547484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FNDTION4__CHIKSAW4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FNDTION4__SPRNDAL4_7 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FREDJC_2__TIPTE_T2_7 | 3 Phase fault on FREDJC-2 (511460) 69 kV Bus a. Apply fault at the FREDJC-2 (511460) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDJC-2 69.0 KV 511460 TO TIPTE T2 69.0 KV 511472 CKT 1 b.2. FREDJC-2 69.0 KV 511460 TO DAV TAP2 69.0 KV 511520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FREDRIK2__HOLLSTR2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FREDRIK2__OMFRDFK_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO OMFRDFK 69.0 KV 529340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FREDRIK2__TIPTONJ2_7 | 3 Phase fault on FREDRIK2 (520914) 69 kV Bus a. Apply fault at the FREDRIK2 (520914) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREDRIK2 69.0 KV 520914 TO TIPTONJ2 69.0 KV 521070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4__SO4TH__4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4__WOODRNG4_7 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSPLY_2__FARGOJCT2_7 | 3 Phase fault on FTSPLY 2 (520456) 69 kV Bus a. Apply fault at the FTSPLY 2 (520456) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSPLY 2 69.0 KV 520456 TO FARGOJCT2 69.0 KV 521196 CKT 1 b.2. FTSPLY 2 69.0 KV 520456 TO FTSUPLY2 69.0 KV 520919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSUPLY4__IODINE_4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO IODINE 4 138.0 KV 520957 CKT 1 b.2. LOAD 1 520957 b.3. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSUPLY4__SLEEPBR4_7 | 3 Phase fault on FTSUPLY4 (520920) 138 kV Bus a. Apply fault at the FTSUPLY4 (520920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 138.0 KV 520920 TO SLEEPBR4 138.0 KV 520922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G15_066T__GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_037_TAP__GEN_2016_037_6 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_063_TAP__GEN_2016_063_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_063_TAP__GEN_2017_075_6 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_119_TAP__GEN_2016_119_6 | 3 Phase fault on G16-119-TAP (587804) 345 kV Bus a. Apply fault at the G16-119-TAP (587804) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-119-TAP 345.0 KV 587804 TO GEN-2016-119 345.0 KV 587950 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_036_TAP__GEN_2017_036_7 | 3 Phase fault on G17-036_TAP (588779) 138 kV Bus a. Apply fault at the G17-036_TAP (588779) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-036_TAP 138.0 KV 588779 TO GEN-2017-036 138.0 KV 588780 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_151TAP__G18_015_TAP_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_151TAP__GEN_2017_151_6 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_171_TAP__GEN_2017_171_6 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G18_015_TAP__G18_092_PROX_6 | 3 Phase fault on G18-015-TAP (762467) 345 kV Bus a. Apply fault at the G18-015-TAP (762467) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G18-015-TAP 345.0 KV 762467 TO G18-092-PROX 345.0 KV 763215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G20_075_TAP__GEN_2020_087_6 | 3 Phase fault on G20-075-TAP (764550) 345 kV Bus a. Apply fault at the G20-075-TAP (764550) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G20-075-TAP 345.0 KV 764550 TO GEN-2020-087 345.0 KV 764555 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G20_087_GSU1__G20_087_XFM1_7 | 3 Phase fault on G20-087-GSU1 (764557) 34.5 kV Bus a. Apply fault at the G20-087-GSU1 (764557) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU1 34.5 KV 764557 TO G20-087-XFM1 34.5 KV 764558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G20_087_GSU2__G20_087_XFM2_7 | 3 Phase fault on G20-087-GSU2 (764560) 34.5 kV Bus a. Apply fault at the G20-087-GSU2 (764560) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G20-087-GSU2 34.5 KV 764560 TO G20-087-XFM2 34.5 KV 764561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GARBER_4__WARREN_4_7 | 3 Phase fault on GARBER 4 (520461) 138 kV Bus a. Apply fault at the GARBER 4 (520461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARBER 4 138.0 KV 520461 TO WARREN 4 138.0 KV 521100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEARYTP4__GEARY__4_7 | 3 Phase fault on GEARYTP4 (515931) 138 kV Bus a. Apply fault at the GEARYTP4 (515931) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARYTP4 138.0 KV 515931 TO GEARY 4 138.0 KV 520460 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2017_150__GEN_2017_233_6 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2017_167__GEN_2017_167_6 | 3 Phase fault on GEN-2017-167 (761859) 345 kV Bus a. Apply fault at the GEN-2017-167 (761859) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-167 345.0 KV 761859 TO GEN-2017-167 345.0 KV 761880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2018_003__G18_003_TAP_7 | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2018_015__G18_015_TAP_6 | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2018_128__G18_128_TAP_6 | 3 Phase fault on GEN-2018-128 (763417) 345 kV Bus a. Apply fault at the GEN-2018-128 (763417) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-128 345.0 KV 763417 TO G18-128-TAP 345.0 KV 763421 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_009__G20_009_TAP_6 | 3 Phase fault on GEN-2020-009 (766290) 345 kV Bus a. Apply fault at the GEN-2020-009 (766290) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-009 345.0 KV 766290 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_010__G20_010_SS1_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-SS1 138.0 KV 765212 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_010__G20_010_TAP_7 | 3 Phase fault on GEN-2020-010 (765205) 138 kV Bus a. Apply fault at the GEN-2020-010 (765205) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-010 138.0 KV 765205 TO G20-010-TAP 138.0 KV 765215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_012__G20_012_SS1_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-SS1 138.0 KV 765231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_012__G20_012_TAP_7 | 3 Phase fault on GEN-2020-012 (765220) 138 kV Bus a. Apply fault at the GEN-2020-012 (765220) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-012 138.0 KV 765220 TO G20-012-TAP 138.0 KV 765230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_016__G20_016_TAP_7 | 3 Phase fault on GEN-2020-016 (764495) 138 kV Bus a. Apply fault at the GEN-2020-016 (764495) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-016 138.0 KV 764495 TO G20-016-TAP 138.0 KV 764505 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_020__G20_020_TAP_6 | 3 Phase fault on GEN-2020-020 (764510) 345 kV Bus a. Apply fault at the GEN-2020-020 (764510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-020 345.0 KV 764510 TO G20-020-TAP 345.0 KV 764520 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_074__G20_074_TAP_6 | 3 Phase fault on GEN-2020-074 (764105) 345 kV Bus a. Apply fault at the GEN-2020-074 (764105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-074 345.0 KV 764105 TO G20-074-TAP 345.0 KV 764115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_075__G20_075_TAP_6 | 3 Phase fault on GEN-2020-075 (764540) 345 kV Bus a. Apply fault at the GEN-2020-075 (764540) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2020-075 345.0 KV 764540 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2020_092__G20_092_TAP_7 | 3 Phase fault on GEN-2020-092 (764150) 138 kV Bus a. Apply fault at the GEN-2020-092 (764150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2020-092 138.0 KV 764150 TO G20-092-TAP 138.0 KV 764160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEROJCT2__GRANFLD2_7 | 3 Phase fault on GEROJCT2 (520506) 69 kV Bus a. Apply fault at the GEROJCT2 (520506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEROJCT2 69.0 KV 520506 TO GRANFLD2 69.0 KV 520926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GLENWD_4__IMO____4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GLENWD_4__NE_ENID4_7 | 3 Phase fault on GLENWD 4 (514734) 138 kV Bus a. Apply fault at the GLENWD 4 (514734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLENWD 4 138.0 KV 514734 TO NE ENID4 138.0 KV 514769 CKT 1 b.2. LOAD 1 514769 b.3. GLENWD 4 138.0 KV 514734 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GOTEBO_2__LONEWLF2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GOTEBO_2__LTELKSW2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO LTELKSW2 69.0 KV 521137 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GOTEBO_2__MTNVWTP2_7 | 3 Phase fault on GOTEBO 2 (520925) 69 kV Bus a. Apply fault at the GOTEBO 2 (520925) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOTEBO 2 69.0 KV 520925 TO MTNVWTP2 69.0 KV 521003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT4__ANADARK4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT4__WASHITA4_7 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7__G16_037_TAP_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7__GEN_2015_093_6 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRANFLD2__HOLLSTR2_7 | 3 Phase fault on GRANFLD2 (520926) 69 kV Bus a. Apply fault at the GRANFLD2 (520926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANFLD2 69.0 KV 520926 TO HOLLSTR2 69.0 KV 520945 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRANITE2__LKCREEK2_7 | 3 Phase fault on GRANITE2 (520927) 69 kV Bus a. Apply fault at the GRANITE2 (520927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANITE2 69.0 KV 520927 TO LKCREEK2 69.0 KV 520978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRAPLND4__SLOCUM_4_7 | 3 Phase fault on GRAPLND4 (509322) 138 kV Bus a. Apply fault at the GRAPLND4 (509322) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAPLND4 138.0 KV 509322 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.2. LOAD 1 509326 b.3. CROCKET4 138.0 KV 509240 TO GRAPLND4 138.0 KV 509322 CKT 1 b.4. LOAD 1 509322 b.5. ALTO 4 138.0 KV 509320 TO SLOCUM 4 138.0 KV 509326 CKT 1 b.6. LOAD 1 509326 b.7. ALTO 4 138.0 KV 509320 TO PINEGRV4 138.0 KV 509324 CKT 1 b.8. LOAD 1 509324 b.9. JACKSNV4 138.0 KV 509242 TO PINEGRV4 138.0 KV 509324 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GROVE__4__COWSKIN_4_7 | 3 Phase fault on GROVE 4 (510402) 138 kV Bus a. Apply fault at the GROVE 4 (510402) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 4 138.0 KV 510402 TO COWSKIN 4 138.0 KV 512719 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GROVE__5__NOL435_5_7 | 3 Phase fault on GROVE 5 (510411) 161 kV Bus a. Apply fault at the GROVE 5 (510411) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROVE 5 161.0 KV 510411 TO NOL435 5 161.0 KV 547496 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HARPER2__ANADARK2_7 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HEADRIK2__SNYDER_2_7 | 3 Phase fault on HEADRIK2 (511462) 69 kV Bus a. Apply fault at the HEADRIK2 (511462) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEADRIK2 69.0 KV 511462 TO SNYDER-2 69.0 KV 511475 CKT 1 b.2. LOAD 1 511475 b.3. HEADRIK2 69.0 KV 511462 TO TIPTN T2 69.0 KV 511543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HENESEY4__BULFTTP4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HENESEY4__DOVERSW4_7 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__POTTER_CO__7_6 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOB_JCT2__HOBART_2_7 | 3 Phase fault on HOB-JCT2 (511464) 69 kV Bus a. Apply fault at the HOB-JCT2 (511464) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT2 69.0 KV 511464 TO HOBART-2 69.0 KV 511465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOB_JCT4__MARTHA_4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO MARTHA 4 138.0 KV 511564 CKT 1 b.2. LOAD 1 511564 b.3. MARTHA 4 138.0 KV 511564 TO OMALTUS4 138.0 KV 529302 CKT 1 b.4. LOAD 1 529302 b.5. OMPVET-4 138.0 KV 529298 TO OMALTUS4 138.0 KV 529302 CKT 1 b.6. LOAD 1 529302 b.7. OMPVET-4 138.0 KV 529298 TO OMPARK-4 138.0 KV 529345 CKT 1 b.8. LOAD 1 529345 b.9. ALTUSJT4 138.0 KV 511440 TO OMPARK-4 138.0 KV 529345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOB_JCT4__RKY_RDG4_7 | 3 Phase fault on HOB-JCT4 (511463) 138 kV Bus a. Apply fault at the HOB-JCT4 (511463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOB-JCT4 138.0 KV 511463 TO RKY_RDG4 138.0 KV 511554 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUGOITC4__HUGO_PP4_7 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUGO___7__G16_063_TAP_6 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUNTERS7__CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUNTERS7__RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IMO____2__CLEVETP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO CLEVETP2 69.0 KV 514722 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IMO____2__GOLTYTP2_7 | 3 Phase fault on IMO 2 (514721) 69 kV Bus a. Apply fault at the IMO 2 (514721) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMO 2 69.0 KV 514721 TO GOLTYTP2 69.0 KV 515493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | INOLATP4__CATOOSA4_7 | 3 Phase fault on INOLATP4 (509752) 138 kV Bus a. Apply fault at the INOLATP4 (509752) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLATP4 138.0 KV 509752 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | INOLA__4__INOLATP4_7 | 3 Phase fault on INOLA 4 (509736) 138 kV Bus a. Apply fault at the INOLA 4 (509736) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INOLA 4 138.0 KV 509736 TO INOLATP4 138.0 KV 509752 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IODINE_4__WWRDEHV4_7 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 b.2. IODINE-4 138.0 KV 514796 TO REDCLFT4 138.0 KV 515533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IPCJEFF4__JEFFRSN4_7 | 3 Phase fault on IPCJEFF4 (508833) 138 kV Bus a. Apply fault at the IPCJEFF4 (508833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IPC_T__4__CASSTP4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IPC_T__4__IPC_DOM4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 b.2. LOAD 1 508060 b.3. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IPC_T__4__IPC____4_7 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JEFFRSN4__LAKEPIN4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JEFFRSN4__WILKES_4_7 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__CANEYCK4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__RUSSET_4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__SXMLCKT4_7 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_7__DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | JOHNCO_7__GEN_2017_149_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | JOHNCO_7__GEN_2020_015_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2020-015 345.0 KV 764270 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | JOHNCO_7__SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | KERR_GR5__412SUB_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO 412SUB 5 161.0 KV 512637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_GR5__KERR_BRK1_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK1 5 161.0 KV 512770 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_GR5__KERR_BRK4_5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO KERR BRK4 5 161.0 KV 512771 CKT Z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_GR5__MAID___5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO MAID 5 161.0 KV 512648 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_GR5__PENSA__5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO PENSA 5 161.0 KV 512654 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KERR_GR5__SALNCRK5_7 | 3 Phase fault on KERR GR5 (512635) 161 kV Bus a. Apply fault at the KERR GR5 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 161.0 KV 512635 TO SALNCRK5 161.0 KV 512805 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNOBHIL4__DGRASSE4_7 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNOXLEE4__BRANDYBR_7 | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LAKEP2WT__ELDORDO2_7 | 3 Phase fault on LAKEP2WT (512111) 69 kV Bus a. Apply fault at the LAKEP2WT (512111) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP2WT 69.0 KV 512111 TO ELDORDO2 69.0 KV 520896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LAKEP4WT__RUSSELL4_7 | 3 Phase fault on LAKEP4WT (512110) 138 kV Bus a. Apply fault at the LAKEP4WT (512110) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKEP4WT 138.0 KV 512110 TO RUSSELL4 138.0 KV 521043 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LEBROCK7__TENRUSK7_6 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_2__LGORE_N2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_2__LGORE_S2_7 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_4__COMMTAP4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_4__ELGINJT4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_4__SHERID4_7 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_7__G17_171_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2018-055 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027 , GEN-2018-055 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LES_7__G18_015_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LES_7__G18_092_PROX_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G18-092-PROX 345.0 KV 763215 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LES_7__G20_009_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-009-TAP 345.0 KV 766291 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LES_7__G20_075_TAP_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G20-075-TAP 345.0 KV 764550 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LES_7__GEN_2018_115_6 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO GEN-2018-115 345.0 KV 763318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 trips on voltage protection settings GEN-2017-027 trips on voltage protection settings GEN-2017-171 trips on voltage protection settings GEN-2017-172 trips on voltage protection settings GEN-2017-173 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2015-045, GEN-2017-027, GEN-2017-171, GEN-2017-172 & GEN-2017-173 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 - Southeast | 25W | Transfer | LG_YEAR4__112GORE4_7 | 3 Phase fault on LG-YEAR4 (511428) 138 kV Bus a. Apply fault at the LG-YEAR4 (511428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LG-YEAR4 138.0 KV 511428 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM4__LONGWD_4_7 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LKCREEK2__LONEWLF2_7 | 3 Phase fault on LKCREEK2 (520978) 69 kV Bus a. Apply fault at the LKCREEK2 (520978) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LKCREEK2 69.0 KV 520978 TO LONEWLF2 69.0 KV 520982 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LLAN_ET4__CATOOSA4_7 | 3 Phase fault on LLAN ET4 (509771) 138 kV Bus a. Apply fault at the LLAN ET4 (509771) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LLAN ET4 138.0 KV 509771 TO CATOOSA4 138.0 KV 509790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LOCKSBRG__4__PATTERS4_7 | 3 Phase fault on LOCKSBRG 4 (504123) 138 kV Bus a. Apply fault at the LOCKSBRG 4 (504123) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGVHT4__WHITNEY4_7 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__OAKPH__4_7 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_7__GEN_2018_050_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_7__WILKES_7_6 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__DIANA__4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__PITTSB_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__WILKES_4_7 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSTAR__3__PRY_JCT3_7 | 3 Phase fault on LSTAR--3 (510399) 115 kV Bus a. Apply fault at the LSTAR--3 (510399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSTAR--3 115.0 KV 510399 TO PRY-JCT3 115.0 KV 510407 CKT 1 b.2. LSTAR--3 115.0 KV 510399 TO L GROVE3 115.0 KV 510423 CKT 1 b.3. LOAD 1 510423 b.4. L GROVE3 115.0 KV 510423 TO KERR GR3 115.0 KV 512634 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWSTAP_4__LES_4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWSTAP_4__RPPAPER4_7 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS_NTP4__112GORE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS_NTP4__53CACHE4_7 | 3 Phase fault on LWS-NTP4 (511471) 138 kV Bus a. Apply fault at the LWS-NTP4 (511471) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS-NTP4 138.0 KV 511471 TO 53CACHE4 138.0 KV 511509 CKT 1 b.2. LOAD 1 511509 b.3. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS___N4__LWS_NTP4_7 | 3 Phase fault on LWS N4 (511430) 138 kV Bus a. Apply fault at the LWS N4 (511430) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS N4 138.0 KV 511430 TO LWS-NTP4 138.0 KV 511471 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS___S4__LWSTAP_4_7 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LYDIA__7__GEN_2018_088_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2018-088 345.0 KV 763164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25W | Transfer | LYDIA__7__GEN_2020_054_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO GEN-2020-054 345.0 KV 764075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LYDIA__7__VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25W | Transfer | LYDIA__7__WELSH__7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2020-054 trips on frequency protection settings | Disabling frequency protection settings for GEN-2020-054 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 - Southeast | 25W | Transfer | L_AIRGS4__LAIRGST4_7 | 3 Phase fault on L AIRGS4 (511429) 138 kV Bus a. Apply fault at the L AIRGS4 (511429) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L AIRGS4 138.0 KV 511429 TO LAIRGST4 138.0 KV 511510 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MADINDT4__CANEYCK4_7 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MAPLERD4__GEARYTP4_7 | 3 Phase fault on MAPLERD4 (511581) 138 kV Bus a. Apply fault at the MAPLERD4 (511581) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPLERD4 138.0 KV 511581 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARIETA4__SWILSON4_7 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__CTNWOOD4_7 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes